## Clean_Generation_Data
Date | Year | Month | Day | Power Plant | Capacity (MW) | Maximum Station Load (MW) | Avg Station Load (MW) | Total Daily Units Generated (kWh) | Daily Net Energy Output (kWh) | Avg Historical Hydrology | Actual Avg Cumic | Daily Actual Plant Factor | Tarif Rate | Daily Design Plant Factor | Avg Annual Design Plant Factor | Expected Generation (KWh) | Expected Revenue (PKR) | Actual Revenue (PKR) | Difference Revenue (PKR) | Aux. Cons. | Remarks/ Issues | Email Address | Row_Type | Fill_Notes | Source_File
2025-01-01 | 2025 | 1 | 1 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 17.52 | 4 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-01 | 2025 | 1 | 1 | Malakand-3 HPS | 81 | 13 | 11.56 | 277375 | 271490 | 25 | 9.16 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 777194.42 | 4787894.38 | 5885 | No | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-01 | 2025 | 1 | 1 | Pehur HPS | 18 | 7.3 | 7.2 | 172900 | 168000 | 10 | 16 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 632856 | 994488 | 4900 | Units on bar delivering power to the system, According to available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-01 | 2025 | 1 | 1 | Reshun HPS | 4.2 | 2.84 | 1.53 | 36000 | 35398 | 1.8 | 2.2 | 73.43 | 13.48 | 60 | 45 | 60480 | 815270.4 | 477165.04 | 338105.36 | 602 | low hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-01 | 2025 | 1 | 1 | Shishi HPS | 1.8 | 0.91 | 0.5 | 11910 | 11672 | 2.88 | 0.97 | 32.33 | 2.47 | 96 | 49 | 41472 | 102435.84 | 28829.84 | 73606 | 238 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-02 | 2025 | 1 | 2 | Machai HPS | 2.6 | 0.9 | 0.5 | 13512 | 12888 | 1 | 15 | 100 | 4.671 | 33.33 | 70 | 20800 | 97156.8 | 60199.85 | 36956.95 | 624 | The Unit after all preliminary checks and started at 0955Hrs Dated 02-01-2025 as rated head was restored due to increase in canal discharge as per new indent of Swabi Irrigation Sub Division. The water diverted to Machai Canal at 0500Hrs dated 02-01-2025 by irrigation department. Unit kept on FSNL for an half hour to carryout heat run test and finding everything normal then synchronized with the system at 1028Hrs and load gradually increased according to available inflow and system condition. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-02 | 2025 | 1 | 2 | Malakand-3 HPS | 81 | 14 | 13.14 | 315353 | 309630 | 27 | 9.87 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 886377.8 | 4678711 | 5723 | No | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-02 | 2025 | 1 | 2 | Pehur HPS | 18 | 7.4 | 7.3 | 176400 | 171000 | 10 | 16.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 644157 | 983187 | 5400 | Units on bar delivering power to the system, According to available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-02 | 2025 | 1 | 2 | Reshun HPS | 4.2 | 2.74 | 1.34 | 33000 | 32400 | 1.8 | 2.02 | 67.33 | 13.48 | 60 | 45 | 60480 | 815270.4 | 436752 | 378518.4 | 600 | low hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-02 | 2025 | 1 | 2 | Shishi HPS | 1.8 | 0.81 | 0.53 | 12690 | 12436 | 2.76 | 0.88 | 29.33 | 2.47 | 92 | 49 | 39744 | 98167.68 | 30716.92 | 67450.76 | 254 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-03 | 2025 | 1 | 3 | Daral Khwar HPS | 36.6 | 6 | 5.67 | 136190 | 136190 | 1.62 | 2.28 | 76 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 1126059.78 | 2795892.57 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-03 | 2025 | 1 | 3 | Machai HPS | 2.6 | 1.14 | 1.02 | 24744 | 23676 | 15.4 | 11 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 110590.6 | 180879.8 | 1068 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-03 | 2025 | 1 | 3 | Malakand-3 HPS | 81 | 18 | 15.81 | 379532 | 374180 | 28 | 11.35 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1071165.09 | 4493923.71 | 5352 | No | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-03 | 2025 | 1 | 3 | Pehur HPS | 18 | 8 | 7.5 | 181700 | 178000 | 10 | 17 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 670526 | 956818 | 3700 | Units on bar delivering power to the system, According to available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-03 | 2025 | 1 | 3 | Reshun HPS | 4.2 | 1.66 | 0.37 | 7000 | 6460 | 1.8 | 0.43 | 14.27 | 13.48 | 60 | 45 | 60480 | 815270.4 | 87080.8 | 728189.6 | 540 | Due to heavily Snowfall electricity is suspended. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-03 | 2025 | 1 | 3 | Shishi HPS | 1.8 | 0.86 | 0.54 | 12840 | 12583 | 2.98 | 0.91 | 30.33 | 2.47 | 99.33 | 49 | 42912 | 105992.64 | 31080.01 | 74912.63 | 257 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-04 | 2025 | 1 | 4 | Daral Khwar HPS | 36.6 | 6 | 5.1 | 122440 | 122440 | 1.62 | 2.05 | 68.33 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 1012370.65 | 2909581.7 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-04 | 2025 | 1 | 4 | Machai HPS | 2.6 | 1.3 | 0.85 | 22528 | 21780 | 15.4 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 101734.38 | 189736.02 | 748 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-04 | 2025 | 1 | 4 | Malakand-3 HPS | 81 | 16 | 5.37 | 128952 | 127110 | 24 | 4.35 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 363877.8 | 5201211 | 1842 | No | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-04 | 2025 | 1 | 4 | Pehur HPS | 18 | 8.1 | 5.6 | 134400 | 129000 | 10 | 13 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 485943 | 1141401 | 5400 | At 1647Hrs, Units were taken Off the bar due to nil irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-04 | 2025 | 1 | 4 | Reshun HPS | 4.2 | 2.11 | 1.03 | 23000 | 22440 | 1.8 | 1.41 | 46.93 | 13.48 | 60 | 45 | 60480 | 815270.4 | 302491.2 | 512779.2 | 560 | Shortage of water. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-04 | 2025 | 1 | 4 | Shishi HPS | 1.8 | 0.89 | 0.46 | 11130 | 10970 | 2.85 | 0.95 | 31.67 | 2.47 | 95 | 49 | 41040 | 101368.8 | 27095.9 | 74272.9 | 160 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-05 | 2025 | 1 | 5 | Daral Khwar HPS | 36.6 | 5 | 4.7 | 112710 | 112710 | 1.62 | 1.88 | 62.67 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 931920.09 | 2990032.26 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-05 | 2025 | 1 | 5 | Machai HPS | 2.6 | 1.33 | 1.15 | 28076 | 85488 | 15.4 | 14.3 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 399314.45 | -107844.05 | 57412 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original | CHECK: Net > Units (source me verify karein) | Link_Generation_Data_Summary.xlsx
2025-01-05 | 2025 | 1 | 5 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-05 | 2025 | 1 | 5 | Pehur HPS | 18 | 8 | 2 | 42800 | 42000 | 10 | 4 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 158214 | 1469130 | 800 | Generation is less because plant shutdown from 1647Hrs dated 04/01/25 to 1810Hrs dated 05/01/25 due to nil irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-05 | 2025 | 1 | 5 | Reshun HPS | 4.2 | 1.83 | 0.36 | 8000 | 7440 | 1.8 | 0.49 | 16.3 | 13.48 | 60 | 45 | 60480 | 815270.4 | 100291.2 | 714979.2 | 560 | Line faults due to heavy snowfall. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-05 | 2025 | 1 | 5 | Shishi HPS | 1.8 | 0.79 | 0.31 | 7500 | 7350 | 2.53 | 0.86 | 28.67 | 2.47 | 84.33 | 49 | 36432 | 89987.04 | 18154.5 | 71832.54 | 150 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-06 | 2025 | 1 | 6 | Daral Khwar HPS | 36.6 | 4.8 | 4.33 | 103870 | 103870 | 1.62 | 1.74 | 58 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 858828.32 | 3063124.03 | 0 | 132KV Supply line failed | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-06 | 2025 | 1 | 6 | Machai HPS | 2.6 | 1.47 | 1.16 | 27820 | 26844 | 18 | 14.8 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 125388.32 | 166082.08 | 976 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-06 | 2025 | 1 | 6 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-06 | 2025 | 1 | 6 | Pehur HPS | 18 | 8 | 3.5 | 85500 | 84000 | 10 | 7 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 316428 | 1310916 | 1500 | Generation is less because Units Off the bar due to tripping of 132kv line Gadoon Grid, | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-06 | 2025 | 1 | 6 | Reshun HPS | 4.2 | 2.18 | 1.11 | 27000 | 26410 | 1.8 | 1.65 | 55.07 | 13.48 | 60 | 45 | 60480 | 815270.4 | 356006.8 | 459263.6 | 590 | Low hydrology | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-06 | 2025 | 1 | 6 | Shishi HPS | 1.8 | 0.84 | 0.52 | 12420 | 12172 | 2.56 | 0.9 | 30 | 2.47 | 85.33 | 49 | 36864 | 91054.08 | 30064.84 | 60989.24 | 248 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-07 | 2025 | 1 | 7 | Daral Khwar HPS | 36.6 | 5 | 4.52 | 108510 | 108510 | 1.62 | 1.81 | 60.33 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 897193.23 | 3024759.12 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-07 | 2025 | 1 | 7 | Machai HPS | 2.6 | 1.48 | 1.33 | 32256 | 31108 | 18 | 14 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 145305.47 | 146164.93 | 1148 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-07 | 2025 | 1 | 7 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-07 | 2025 | 1 | 7 | Pehur HPS | 18 | 8.1 | 8 | 193900 | 188000 | 10 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 708196 | 919148 | 5900 | Units on bar delivering power to the system, According to available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-07 | 2025 | 1 | 7 | Reshun HPS | 4.2 | 2.76 | 1.64 | 35000 | 34400 | 1.8 | 2.14 | 71.4 | 13.48 | 60 | 45 | 60480 | 815270.4 | 463712 | 351558.4 | 600 | Shortage of Water. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-07 | 2025 | 1 | 7 | Shishi HPS | 1.8 | 0.76 | 0.55 | 13110 | 12848 | 2.65 | 0.84 | 28 | 2.47 | 88.33 | 49 | 38160 | 94255.2 | 31734.56 | 62520.64 | 262 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-08 | 2025 | 1 | 8 | Daral Khwar HPS | 36.6 | 5 | 4.64 | 111400 | 111400 | 1.62 | 1.86 | 62 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 921088.62 | 3000863.73 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-08 | 2025 | 1 | 8 | Machai HPS | 2.6 | 1.1 | 0.89 | 21924 | 20988 | 18 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 98034.95 | 193435.45 | 936 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-08 | 2025 | 1 | 8 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-08 | 2025 | 1 | 8 | Pehur HPS | 18 | 8.3 | 7.2 | 173400 | 168000 | 10 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 632856 | 994488 | 5400 | Units on bar delivering power to the system, According to available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-08 | 2025 | 1 | 8 | Reshun HPS | 4.2 | 2.94 | 1.64 | 36000 | 35406 | 1.8 | 2.2 | 73.43 | 13.48 | 60 | 45 | 60480 | 815270.4 | 477272.88 | 337997.52 | 594 | Low hydrology/load shedding observed. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-08 | 2025 | 1 | 8 | Shishi HPS | 1.8 | 0.85 | 0.55 | 13230 | 12965 | 2.54 | 0.89 | 29.67 | 2.47 | 84.67 | 49 | 36576 | 90342.72 | 32023.55 | 58319.17 | 265 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-09 | 2025 | 1 | 9 | Daral Khwar HPS | 36.6 | 4.7 | 4.47 | 107310 | 107310 | 1.62 | 1.79 | 59.67 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 887271.27 | 3034681.08 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-09 | 2025 | 1 | 9 | Machai HPS | 2.6 | 1.43 | 0.91 | 21920 | 21076 | 18 | 4 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 98446 | 193024.4 | 844 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-09 | 2025 | 1 | 9 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-09 | 2025 | 1 | 9 | Pehur HPS | 18 | 6.4 | 5.1 | 122700 | 118000 | 10 | 12 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 444506 | 1182838 | 4700 | Generation is less because of nil irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-09 | 2025 | 1 | 9 | Reshun HPS | 4.2 | 3.2 | 1.59 | 37000 | 36402 | 1.8 | 2.26 | 75.5 | 13.48 | 60 | 45 | 60480 | 815270.4 | 490698.96 | 324571.44 | 598 | (I). Tariff rate PESCO's Slab wise prevailing rates starting from basic slab of Rs. 13.48/kwh. Shortage of Water/low hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-09 | 2025 | 1 | 9 | Shishi HPS | 1.8 | 0.82 | 0.54 | 13050 | 12789 | 2.43 | 0.9 | 30 | 2.47 | 81 | 49 | 34992 | 86430.24 | 31588.83 | 54841.41 | 261 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-10 | 2025 | 1 | 10 | Daral Khwar HPS | 36.6 | 4.8 | 4.38 | 105050 | 105050 | 1.62 | 1.76 | 58.67 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 868584.92 | 3053367.43 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-10 | 2025 | 1 | 10 | Machai HPS | 2.6 | 1.34 | 0.43 | 11192 | 10780 | 5 | 4 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 50353.38 | 241117.02 | 412 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-10 | 2025 | 1 | 10 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-10 | 2025 | 1 | 10 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | Plant completely shutdown since 2400Hrs dated 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-10 | 2025 | 1 | 10 | Reshun HPS | 4.2 | 3.24 | 1.38 | 32000 | 31400 | 1.8 | 1.96 | 65.3 | 13.48 | 60 | 45 | 60480 | 815270.4 | 423272 | 391998.4 | 600 | due to low hydrology load shedding is observing. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-10 | 2025 | 1 | 10 | Shishi HPS | 1.8 | 0.8 | 0.52 | 12600 | 12348 | 2.28 | 0.87 | 29 | 2.47 | 76 | 49 | 32832 | 81095.04 | 30499.56 | 50595.48 | 252 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-11 | 2025 | 1 | 11 | Daral Khwar HPS | 36.6 | 4.5 | 4.3 | 103210 | 103210 | 1.62 | 1.73 | 57.67 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 853371.24 | 3068581.11 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-11 | 2025 | 1 | 11 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-11 | 2025 | 1 | 11 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-11 | 2025 | 1 | 11 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-11 | 2025 | 1 | 11 | Reshun HPS | 4.2 | 3.24 | 1.48 | 37000 | 36370 | 1.8 | 2.26 | 75.5 | 13.48 | 60 | 45 | 60480 | 815270.4 | 490267.6 | 325002.8 | 630 | low hydrology/water of storage | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-11 | 2025 | 1 | 11 | Shishi HPS | 1.8 | 0.94 | 0.47 | 11280 | 11054 | 1.98 | 1 | 33.33 | 2.47 | 66 | 49 | 28512 | 70424.64 | 27303.38 | 43121.26 | 226 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-12 | 2025 | 1 | 12 | Daral Khwar HPS | 36.6 | 4.8 | 4.3 | 103200 | 103200 | 1.62 | 1.73 | 57.67 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 853288.56 | 3068663.79 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-12 | 2025 | 1 | 12 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-12 | 2025 | 1 | 12 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-12 | 2025 | 1 | 12 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-12 | 2025 | 1 | 12 | Reshun HPS | 4.2 | 3.25 | 1.62 | 33000 | 32399 | 1.8 | 2.02 | 67.33 | 13.48 | 60 | 45 | 60480 | 815270.4 | 436738.52 | 378531.88 | 601 | Storage of water due to low hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-12 | 2025 | 1 | 12 | Shishi HPS | 1.8 | 0.81 | 0.54 | 12840 | 12583 | 2 | 0.89 | 29.67 | 2.47 | 66.67 | 49 | 28800 | 71136 | 31080.01 | 40055.99 | 257 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-13 | 2025 | 1 | 13 | Daral Khwar HPS | 36.6 | 4.8 | 4.02 | 96460 | 96460 | 1.62 | 1.61 | 53.67 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 797560.22 | 3124392.13 | 0 | 132KV Supply line failed | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-13 | 2025 | 1 | 13 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-13 | 2025 | 1 | 13 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-13 | 2025 | 1 | 13 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-13 | 2025 | 1 | 13 | Reshun HPS | 4.2 | 3.32 | 1.54 | 33000 | 32398 | 1.8 | 2.02 | 67.33 | 13.48 | 60 | 45 | 60480 | 815270.4 | 436725.04 | 378545.36 | 602 | load shedding is observed due to low hydrology | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-13 | 2025 | 1 | 13 | Shishi HPS | 1.8 | 0.74 | 0.48 | 11490 | 11260 | 1.87 | 0.82 | 27.33 | 2.47 | 62.33 | 49 | 26928 | 66512.16 | 27812.2 | 38699.96 | 230 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-14 | 2025 | 1 | 14 | Daral Khwar HPS | 36.6 | 4.3 | 4.18 | 100400 | 100400 | 1.62 | 1.68 | 56 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 830137.32 | 3091815.03 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-14 | 2025 | 1 | 14 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-14 | 2025 | 1 | 14 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-14 | 2025 | 1 | 14 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-14 | 2025 | 1 | 14 | Reshun HPS | 4.2 | 3.38 | 1.62 | 34000 | 33388 | 1.8 | 2.08 | 69.37 | 13.48 | 60 | 45 | 60480 | 815270.4 | 450070.24 | 365200.16 | 612 | Storage of water due to low hydrology | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-14 | 2025 | 1 | 14 | Shishi HPS | 1.8 | 0.79 | 0.52 | 12360 | 12113 | 1.91 | 0.85 | 28.33 | 2.47 | 63.67 | 49 | 27504 | 67934.88 | 29919.11 | 38015.77 | 247 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-15 | 2025 | 1 | 15 | Daral Khwar HPS | 36.6 | 4.3 | 3.98 | 95480 | 95480 | 1.62 | 1.6 | 53.33 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 789457.28 | 3132495.06 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-15 | 2025 | 1 | 15 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-15 | 2025 | 1 | 15 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-15 | 2025 | 1 | 15 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-15 | 2025 | 1 | 15 | Reshun HPS | 4.2 | 3.3 | 1.56 | 33000 | 32385 | 1.8 | 2.02 | 67.33 | 13.48 | 60 | 45 | 60480 | 815270.4 | 436549.8 | 378720.6 | 615 | Low hydrology/load shedding | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-15 | 2025 | 1 | 15 | Shishi HPS | 1.8 | 0.79 | 0.53 | 12720 | 12466 | 1.89 | 0.86 | 28.67 | 2.47 | 63 | 49 | 27216 | 67223.52 | 30791.02 | 36432.5 | 254 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-16 | 2025 | 1 | 16 | Daral Khwar HPS | 36.6 | 4.1 | 3.96 | 95040 | 95040 | 1.62 | 1.59 | 53 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 785819.23 | 3136133.12 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-16 | 2025 | 1 | 16 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-16 | 2025 | 1 | 16 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-16 | 2025 | 1 | 16 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-16 | 2025 | 1 | 16 | Reshun HPS | 4.2 | 3.14 | 1.51 | 33000 | 32374 | 1.8 | 2.02 | 67.33 | 13.48 | 60 | 45 | 60480 | 815270.4 | 436401.52 | 378868.88 | 626 | Load shedding/low hydrology | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-16 | 2025 | 1 | 16 | Shishi HPS | 1.8 | 0.79 | 0.54 | 12840 | 12583 | 1.89 | 0.86 | 28.77 | 2.47 | 63.07 | 49 | 27244.8 | 67294.66 | 31080.01 | 36214.65 | 257 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-17 | 2025 | 1 | 17 | Daral Khwar HPS | 36.6 | 4.1 | 3.77 | 90520 | 90520 | 1.62 | 1.51 | 50.33 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 748446.52 | 3173505.83 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-17 | 2025 | 1 | 17 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-17 | 2025 | 1 | 17 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-17 | 2025 | 1 | 17 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-17 | 2025 | 1 | 17 | Reshun HPS | 4.2 | 3.21 | 1.53 | 34000 | 33390 | 1.8 | 2.08 | 69.37 | 13.48 | 60 | 45 | 60480 | 815270.4 | 450097.2 | 365173.2 | 610 | Storage of water/load shedding | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-17 | 2025 | 1 | 17 | Shishi HPS | 1.8 | 0.8 | 0.74 | 11613 | 11378 | 1.93 | 0.88 | 29.33 | 2.47 | 64.33 | 49 | 27792 | 68646.24 | 28103.66 | 40542.58 | 235 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-18 | 2025 | 1 | 18 | Daral Khwar HPS | 36.6 | 3.8 | 3.69 | 88450 | 88450 | 1.62 | 1.48 | 49.33 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 731331.14 | 3190621.21 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-18 | 2025 | 1 | 18 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-18 | 2025 | 1 | 18 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-18 | 2025 | 1 | 18 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-18 | 2025 | 1 | 18 | Reshun HPS | 4.2 | 3.09 | 1.48 | 32000 | 31380 | 1.8 | 1.96 | 65.3 | 13.48 | 60 | 45 | 60480 | 815270.4 | 423002.4 | 392268 | 620 | load shedding/Low hydrology/storage of water | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-18 | 2025 | 1 | 18 | Shishi HPS | 1.8 | 0.89 | 0.53 | 12770 | 12495 | 1.94 | 0.94 | 31.33 | 2.47 | 64.6 | 49 | 27907.2 | 68930.78 | 30862.65 | 38068.13 | 275 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-19 | 2025 | 1 | 19 | Daral Khwar HPS | 36.6 | 3.8 | 3.71 | 88960 | 88960 | 1.62 | 1.49 | 49.67 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 735547.97 | 3186404.38 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-19 | 2025 | 1 | 19 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-19 | 2025 | 1 | 19 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-19 | 2025 | 1 | 19 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-19 | 2025 | 1 | 19 | Reshun HPS | 4.2 | 3.01 | 1.46 | 31000 | 30399 | 1.8 | 1.9 | 63.23 | 13.48 | 60 | 45 | 60480 | 815270.4 | 409778.52 | 405491.88 | 601 | Water storage due to low hydrology | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-19 | 2025 | 1 | 19 | Shishi HPS | 1.8 | 0.88 | 0.41 | 9840 | 9643 | 1.88 | 0.92 | 30.67 | 2.47 | 62.53 | 49 | 27014.4 | 66725.57 | 23818.21 | 42907.36 | 197 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-20 | 2025 | 1 | 20 | Daral Khwar HPS | 36.6 | 3.8 | 3.7 | 88710 | 88710 | 1.62 | 1.48 | 49.33 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 733480.89 | 3188471.46 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-20 | 2025 | 1 | 20 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-20 | 2025 | 1 | 20 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-20 | 2025 | 1 | 20 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-20 | 2025 | 1 | 20 | Reshun HPS | 4.2 | 3.05 | 1.5 | 31000 | 30400 | 1.8 | 1.9 | 63.23 | 13.48 | 60 | 45 | 60480 | 815270.4 | 409792 | 405478.4 | 600 | (I). Shortage of Water/low hydrology/ Tariff rate PESCO's Slab wise prevailing rates starting from basic slab of Rs. 13.48/kwh. . | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-20 | 2025 | 1 | 20 | Shishi HPS | 1.8 | 0.75 | 0.49 | 11730 | 11495 | 1.79 | 0.85 | 28.33 | 2.47 | 59.63 | 49 | 25761.6 | 63631.15 | 28392.65 | 35238.5 | 235 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-21 | 2025 | 1 | 21 | Daral Khwar HPS | 36.6 | 4 | 2.86 | 68720 | 68720 | 1.62 | 1.15 | 38.33 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 568197.58 | 3353754.77 | 0 | Plant Shutdown due to PESCO Permit | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-21 | 2025 | 1 | 21 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-21 | 2025 | 1 | 21 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-21 | 2025 | 1 | 21 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-21 | 2025 | 1 | 21 | Reshun HPS | 4.2 | 3.19 | 1.48 | 33000 | 32378 | 1.8 | 2.02 | 67.33 | 13.48 | 60 | 45 | 60480 | 815270.4 | 436455.44 | 378814.96 | 622 | Load shedding observed/low hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-21 | 2025 | 1 | 21 | Shishi HPS | 1.8 | 0.76 | 0.54 | 13050 | 12789 | 1.8 | 0.84 | 28 | 2.47 | 59.9 | 49 | 25876.8 | 63915.7 | 31588.83 | 32326.87 | 261 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-22 | 2025 | 1 | 22 | Daral Khwar HPS | 36.6 | 4 | 3.76 | 90320 | 90320 | 1.62 | 1.51 | 50.33 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 746792.86 | 3175159.49 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-22 | 2025 | 1 | 22 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-22 | 2025 | 1 | 22 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-22 | 2025 | 1 | 22 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-22 | 2025 | 1 | 22 | Reshun HPS | 4.2 | 3.3 | 1.48 | 32000 | 31398 | 1.8 | 1.96 | 65.3 | 13.48 | 60 | 45 | 60480 | 815270.4 | 423245.04 | 392025.36 | 602 | low hydrology/water storage. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-22 | 2025 | 1 | 22 | Shishi HPS | 1.8 | 0.76 | 0.52 | 12360 | 12113 | 1.77 | 0.81 | 27.1 | 2.47 | 59 | 49 | 25488 | 62955.36 | 29919.11 | 33036.25 | 247 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-23 | 2025 | 1 | 23 | Daral Khwar HPS | 36.6 | 4 | 3.76 | 90160 | 90160 | 1.62 | 1.51 | 50.33 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 745469.93 | 3176482.42 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-23 | 2025 | 1 | 23 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-23 | 2025 | 1 | 23 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-23 | 2025 | 1 | 23 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-23 | 2025 | 1 | 23 | Reshun HPS | 4.2 | 3.17 | 1.47 | 32000 | 31396 | 1.8 | 1.96 | 65.3 | 13.48 | 60 | 45 | 60480 | 815270.4 | 423218.08 | 392052.32 | 604 | Shortage of water/load shedding | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-23 | 2025 | 1 | 23 | Shishi HPS | 1.8 | 0.78 | 0.53 | 12730 | 12475 | 1.79 | 0.83 | 27.67 | 2.47 | 59.67 | 49 | 25776 | 63666.72 | 30813.25 | 32853.47 | 255 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-24 | 2025 | 1 | 24 | Daral Khwar HPS | 36.6 | 4 | 3.5 | 84080 | 84080 | 1.62 | 1.41 | 47 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 695198.66 | 3226753.68 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-24 | 2025 | 1 | 24 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-24 | 2025 | 1 | 24 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-24 | 2025 | 1 | 24 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-24 | 2025 | 1 | 24 | Reshun HPS | 4.2 | 3.23 | 1.54 | 34000 | 33405 | 1.8 | 2.08 | 69.37 | 13.48 | 60 | 45 | 60480 | 815270.4 | 450299.4 | 364971 | 595 | (I). Tariff rate PESCO's Slab wise prevailing rates starting from basic slab of Rs. 13.48/kwh. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-24 | 2025 | 1 | 24 | Shishi HPS | 1.8 | 0.77 | 0.5 | 12128 | 11936 | 3 | 0.86 | 28.67 | 2.47 | 100 | 49 | 43200 | 106704 | 29481.92 | 77222.08 | 192 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-25 | 2025 | 1 | 25 | Daral Khwar HPS | 36.6 | 3.8 | 3.33 | 79890 | 79890 | 1.62 | 1.34 | 44.67 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 660554.49 | 3261397.86 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-25 | 2025 | 1 | 25 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-25 | 2025 | 1 | 25 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-25 | 2025 | 1 | 25 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-25 | 2025 | 1 | 25 | Reshun HPS | 4.2 | 2.63 | 1.38 | 32000 | 31399 | 1.8 | 1.96 | 65.3 | 13.48 | 60 | 45 | 60480 | 815270.4 | 423258.52 | 392011.88 | 601 | load shedding is observed due to low hydrology and storage of water in the Reservoir. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-25 | 2025 | 1 | 25 | Shishi HPS | 1.8 | 0.88 | 0.53 | 12668 | 12407 | 1.7 | 0.93 | 31 | 2.47 | 56.63 | 49 | 24465.6 | 60430.03 | 30645.29 | 29784.74 | 261 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-26 | 2025 | 1 | 26 | Daral Khwar HPS | 36.6 | 3.5 | 3.43 | 82200 | 82200 | 1.62 | 1.37 | 45.67 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 679654.26 | 3242298.09 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-26 | 2025 | 1 | 26 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-26 | 2025 | 1 | 26 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-26 | 2025 | 1 | 26 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-26 | 2025 | 1 | 26 | Reshun HPS | 4.2 | 2.96 | 1.29 | 32000 | 31387 | 1.8 | 1.96 | 65.3 | 13.48 | 60 | 45 | 60480 | 815270.4 | 423096.76 | 392173.64 | 613 | Low hydrology/load shedding. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-26 | 2025 | 1 | 26 | Shishi HPS | 1.8 | 0.74 | 0.49 | 11820 | 11584 | 1.7 | 0.82 | 27.33 | 2.47 | 56.57 | 49 | 24439.68 | 60366.01 | 28612.48 | 31753.53 | 236 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-27 | 2025 | 1 | 27 | Daral Khwar HPS | 36.6 | 3.8 | 3.51 | 84310 | 84310 | 1.62 | 1.41 | 47 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 697100.37 | 3224851.98 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-27 | 2025 | 1 | 27 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-27 | 2025 | 1 | 27 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-27 | 2025 | 1 | 27 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-27 | 2025 | 1 | 27 | Reshun HPS | 4.2 | 3.13 | 1.46 | 33000 | 32380 | 1.8 | 2.02 | 67.33 | 13.48 | 60 | 45 | 60480 | 815270.4 | 436482.4 | 378788 | 620 | (I). Tariff rate PESCO's Slab wise prevailing rates starting from basic slab of Rs. 13.48/kwh. Shortage of Water/low hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-27 | 2025 | 1 | 27 | Shishi HPS | 1.8 | 0.76 | 0.5 | 12690 | 11819 | 1.58 | 0.84 | 28 | 2.47 | 52.67 | 49 | 22752 | 56197.44 | 29192.93 | 27004.51 | 871 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-28 | 2025 | 1 | 28 | Daral Khwar HPS | 36.6 | 3.8 | 2.84 | 68070 | 68070 | 1.62 | 1.14 | 38 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 562823.18 | 3359129.17 | 0 | Plant Shutdown due to PESCO Permit | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-28 | 2025 | 1 | 28 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-28 | 2025 | 1 | 28 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-28 | 2025 | 1 | 28 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-28 | 2025 | 1 | 28 | Reshun HPS | 4.2 | 3.02 | 1.5 | 32000 | 3 | 1.8 | 1.96 | 65.3 | 13.48 | 60 | 45 | 60480 | 815270.4 | 40.68 | 815229.72 | 31996.98 | Load shedding has been observed due to storage of water in the Reservoir. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-28 | 2025 | 1 | 28 | Shishi HPS | 1.8 | 0.72 | 0.51 | 12210 | 11966 | 1.72 | 0.8 | 26.67 | 2.47 | 57.33 | 49 | 24768 | 61176.96 | 29556.02 | 31620.94 | 244 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-29 | 2025 | 1 | 29 | Daral Khwar HPS | 36.6 | 4.3 | 3.94 | 94550 | 94550 | 1.62 | 1.58 | 52.67 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 781767.76 | 3140184.58 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-29 | 2025 | 1 | 29 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-29 | 2025 | 1 | 29 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-29 | 2025 | 1 | 29 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-29 | 2025 | 1 | 29 | Reshun HPS | 4.2 | 3.11 | 1.47 | 32000 | 31404 | 1.8 | 1.96 | 65.3 | 13.48 | 60 | 45 | 60480 | 815270.4 | 423325.92 | 391944.48 | 596 | Low hydrology and load shedding. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-29 | 2025 | 1 | 29 | Shishi HPS | 1.8 | 0.73 | 0.44 | 10620 | 10408 | 1.65 | 0.84 | 28 | 2.47 | 55 | 49 | 23760 | 58687.2 | 25707.76 | 32979.44 | 212 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-30 | 2025 | 1 | 30 | Daral Khwar HPS | 36.6 | 4 | 3.84 | 92080 | 92080 | 1.62 | 1.54 | 51.33 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 761345.06 | 3160607.28 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-30 | 2025 | 1 | 30 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-30 | 2025 | 1 | 30 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-30 | 2025 | 1 | 30 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-30 | 2025 | 1 | 30 | Reshun HPS | 4.2 | 3.14 | 1.5 | 31000 | 30400 | 1.8 | 1.9 | 63.23 | 13.48 | 60 | 45 | 60480 | 815270.4 | 409792 | 405478.4 | 600 | Storage of Water in the Reservoir. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-30 | 2025 | 1 | 30 | Shishi HPS | 1.8 | 0.84 | 0.49 | 11790 | 11554 | 2 | 0.88 | 29.33 | 2.47 | 66.67 | 49 | 28800 | 71136 | 28538.38 | 42597.62 | 236 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-31 | 2025 | 1 | 31 | Daral Khwar HPS | 36.6 | 4 | 3.82 | 91780 | 91780 | 1.62 | 1.53 | 51 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 758864.57 | 3163087.78 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-31 | 2025 | 1 | 31 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-31 | 2025 | 1 | 31 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-31 | 2025 | 1 | 31 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-31 | 2025 | 1 | 31 | Reshun HPS | 4.2 | 3.24 | 1.52 | 31000 | 30404 | 1.8 | 1.9 | 63.23 | 13.48 | 60 | 45 | 60480 | 815270.4 | 409845.92 | 405424.48 | 596 | During the storage of water in the Reservoir, load shedding has been observed. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-01-31 | 2025 | 1 | 31 | Shishi HPS | 1.8 | 0.84 | 0.5 | 11910 | 11672 | 2 | 0.84 | 27.87 | 2.47 | 66.67 | 49 | 28800 | 71136 | 28829.84 | 42306.16 | 238 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-01 | 2025 | 2 | 1 | Daral Khwar HPS | 36.6 | 4 | 3.76 | 90360 | 90360 | 1.85 | 1.51 | 50.33 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 747123.59 | 3731649.16 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-01 | 2025 | 2 | 1 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-01 | 2025 | 2 | 1 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-01 | 2025 | 2 | 1 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-01 | 2025 | 2 | 1 | Reshun HPS | 4.2 | 3.15 | 1.49 | 31000 | 30402 | 1.99 | 1.9 | 63.33 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 409818.96 | 491507.76 | 598 | Low hydrology | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-01 | 2025 | 2 | 1 | Shishi HPS | 1.8 | 0.84 | 0.4 | 9660 | 9467 | 1.8 | 0.87 | 29 | 2.47 | 60 | 49 | 25920 | 64022.4 | 23383.49 | 40638.91 | 193 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-02 | 2025 | 2 | 2 | Daral Khwar HPS | 36.6 | 3.8 | 3.48 | 83430 | 83430 | 1.85 | 1.4 | 46.67 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 689824.27 | 3788948.48 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-02 | 2025 | 2 | 2 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-02 | 2025 | 2 | 2 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-02 | 2025 | 2 | 2 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-02 | 2025 | 2 | 2 | Reshun HPS | 4.2 | 3.2 | 1.4 | 30000 | 29406 | 1.99 | 1.83 | 61 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 396392.88 | 504933.84 | 594 | (I). Tariff rate PESCO's Slab wise prevailing rates starting from basic slab of Rs. 13.48/kwh. (II). Shortage of Water/low hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-02 | 2025 | 2 | 2 | Shishi HPS | 1.8 | 0.78 | 0.52 | 12360 | 12113 | 2.11 | 0.84 | 28 | 2.47 | 70.33 | 49 | 30384 | 75048.48 | 29919.11 | 45129.37 | 247 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-03 | 2025 | 2 | 3 | Daral Khwar HPS | 36.6 | 3.8 | 3.46 | 83150 | 83150 | 1.85 | 1.39 | 46.33 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 687509.14 | 3791263.6 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-03 | 2025 | 2 | 3 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-03 | 2025 | 2 | 3 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-03 | 2025 | 2 | 3 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-03 | 2025 | 2 | 3 | Reshun HPS | 4.2 | 3.33 | 1.53 | 30000 | 29409 | 1.99 | 1.83 | 61 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 396433.32 | 504893.4 | 591 | due to low hydrology load shedding has been observed. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-03 | 2025 | 2 | 3 | Shishi HPS | 1.8 | 0.48 | 0.48 | 11580 | 11348 | 2.55 | 0.8 | 26.67 | 2.47 | 85 | 49 | 36720 | 90698.4 | 28029.56 | 62668.84 | 232 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-04 | 2025 | 2 | 4 | Daral Khwar HPS | 36.6 | 3.8 | 3.56 | 85520 | 85520 | 1.85 | 1.43 | 47.67 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 707105.02 | 3771667.73 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-04 | 2025 | 2 | 4 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-04 | 2025 | 2 | 4 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-04 | 2025 | 2 | 4 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-04 | 2025 | 2 | 4 | Reshun HPS | 4.2 | 3.35 | 1.49 | 29000 | 28202 | 1.99 | 1.83 | 61 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 380162.96 | 521163.76 | 798 | due to low hydrology load shedding has been observed. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-04 | 2025 | 2 | 4 | Shishi HPS | 1.8 | 0.73 | 0.5 | 11940 | 11701 | 2.34 | 0.81 | 27 | 2.47 | 78 | 49 | 33696 | 83229.12 | 28901.47 | 54327.65 | 239 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-05 | 2025 | 2 | 5 | Daral Khwar HPS | 36.6 | 3.6 | 3.4 | 81580 | 81580 | 1.85 | 1.36 | 45.33 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 674527.91 | 3804244.83 | 0 | Unit tripped due to over frequency from National Grid side | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-05 | 2025 | 2 | 5 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | No data submitted for this date | engr.atifwazir@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-02-05 | 2025 | 2 | 5 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-05 | 2025 | 2 | 5 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-05 | 2025 | 2 | 5 | Reshun HPS | 4.2 | 3.18 | 1.42 | 31000 | 30408 | 1.99 | 1.9 | 63.33 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 409899.84 | 491426.88 | 592 | (I). Low hydrology. (II). Tariff rate PESCO's Slab wise prevailing rates starting from basic slab of Rs. 13.48/kwh. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-05 | 2025 | 2 | 5 | Shishi HPS | 1.8 | 0.78 | 0.51 | 12210 | 11966 | 2.45 | 0.84 | 28 | 2.47 | 81.67 | 49 | 35280 | 87141.6 | 29556.02 | 57585.58 | 244 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-06 | 2025 | 2 | 6 | Daral Khwar HPS | 36.6 | 3.6 | 3.35 | 80420 | 80420 | 1.85 | 1.34 | 44.67 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 664936.69 | 3813836.06 | 0 | Unit tripped due to over frequency from National Grid side | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-06 | 2025 | 2 | 6 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-06 | 2025 | 2 | 6 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-06 | 2025 | 2 | 6 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-06 | 2025 | 2 | 6 | Reshun HPS | 4.2 | 3.13 | 1.4 | 30000 | 29409 | 1.99 | 1.83 | 61 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 396433.32 | 504893.4 | 591 | Low hydrology and load shedding observed. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-06 | 2025 | 2 | 6 | Shishi HPS | 1.8 | 0.69 | 0.49 | 11700 | 11466 | 2.21 | 0.8 | 26.67 | 2.47 | 73.67 | 49 | 31824 | 78605.28 | 28321.02 | 50284.26 | 234 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-07 | 2025 | 2 | 7 | Daral Khwar HPS | 36.6 | 3.6 | 2.22 | 53300 | 53300 | 1.85 | 0.89 | 29.67 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 440700.39 | 4038072.35 | 0 | In-House Fault on CB of MTR#03 | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-07 | 2025 | 2 | 7 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-07 | 2025 | 2 | 7 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-07 | 2025 | 2 | 7 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-07 | 2025 | 2 | 7 | Reshun HPS | 4.2 | 3.25 | 1.54 | 29000 | 28402 | 1.99 | 1.77 | 59 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 382858.96 | 518467.76 | 598 | Load hydrology and load shedding. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-07 | 2025 | 2 | 7 | Shishi HPS | 1.8 | 0.7 | 0.5 | 11940 | 11710 | 2.3 | 0.8 | 26.67 | 2.47 | 76.67 | 49 | 33120 | 81806.4 | 28923.7 | 52882.7 | 230 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-08 | 2025 | 2 | 8 | Daral Khwar HPS | 36.6 | 3.6 | 3.3 | 79270 | 79270 | 1.85 | 1.33 | 44.33 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 655428.14 | 3823344.6 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-08 | 2025 | 2 | 8 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-08 | 2025 | 2 | 8 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-08 | 2025 | 2 | 8 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-08 | 2025 | 2 | 8 | Reshun HPS | 4.2 | 3.18 | 1.18 | 25000 | 24600 | 1.99 | 1.52 | 50.67 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 331608 | 569718.72 | 400 | outgoing breaker tripping due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-08 | 2025 | 2 | 8 | Shishi HPS | 1.8 | 0.84 | 0.51 | 12210 | 11966 | 2.66 | 0.91 | 30.33 | 2.47 | 88.67 | 49 | 38304 | 94610.88 | 29556.02 | 65054.86 | 244 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-09 | 2025 | 2 | 9 | Daral Khwar HPS | 36.6 | 3.4 | 3.3 | 79110 | 79110 | 1.85 | 1.32 | 44 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 654105.21 | 3824667.53 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-09 | 2025 | 2 | 9 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-09 | 2025 | 2 | 9 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-09 | 2025 | 2 | 9 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-09 | 2025 | 2 | 9 | Reshun HPS | 4.2 | 3.44 | 1.7 | 41000 | 40431 | 2.52 | 2.51 | 83.67 | 13.48 | 84.17 | 45 | 84840 | 1143643.2 | 545009.88 | 598633.32 | 569 | outgoing feeder breaker tripped at 2:35am and remaind off till 8:30am | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-09 | 2025 | 2 | 9 | Shishi HPS | 1.8 | 0.75 | 0.46 | 10920 | 10702 | 2.7 | 0.84 | 28 | 2.47 | 90 | 49 | 38880 | 96033.6 | 26433.94 | 69599.66 | 218 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-10 | 2025 | 2 | 10 | Daral Khwar HPS | 36.6 | 3.4 | 3.27 | 78490 | 78490 | 1.85 | 1.31 | 43.67 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 648978.87 | 3829793.88 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-10 | 2025 | 2 | 10 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-10 | 2025 | 2 | 10 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-10 | 2025 | 2 | 10 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-10 | 2025 | 2 | 10 | Reshun HPS | 4.2 | 2.11 | 1.39 | 28000 | 27440 | 1.99 | 1.71 | 57 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 369891.2 | 531435.52 | 560 | low hydrology, load shedding observed | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-10 | 2025 | 2 | 10 | Shishi HPS | 1.8 | 0.73 | 0.57 | 13800 | 13524 | 2.87 | 0.81 | 27 | 2.47 | 95.67 | 49 | 41328 | 102080.16 | 33404.28 | 68675.88 | 276 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-11 | 2025 | 2 | 11 | Daral Khwar HPS | 36.6 | 3.4 | 3.25 | 78070 | 78070 | 1.85 | 1.31 | 43.67 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 645506.18 | 3833266.56 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-11 | 2025 | 2 | 11 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-11 | 2025 | 2 | 11 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-11 | 2025 | 2 | 11 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Plant completely shutdown since 09/01/25 upon notification of annual canal closure period from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-11 | 2025 | 2 | 11 | Reshun HPS | 4.2 | 2.94 | 1.1 | 25000 | 24540 | 1.99 | 1.52 | 50.67 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 330799.2 | 570527.52 | 460 | Low hydrology and line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-11 | 2025 | 2 | 11 | Shishi HPS | 1.8 | 0.72 | 0.4 | 9720 | 9526 | 2.46 | 0.8 | 26.67 | 2.47 | 82 | 49 | 35424 | 87497.28 | 23529.22 | 63968.06 | 194 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-12 | 2025 | 2 | 12 | Daral Khwar HPS | 36.6 | 3.5 | 3.25 | 78100 | 78100 | 1.85 | 1.31 | 43.67 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 645754.23 | 3833018.51 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-12 | 2025 | 2 | 12 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-12 | 2025 | 2 | 12 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-12 | 2025 | 2 | 12 | Pehur HPS | 18 | 7.3 | 1.3 | 31500 | 30000 | 21 | 4 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 113010 | 1514334 | 1500 | Unit Synchronised with the system at 0910Hrs dated 12/02/25 , Delivering power ,According to the available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-12 | 2025 | 2 | 12 | Reshun HPS | 4.2 | 2.84 | 1.38 | 29000 | 28452 | 1.99 | 1.77 | 59 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 383532.96 | 517793.76 | 548 | due to shortage of water load shedding is observed. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-12 | 2025 | 2 | 12 | Shishi HPS | 1.8 | 0.66 | 0.41 | 9750 | 9555 | 3 | 0.77 | 25.67 | 2.47 | 100 | 49 | 43200 | 106704 | 23600.85 | 83103.15 | 195 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-13 | 2025 | 2 | 13 | Daral Khwar HPS | 36.6 | 3.7 | 2.51 | 60290 | 60290 | 1.85 | 1.01 | 33.67 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 498495.81 | 3980276.94 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-13 | 2025 | 2 | 13 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure by Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-13 | 2025 | 2 | 13 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | 0 | 77.5 | 0 | 0 | 0 | 0 | 0 | The power plant is shutdown due to upper Swat canal annual closure by Irrigation department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-13 | 2025 | 2 | 13 | Pehur HPS | 18 | 7.4 | 5.3 | 128600 | 126000 | 21 | 13 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 474642 | 1152702 | 2600 | Units on bar delivering power to the system, According to available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-13 | 2025 | 2 | 13 | Reshun HPS | 4.2 | 3.04 | 1.43 | 28000 | 27409 | 1.99 | 1.71 | 57 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 369473.32 | 531853.4 | 591 | Tariff rate PESCO's Slab wise prevailing rates starting from basic slab of Rs. 13.48/kwh. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-13 | 2025 | 2 | 13 | Shishi HPS | 1.8 | 0.67 | 0.54 | 12870 | 12613 | 2.67 | 0.76 | 25.33 | 2.47 | 89 | 49 | 38448 | 94966.56 | 31154.11 | 63812.45 | 257 | Less hydrology in winter season | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-14 | 2025 | 2 | 14 | Daral Khwar HPS | 36.6 | 3.5 | 3.44 | 82630 | 82630 | 1.85 | 1.38 | 46 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 683209.63 | 3795563.12 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-14 | 2025 | 2 | 14 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 1 | 3 | 100 | 4.671 | 33.33 | 70 | 20800 | 97156.8 | 0 | 97156.8 | 0 | Weekly canal closure | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-14 | 2025 | 2 | 14 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 8.57 | 0 | 0 | 2.8627 | 33.33 | 77.5 | 648000 | 1855029.6 | 0 | 1855029.6 | 0 | No data submitted for this date | malakand03hpc@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-02-14 | 2025 | 2 | 14 | Pehur HPS | 18 | 6.5 | 6.1 | 146600 | 143000 | 21 | 17 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 538681 | 1088663 | 3600 | Units on bar delivering power to the system, According to available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-14 | 2025 | 2 | 14 | Reshun HPS | 4.2 | 1.89 | 1.12 | 27000 | 26409 | 1.99 | 1.65 | 26.79 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 355993.32 | 545333.4 | 591 | No data submitted for this date | zafar.src@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-02-14 | 2025 | 2 | 14 | Shishi HPS | 1.8 | 0.74 | 0.46 | 11100 | 10878 | 0.82 | 3 | 100 | 2.47 | 27.33 | 49 | 11808 | 29165.76 | 26868.66 | 2297.1 | 222 | The load varies as per the load demand of the local feeder, plain load shedding | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-15 | 2025 | 2 | 15 | Daral Khwar HPS | 36.6 | 3.5 | 3.36 | 80660 | 80660 | 1.85 | 1.35 | 45 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 666921.08 | 3811851.67 | 0 | none | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-15 | 2025 | 2 | 15 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 1 | 3 | 100 | 4.671 | 33.33 | 70 | 20800 | 97156.8 | 0 | 97156.8 | 0 | Weekly canal closure | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-15 | 2025 | 2 | 15 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 17.15 | 0 | 0 | 2.8627 | 66.67 | 77.5 | 1296000 | 3710059.2 | 0 | 3710059.2 | 0 | No data submitted for this date | malakand03hpc@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-02-15 | 2025 | 2 | 15 | Pehur HPS | 18 | 6.4 | 6.02 | 144444 | 141111 | 20.89 | 16.89 | 33.44 | 3.767 | 100 | 41 | 432000 | 1627344 | 531565.14 | 1095778.86 | 3333 | No data submitted for this date | phpcmw18@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-02-15 | 2025 | 2 | 15 | Reshun HPS | 4.2 | 2.93 | 1.31 | 26000 | 25409 | 1.99 | 1.59 | 53 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 342513.32 | 558813.4 | 591 | Tariff rate PESCO's Slab wise prevailing rates starting from basic slab of Rs. 13.48/kwh. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-15 | 2025 | 2 | 15 | Shishi HPS | 1.8 | 0.88 | 0.46 | 10878 | 10878 | 0.96 | 3 | 100 | 2.47 | 32 | 49 | 13824 | 34145.28 | 26868.66 | 7276.62 | 0 | Planned loadshedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-16 | 2025 | 2 | 16 | Daral Khwar HPS | 36.6 | 4 | 3.65 | 87660 | 87660 | 1.85 | 1.47 | 49 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 724799.18 | 3753973.57 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-16 | 2025 | 2 | 16 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 1 | 3 | 100 | 4.671 | 33.33 | 70 | 20800 | 97156.8 | 0 | 97156.8 | 0 | Weekly canal closure | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-16 | 2025 | 2 | 16 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 25.72 | 0 | 0 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 0 | 5565088.8 | 0 | Malakand-III HPC Total shutdown at 09:26am dated 04-01-2025 to carry out major over Hauling of the Units approved by NPCC as per letter No 102-07 GM (SO/scheduled outage 2025) dated 03-01-2025. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-16 | 2025 | 2 | 16 | Pehur HPS | 18 | 6.3 | 5.93 | 142289 | 139222 | 20.78 | 16.78 | 32.94 | 3.767 | 100 | 41 | 432000 | 1627344 | 524449.27 | 1102894.73 | 3067 | No data submitted for this date | phpcmw18@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-02-16 | 2025 | 2 | 16 | Reshun HPS | 4.2 | 1.46 | 1.34 | 29000 | 28411 | 1.43 | 1.4 | 46.67 | 13.48 | 47.67 | 45 | 48048 | 647687.04 | 382980.28 | 264706.76 | 589 | no | aamirsaeed0343@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-16 | 2025 | 2 | 16 | Shishi HPS | 1.8 | 0.74 | 0.5 | 11880 | 11642 | 0.83 | 3 | 100 | 2.47 | 27.67 | 49 | 11952 | 29521.44 | 28755.74 | 765.7 | 238 | Un force loadshedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-17 | 2025 | 2 | 17 | Daral Khwar HPS | 36.6 | 4 | 3.84 | 92050 | 92050 | 1.85 | 1.54 | 51.33 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 761097.02 | 3717675.73 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-17 | 2025 | 2 | 17 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 1 | 3 | 0 | 4.671 | 33.33 | 70 | 20800 | 97156.8 | 0 | 97156.8 | 0 | Weekly canal closure | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-02-17 | 2025 | 2 | 17 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 25.72 | 0 | 0 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 0 | 5565088.8 | 0 | Malakand-III HPC Total shutdown at 09:26am dated 04-01-2025 to carry out major over Hauling of the Units approved by NPCC as per letter No 102-07 GM (SO/scheduled outage 2025) dated 03-01-2025. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-17 | 2025 | 2 | 17 | Pehur HPS | 18 | 6.21 | 5.84 | 140133 | 137333 | 20.67 | 16.67 | 32.44 | 3.767 | 100 | 41 | 432000 | 1627344 | 517333.41 | 1110010.59 | 2800 | No data submitted for this date | phpcmw18@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-02-17 | 2025 | 2 | 17 | Reshun HPS | 4.2 | 2.99 | 1.34 | 27000 | 26409 | 1.99 | 1.65 | 55 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 355993.32 | 545333.4 | 591 | Tariff rate PESCO's Slab wise prevailing rates starting from basic slab of Rs. 13.48/kwh. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-17 | 2025 | 2 | 17 | Shishi HPS | 1.8 | 0.73 | 0.52 | 12390 | 12142 | 0.83 | 3 | 100 | 2.47 | 27.67 | 49 | 11952 | 29521.44 | 29990.74 | -469.3 | 248 | Un force loadshedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-18 | 2025 | 2 | 18 | Daral Khwar HPS | 36.6 | 4 | 3.75 | 90030 | 90030 | 1.85 | 1.51 | 50.33 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 744395.05 | 3734377.7 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-18 | 2025 | 2 | 18 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 1 | 4 | 0 | 4.671 | 33.33 | 70 | 20800 | 97156.8 | 0 | 97156.8 | 0 | Weekly canal closure | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-02-18 | 2025 | 2 | 18 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 25.72 | 0 | 0 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 0 | 5565088.8 | 0 | Not reported | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-18 | 2025 | 2 | 18 | Pehur HPS | 18 | 6.11 | 5.75 | 137978 | 135444 | 20.56 | 16.56 | 31.94 | 3.767 | 100 | 41 | 432000 | 1627344 | 510217.55 | 1117126.45 | 2534 | No data submitted for this date | phpcmw18@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-02-18 | 2025 | 2 | 18 | Reshun HPS | 4.2 | 2.92 | 1.34 | 27000 | 26390 | 1.44 | 1.38 | 46 | 13.48 | 48 | 45 | 48384 | 652216.32 | 355737.2 | 296479.12 | 610 | storage of water at reservoir | aamirsaeed0343@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-18 | 2025 | 2 | 18 | Shishi HPS | 1.8 | 0.7 | 0.35 | 8400 | 8232 | 0.79 | 3 | 100 | 2.47 | 26.33 | 49 | 11376 | 28098.72 | 20333.04 | 7765.68 | 168 | Un force loadshedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-19 | 2025 | 2 | 19 | Daral Khwar HPS | 36.6 | 4 | 3.76 | 90230 | 90230 | 1.85 | 1.51 | 50.33 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 746048.71 | 3732724.04 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-19 | 2025 | 2 | 19 | Machai HPS | 2.6 | 0.81 | 0.03 | 4736 | 4356 | 0 | 16 | 100 | 4.671 | 0 | 70 | 0 | 0 | 20346.88 | -20346.88 | 380 | Unit synchronised at 1418hrs as the inflow has been restored. Unit stopped normally at 1455hrs due to Trash reck choking and resynched at 1522 hrs. Unit stopped normally at 2344 due to low inflow. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-19 | 2025 | 2 | 19 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 25.72 | 0 | 0 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 0 | 5565088.8 | 0 | Unit # 02 Desynchronized from the system at 9:26hrs,Dated 04-01-2025. Malakand-III HPC Total shutdown to carry out major overHauling of the Units approved by NPCC as per letter No 102-07 GM (SO/scheduled outage 2025) dated 03-01-2025. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-19 | 2025 | 2 | 19 | Pehur HPS | 18 | 6.02 | 5.66 | 135822 | 133556 | 20.46 | 16.44 | 31.44 | 3.767 | 100 | 41 | 432000 | 1627344 | 503105.45 | 1124238.55 | 2266 | No data submitted for this date | phpcmw18@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-02-19 | 2025 | 2 | 19 | Reshun HPS | 4.2 | 2.93 | 1.16 | 27000 | 26400 | 1.99 | 1.65 | 55 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 355872 | 545454.72 | 600 | Tariff rate PESCO's Slab wise prevailing rates starting from basic slab of Rs. 13.48/kwh. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-19 | 2025 | 2 | 19 | Shishi HPS | 1.8 | 0.71 | 0.41 | 9870 | 9672 | 0.8 | 3 | 22.85 | 2.47 | 26.5 | 49 | 11448 | 28276.56 | 23889.84 | 4386.72 | 198 | No data submitted for this date | ibrarahmadmkd@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-02-20 | 2025 | 2 | 20 | Daral Khwar HPS | 36.6 | 4.5 | 4.11 | 98710 | 98710 | 1.85 | 1.65 | 55 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 816163.89 | 3662608.85 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-20 | 2025 | 2 | 20 | Machai HPS | 2.6 | 0.99 | 0.55 | 13712 | 13200 | 0 | 14 | 100 | 4.671 | 0 | 70 | 0 | 0 | 61657.2 | -61657.2 | 512 | Unit synchronised at 0815hrs as the inflow has been restored. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-20 | 2025 | 2 | 20 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 25.72 | 0 | 0 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 0 | 5565088.8 | 0 | complex shutdown | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-20 | 2025 | 2 | 20 | Pehur HPS | 18 | 5.92 | 5.57 | 133667 | 131667 | 20.35 | 16.33 | 30.94 | 3.767 | 100 | 41 | 432000 | 1627344 | 495989.59 | 1131354.41 | 2000 | No data submitted for this date | phpcmw18@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-02-20 | 2025 | 2 | 20 | Reshun HPS | 4.2 | 2.23 | 1 | 22000 | 21408 | 1.58 | 1.59 | 53 | 13.48 | 52.67 | 45 | 53088 | 715626.24 | 288579.84 | 427046.4 | 592 | TL fault at Feeder-II | aamirsaeed0343@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-20 | 2025 | 2 | 20 | Shishi HPS | 1.8 | 0.71 | 0.47 | 11340 | 11113 | 0.8 | 3 | 100 | 2.47 | 26.67 | 49 | 11520 | 28454.4 | 27449.11 | 1005.29 | 227 | Power house Off loaded for replacement of T/F on LT line | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-21 | 2025 | 2 | 21 | Daral Khwar HPS | 36.6 | 4 | 3.97 | 95350 | 95350 | 1.85 | 1.59 | 53 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 788382.4 | 3690390.34 | 0 | Not reported | 1973akkhan@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-21 | 2025 | 2 | 21 | Machai HPS | 2.6 | 1.52 | 0.95 | 23080 | 22180 | 0 | 19 | 100 | 4.671 | 0 | 70 | 0 | 0 | 103602.78 | -103602.78 | 900 | Unit tripped at 0348 hrs due to Earth fault , 11KV line restored at 0350 hrs.Unit synchronised at 0359 hrs. Unit stopped normally at 1049 hrs due to PTW#02/2025 while synchronised at 1318 hrs. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-21 | 2025 | 2 | 21 | Malakand-3 HPS | 81 | 4.57 | 4.2 | 100898 | 99580 | 25.72 | 5.39 | 5.19 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 285067.67 | 5280021.13 | 1318 | No data submitted for this date | malakand03hpc@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-02-21 | 2025 | 2 | 21 | Pehur HPS | 18 | 5.83 | 5.48 | 131511 | 129778 | 20.24 | 16.22 | 30.44 | 3.767 | 100 | 41 | 432000 | 1627344 | 488873.73 | 1138470.27 | 1733 | No data submitted for this date | phpcmw18@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-02-21 | 2025 | 2 | 21 | Reshun HPS | 4.2 | 2.8 | 1.29 | 28000 | 27399 | 1.4 | 1.2 | 40 | 13.48 | 46.67 | 45 | 47040 | 634099.2 | 369338.52 | 264760.68 | 601 | Snow at intake side | aamirsaeed0343@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-21 | 2025 | 2 | 21 | Shishi HPS | 1.8 | 0.77 | 0.46 | 11261 | 11040 | 0.85 | 3 | 100 | 2.47 | 28.33 | 49 | 12240 | 30232.8 | 27268.8 | 2964 | 221 | Power house Off loaded for replacement of T/F on LT line | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-22 | 2025 | 2 | 22 | Daral Khwar HPS | 36.6 | 4.3 | 4.19 | 100620 | 100620 | 1.85 | 1.68 | 56 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 831956.35 | 3646816.4 | 0 | Nill | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-22 | 2025 | 2 | 22 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0.5 | 18.5 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Not reported | machai.12333@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load; Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-02-22 | 2025 | 2 | 22 | Malakand-3 HPS | 81 | 19 | 8.41 | 201796 | 199160 | 25.72 | 10.78 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 570135.33 | 4994953.47 | 2636 | unit #02 synchronized with the system at 12:33hrs | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-22 | 2025 | 2 | 22 | Pehur HPS | 18 | 5.73 | 5.39 | 129356 | 127889 | 18.83 | 0 | 29.94 | 3.767 | 100 | 41 | 432000 | 1627344 | 481757.86 | 1145586.14 | 1467 | No data submitted for this date | phpcmw18@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-02-22 | 2025 | 2 | 22 | Reshun HPS | 4.2 | 2.85 | 1.26 | 26000 | 25410 | 1.52 | 1.57 | 52.33 | 13.48 | 50.67 | 45 | 51072 | 688450.56 | 342526.8 | 345923.76 | 590 | Repair of governor-I | aamirsaeed0343@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-22 | 2025 | 2 | 22 | Shishi HPS | 1.8 | 0.77 | 0.46 | 9394 | 9210 | 0.87 | 3 | 100 | 2.47 | 29 | 49 | 12528 | 30944.16 | 22748.7 | 8195.46 | 184 | Power house Off loaded for replacement of T/F on LT line | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-23 | 2025 | 2 | 23 | Daral Khwar HPS | 36.6 | 4.3 | 4.09 | 98200 | 98200 | 1.85 | 1.64 | 54.67 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 811947.06 | 3666825.68 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-23 | 2025 | 2 | 23 | Machai HPS | 2.6 | 1.11 | 0.92 | 22680 | 21732 | 1 | 18 | 100 | 4.671 | 33.33 | 70 | 20800 | 97156.8 | 101510.17 | -4353.37 | 948 | Unit operates normally | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-23 | 2025 | 2 | 23 | Malakand-3 HPS | 81 | 18 | 16.41 | 393840 | 388410 | 25.72 | 10.44 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1111901.31 | 4453187.49 | 5430 | Unit # 01 is on bar whlie Unit # 02,03 kept Standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-23 | 2025 | 2 | 23 | Pehur HPS | 18 | 5.43 | 5.3 | 127200 | 126000 | 20.02 | 16 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 474642 | 1152702 | 1200 | Plant delivering power ,According to available hydrology. | hazrathamza204@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-23 | 2025 | 2 | 23 | Reshun HPS | 4.2 | 3.03 | 1.27 | 28000 | 27380 | 1.99 | 1.71 | 57 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 369082.4 | 532244.32 | 620 | Tariff rate PESCO's Slab wise prevailing rates starting from basic slab of Rs. 13.48/kwh. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-23 | 2025 | 2 | 23 | Shishi HPS | 1.8 | 0.69 | 0.4 | 9547 | 9360 | 0.88 | 3 | 22.1 | 2.47 | 29.17 | 49 | 12600 | 31122 | 23119.2 | 8002.8 | 187 | No data submitted for this date | ibrarahmadmkd@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-02-24 | 2025 | 2 | 24 | Daral Khwar HPS | 36.6 | 4.3 | 4.29 | 102850 | 102850 | 1.85 | 1.72 | 57.33 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 850394.66 | 3628378.09 | 0 | Not reported | 1973akkhan@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-24 | 2025 | 2 | 24 | Machai HPS | 2.6 | 0.95 | 0.84 | 20412 | 19632 | 2 | 15 | 100 | 4.671 | 66.67 | 70 | 41600 | 194313.6 | 91701.07 | 102612.53 | 780 | Unit remained on bar delivering power to National Grid as per available inflow and system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-24 | 2025 | 2 | 24 | Malakand-3 HPS | 81 | 17 | 16.52 | 396407 | 389990 | 25.72 | 11.06 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1116424.37 | 4448664.43 | 6417 | Unit # 01 is on bar while unit # 02 & 03 standby | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-24 | 2025 | 2 | 24 | Pehur HPS | 18 | 5.28 | 5.2 | 125000 | 122000 | 18.83 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 459574 | 1167770 | 3000 | Plant delivering power ,According to available hydrology. | hazrathamza204@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-24 | 2025 | 2 | 24 | Reshun HPS | 4.2 | 2.96 | 1.26 | 27500 | 26870 | 1.56 | 1.5 | 50 | 13.48 | 52 | 45 | 52416 | 706567.68 | 362207.6 | 344360.08 | 630 | no | aamirsaeed0343@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-24 | 2025 | 2 | 24 | Shishi HPS | 1.8 | 0.8 | 0.4 | 9700 | 9510 | 0.88 | 3 | 100 | 2.47 | 29.33 | 49 | 12672 | 31299.84 | 23489.7 | 7810.14 | 190 | Power house Off loaded for replacement of T/F on LT line | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-25 | 2025 | 2 | 25 | Daral Khwar HPS | 36.6 | 6 | 4.88 | 117040 | 117040 | 1.85 | 1.96 | 65.33 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 967721.83 | 3511050.91 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-25 | 2025 | 2 | 25 | Machai HPS | 2.6 | 0.77 | 0.7 | 17032 | 16100 | 2 | 15 | 100 | 4.671 | 66.67 | 70 | 41600 | 194313.6 | 75203.1 | 119110.5 | 932 | Unit remained on the bar delivering the power to the National Grid as per available hydrology and system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-25 | 2025 | 2 | 25 | Malakand-3 HPS | 81 | 20 | 16.6 | 398461 | 391470 | 25.72 | 11.47 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1120661.17 | 4444427.63 | 6991 | Unit # 03 is on bar while unit # 01,02 kept standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-25 | 2025 | 2 | 25 | Pehur HPS | 18 | 5.76 | 3.08 | 74000 | 73000 | 18.83 | 10 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 274991 | 1352353 | 1000 | plant delivering power according to available hydrology. | hazrathamza204@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-25 | 2025 | 2 | 25 | Reshun HPS | 4.2 | 2.82 | 1.3 | 28000 | 27412 | 1.47 | 1.4 | 46.67 | 13.48 | 49 | 45 | 49392 | 665804.16 | 369513.76 | 296290.4 | 588 | no | aamirsaeed0343@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-25 | 2025 | 2 | 25 | Shishi HPS | 1.8 | 0.78 | 0.37 | 9058 | 8880 | 0.86 | 3 | 100 | 2.47 | 28.67 | 49 | 12384 | 30588.48 | 21933.6 | 8654.88 | 178 | Power house Off loaded for replacement of T/F on LT line | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-26 | 2025 | 2 | 26 | Daral Khwar HPS | 36.6 | 9 | 6.79 | 162880 | 162880 | 1.85 | 2.72 | 90.67 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 1346740.7 | 3132032.04 | 0 | Unit No.1 stopped, and Unit No.2 synchronized with the national grid due to increase in hydrology. | 1973akkhan@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-26 | 2025 | 2 | 26 | Machai HPS | 2.6 | 0.9 | 0.57 | 14064 | 13288 | 2 | 15 | 100 | 4.671 | 66.67 | 70 | 41600 | 194313.6 | 62068.25 | 132245.35 | 776 | Unit precautionary shut down at 1149Hrs dated 26-02-2025 due to the drop in head race level .Unit synchronized with the system at 1541Hrs as rated head was restored . | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-26 | 2025 | 2 | 26 | Malakand-3 HPS | 81 | 21 | 17.95 | 430734 | 424020 | 25.72 | 12.63 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1213842.05 | 4351246.75 | 6714 | As per available hydrology from Irrigation Department One Unit at Malakand- III Power House is running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-26 | 2025 | 2 | 26 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.767 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | Power Plant is completely shut down due to zero irrigation demand. | 1973akkhan@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-26 | 2025 | 2 | 26 | Reshun HPS | 4.2 | 1.66 | 0.76 | 18000 | 17418 | 1.99 | 1.1 | 36.67 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 234794.64 | 666532.08 | 582 | Tariff rate PESCO's Slab wise prevailing rates starting from basic slab of Rs. 13.48/kwh. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-26 | 2025 | 2 | 26 | Shishi HPS | 1.8 | 0.71 | 0.36 | 8670 | 8497 | 0.82 | 3 | 100 | 2.47 | 27.33 | 49 | 11808 | 29165.76 | 20987.59 | 8178.17 | 173 | The load varies as per the load demand of the local feeder, plain load shedding | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-27 | 2025 | 2 | 27 | Daral Khwar HPS | 36.6 | 8.3 | 8.21 | 197100 | 197100 | 1.85 | 3.3 | 100 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 1629681.93 | 2849090.81 | 0 | Not reported | 1973akkhan@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-27 | 2025 | 2 | 27 | Machai HPS | 2.6 | 0.95 | 0.28 | 8768 | 8272 | 1 | 15 | 100 | 4.671 | 33.33 | 70 | 20800 | 97156.8 | 38638.51 | 58518.29 | 496 | Unit being on bar delivering power to National Grid as per available water inflow and system conditions, precautionary shut down at 1045Hrs dated 27-02-2025 on the request of GSO staff (Katlang Grid) as PTW issued to Operation staff (PESCO) on KATLANG Grid.11KV Machai-HPS line re-energized at 1616Hrs as PTW canceled by Operation staff (PESCO). Unit synchronized with the system at 1805Hrs and load gradually increased according to available inflow and system condition. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-27 | 2025 | 2 | 27 | Malakand-3 HPS | 81 | 23.43 | 21.57 | 517682 | 517972 | 25.72 | 14.24 | 26.63 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1482798.44 | 4082290.36 | 0 | No data submitted for this date | malakand03hpc@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-02-27 | 2025 | 2 | 27 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | Plant completely shutdown due to nil irrigation demand. | hazrathamza204@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-27 | 2025 | 2 | 27 | Reshun HPS | 4.2 | 2.48 | 1.33 | 54000 | 27000 | 1.99 | 1.65 | 53.57 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 363960 | 537366.72 | 27000 | Tariff rate PESCO's Slab wise prevailing rates starting from basic slab of Rs. 13.48/kwh. | zafar.src@gmail.com | Original | Units = Net + Aux; Plant factor recalculated | Link_Generation_Data_Summary.xlsx
2025-02-27 | 2025 | 2 | 27 | Shishi HPS | 1.8 | 0.74 | 0.39 | 9330 | 8670 | 0.84 | 3 | 100 | 2.47 | 28 | 49 | 12096 | 29877.12 | 21414.9 | 8462.22 | 660 | The load varies as per the load demand of the local feeder, plain load shedding | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-28 | 2025 | 2 | 28 | Daral Khwar HPS | 36.6 | 8 | 7.68 | 184250 | 124250 | 1.85 | 3.08 | 100 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 1027336.28 | 3451436.47 | 60000 | Not reported | 1973akkhan@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-28 | 2025 | 2 | 28 | Machai HPS | 2.6 | 1.05 | 0.7 | 17140 | 16324 | 2 | 15 | 100 | 4.671 | 66.67 | 70 | 41600 | 194313.6 | 76249.4 | 118064.2 | 816 | Not reported | 1973akkhan@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-28 | 2025 | 2 | 28 | Malakand-3 HPS | 81 | 27 | 25.5 | 604630 | 611924 | 25.72 | 15.84 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1751754.84 | 3813333.96 | 7294 | As per available hydrology from Irrigation Department Two Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original | CHECK: Net > Units (source me verify karein) | Link_Generation_Data_Summary.xlsx
2025-02-28 | 2025 | 2 | 28 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 18 | 2.33 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | Power Plant is completely shut down due to zero irrigation demand. | 1973akkhan@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load; Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-02-28 | 2025 | 2 | 28 | Reshun HPS | 4.2 | 2.54 | 1312 | 27000 | 26418 | 1.67 | 1.58 | 52.67 | 13.48 | 55.67 | 45 | 56112 | 756389.76 | 356114.64 | 400275.12 | 582 | Breaker tripped twice due to line fault | aamirsaeed0343@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-02-28 | 2025 | 2 | 28 | Shishi HPS | 1.8 | 0.76 | 0.38 | 9000 | 8670 | 0.86 | 3 | 100 | 2.47 | 28.67 | 49 | 12384 | 30588.48 | 21414.9 | 9173.58 | 330 | The load varies as per the load demand of the local feeder, plain load shedding | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-01 | 2025 | 3 | 1 | Daral Khwar HPS | 36.6 | 7.5 | 6.95 | 166780 | 166780 | 4.76 | 2.79 | 93 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1378987.07 | 5883887.65 | 0 | Not reported | 1973akkhan@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-01 | 2025 | 3 | 1 | Machai HPS | 2.6 | 0.98 | 0.91 | 22728 | 21916 | 16.2 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 102369.64 | 189100.76 | 812 | Unit remained on bar delivering power to National Grid as per available inflow and system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-01 | 2025 | 3 | 1 | Malakand-3 HPS | 81 | 25 | 23.73 | 569634 | 563390 | 47.34 | 15.01 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1612816.55 | 3952272.25 | 6244 | As per available hydrology from Irrigation Department One Unit at Malakand- III Power House is running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-01 | 2025 | 3 | 1 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 18 | 4.67 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | No data submitted for this date | phpcmw18@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-03-01 | 2025 | 3 | 1 | Reshun HPS | 4.2 | 3.02 | 1.22 | 28000 | 27409 | 1.41 | 1.71 | 57.13 | 13.48 | 47 | 45 | 47376 | 638628.48 | 369473.32 | 269155.16 | 591 | (I) Low Hydrology, (II) Line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-01 | 2025 | 3 | 1 | Shishi HPS | 1.8 | 0.83 | 0.4 | 9486 | 9300 | 0.95 | 3 | 100 | 2.47 | 31.67 | 49 | 13680 | 33789.6 | 22971 | 10818.6 | 186 | Force loadshedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-02 | 2025 | 3 | 2 | Daral Khwar HPS | 36.6 | 6.5 | 6.3 | 151140 | 151140 | 4.76 | 2.53 | 84.33 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1249670.86 | 6013203.86 | 0 | Not reported | 1973akkhan@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-02 | 2025 | 3 | 2 | Machai HPS | 2.6 | 1.2 | 0.77 | 19708 | 19092 | 16.2 | 16 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 89178.73 | 202291.67 | 616 | 1. The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 0948Hrs dated 02.03.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault.Unit synchronized with the system at 1032Hrs as 11KV Machai-HPS line energized at 0953Hrs . 2. The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 1657Hrs dated 02.03.2025 due to the tripping of 11KV Machai-HPS feeder as 132KV line Mardan tripped.Unit synchronized with the system at 1742Hrs as 11KV Machai-HPS line energized at 1732Hrs . | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-02 | 2025 | 3 | 2 | Malakand-3 HPS | 81 | 23 | 21.86 | 524585 | 518990 | 47.34 | 13.97 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1485712.67 | 4079376.13 | 5595 | As per available hydrology from Irrigation Department One Unit at Malakand- III Power House is running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-02 | 2025 | 3 | 2 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 18 | 7 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | Power Plant is completely shut down due to zero irrigation demand. | 1973akkhan@gmail.com | Original | Net = Units - Aux; Avg load = Units / 24h; Max load estimated from Avg load; Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-03-02 | 2025 | 3 | 2 | Reshun HPS | 4.2 | 2.68 | 1.04 | 24000 | 23420 | 1.41 | 1.47 | 48.97 | 13.48 | 47 | 45 | 47376 | 638628.48 | 315701.6 | 322926.88 | 580 | Line faults and shortage of water. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-02 | 2025 | 3 | 2 | Shishi HPS | 1.8 | 0.87 | 0.42 | 10220 | 10020 | 0.93 | 3 | 100 | 2.47 | 31 | 49 | 13392 | 33078.24 | 24749.4 | 8328.84 | 200 | The load varies as per the load demand of the local feeder, plain load shedding | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-03 | 2025 | 3 | 3 | Daral Khwar HPS | 36.6 | 6.9 | 6.13 | 147160 | 147160 | 4.76 | 2.46 | 82 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1216763.03 | 6046111.69 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-03 | 2025 | 3 | 3 | Machai HPS | 2.6 | 1.18 | 0.95 | 23684 | 22836 | 16.1 | 15.5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 106666.96 | 184803.44 | 848 | The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 1700Hrs dated 03.03.2025 due to the tripping of 11KV Machai-HPS feeder as 132KV line Mardan tripped.Unit synchronized with the system at 1721Hrs as 11KV Machai-HPS line energized at 1704Hrs . | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-03 | 2025 | 3 | 3 | Malakand-3 HPS | 81 | 25 | 22.34 | 536231 | 529580 | 47.34 | 14.32 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1516028.67 | 4049060.13 | 6651 | As per available hydrology from Irrigation Department One Unit at Malakand- III Power House is running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-03 | 2025 | 3 | 3 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 18 | 9.33 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | Power Plant is completely shut down due to zero irrigation demand | 1973akkhan@gmail.com | Original | Net = Units - Aux; Avg load = Units / 24h; Max load estimated from Avg load; Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-03-03 | 2025 | 3 | 3 | Reshun HPS | 4.2 | 3.17 | 1.14 | 25000 | 24412 | 1.41 | 1.53 | 51 | 13.48 | 47 | 45 | 47376 | 638628.48 | 329073.76 | 309554.72 | 588 | (I). Shortage of Water, Line faults (II)Tariff rate PESCO's Slab wise prevailing rates starting from basic slab of Rs. 13.48/kwh. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-03 | 2025 | 3 | 3 | Shishi HPS | 1.8 | 0.74 | 0.39 | 9302 | 9120 | 0.84 | 3 | 100 | 2.47 | 28 | 49 | 12096 | 29877.12 | 22526.4 | 7350.72 | 182 | Un force loadshedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-04 | 2025 | 3 | 4 | Daral Khwar HPS | 36.6 | 6 | 5.57 | 133600 | 133600 | 4.76 | 2.23 | 74.33 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1104644.88 | 6158229.84 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-04 | 2025 | 3 | 4 | Machai HPS | 2.6 | 1.07 | 0.92 | 23440 | 22484 | 16.1 | 15.5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 105022.76 | 186447.64 | 956 | Unit remained on bar delivering power to National Grid as per available inflow and system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-04 | 2025 | 3 | 4 | Malakand-3 HPS | 81 | 25 | 22.8 | 547132 | 540620 | 47.34 | 14.75 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1547632.87 | 4017455.93 | 6512 | As per available hydrology from Irrigation Department One Unit at Malakand- III Power House is running | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-04 | 2025 | 3 | 4 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 18 | 11.67 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | Power Plant is completely shut down due to zero irrigation demand. | 1973akkhan@gmail.com | Original | Net = Units - Aux; Avg load = Units / 24h; Max load estimated from Avg load; Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-03-04 | 2025 | 3 | 4 | Reshun HPS | 4.2 | 3.35 | 1.49 | 29000 | 28402 | 1.99 | 1.77 | 59 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 382858.96 | 518467.76 | 598 | Load shedding due to low hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-04 | 2025 | 3 | 4 | Shishi HPS | 1.8 | 0.76 | 0.31 | 7466 | 7320 | 0.85 | 3 | 100 | 2.47 | 28.33 | 49 | 12240 | 30232.8 | 18080.4 | 12152.4 | 146 | Un force loadshedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-05 | 2025 | 3 | 5 | Daral Khwar HPS | 36.6 | 5.8 | 5.48 | 131620 | 131620 | 4.76 | 2.2 | 73.33 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1088273.65 | 6174601.07 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-05 | 2025 | 3 | 5 | Machai HPS | 2.6 | 1.39 | 1.08 | 25852 | 25036 | 16.2 | 16.6 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 116943.16 | 174527.24 | 816 | The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 1731Hrs dated 05.03.2025 due to the tripping of 11KV Machai-HPS feeder as 132KV line Mardan tripped.Unit synchronized with the system at 1756Hrs as 11KV Machai-HPS line energized at 1734Hrs . | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-05 | 2025 | 3 | 5 | Malakand-3 HPS | 81 | 22 | 20.19 | 484473 | 478430 | 47.34 | 13.31 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1369601.56 | 4195487.24 | 6043 | As per available hydrology from Irrigation Department One Unit at Malakand- III Power House is running | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-05 | 2025 | 3 | 5 | Pehur HPS | 18 | 5.13 | 4.8 | 117500 | 115000 | 18 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 433205 | 1194139 | 2500 | Plant delivering power, According to available hydrology | hazrathamza204@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-05 | 2025 | 3 | 5 | Reshun HPS | 4.2 | 3.2 | 1.27 | 26000 | 25317 | 1.41 | 1.59 | 53.03 | 13.48 | 47 | 45 | 47376 | 638628.48 | 341273.16 | 297355.32 | 683 | shortage of water | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-05 | 2025 | 3 | 5 | Shishi HPS | 1.8 | 0.72 | 0.51 | 12240 | 12000 | 0.81 | 3 | 100 | 2.47 | 27 | 49 | 11664 | 28810.08 | 29640 | -829.92 | 240 | The load varies as per the load demand of the local feeder, plain load shedding | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-06 | 2025 | 3 | 6 | Daral Khwar HPS | 36.6 | 7 | 5.82 | 139660 | 139660 | 4.76 | 2.34 | 78 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1154750.78 | 6108123.94 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-06 | 2025 | 3 | 6 | Machai HPS | 2.6 | 1.34 | 0.94 | 22528 | 21604 | 16.2 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 100912.28 | 190558.12 | 924 | The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 1733Hrs dated 06.03.2025 due to the tripping of 11KV Machai-HPS feeder as 132KV line Mardan tripped.Unit synchronized with the system at 1757Hrs as 11KV Machai-HPS line energized at 1742Hrs . | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-06 | 2025 | 3 | 6 | Malakand-3 HPS | 81 | 21 | 19.27 | 462488 | 456720 | 47.34 | 12.7 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1307452.34 | 4257636.46 | 5768 | As per available hydrology from Irrigation Department One Unit at Malakand- III Power House is running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-06 | 2025 | 3 | 6 | Pehur HPS | 18 | 4.81 | 4.53 | 108617 | 106333 | 19.52 | 13 | 25.14 | 3.767 | 100 | 41 | 432000 | 1627344 | 400556.41 | 1226787.59 | 2284 | No data submitted for this date | phpcmw18@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-03-06 | 2025 | 3 | 6 | Reshun HPS | 4.2 | 3.24 | 1.31 | 25000 | 24404 | 1.41 | 1.53 | 51 | 13.48 | 47 | 45 | 47376 | 638628.48 | 328965.92 | 309662.56 | 596 | (I)Low Hydrology. (II)Tariff rate PESCO's Slab wise prevailing rates starting from basic slab of Rs. 13.48/kwh. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-06 | 2025 | 3 | 6 | Shishi HPS | 1.8 | 0.75 | 0.37 | 8905 | 8730 | 0.84 | 3 | 100 | 2.47 | 28 | 49 | 12096 | 29877.12 | 21563.1 | 8314.02 | 175 | Power house Off loaded for replacement of T/F on LT line | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-07 | 2025 | 3 | 7 | Daral Khwar HPS | 36.6 | 7.5 | 6.84 | 164270 | 164270 | 4.76 | 2.75 | 91.67 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1358233.64 | 5904641.08 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-07 | 2025 | 3 | 7 | Machai HPS | 2.6 | 1.25 | 0.71 | 18300 | 17600 | 16.2 | 15.5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 82209.6 | 209260.8 | 700 | The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 1553Hrs and 1849Hrs dated 07.03.2025 due to the tripping of 11KV Machai-HPS feeder as 132KV line Mardan tripped.Unit synchronized with the system at 1621Hrs and 2009Hrs respectively as 11KV Machai-HPS line energized at 1556Hrs and 1913Hrs . | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-07 | 2025 | 3 | 7 | Malakand-3 HPS | 81 | 24 | 21.12 | 506970 | 501370 | 47.34 | 13.74 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1435271.9 | 4129816.9 | 5600 | Unit # 01 is on bar while Unit # 02,03 | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-07 | 2025 | 3 | 7 | Pehur HPS | 18 | 4.42 | 4.16 | 99733 | 97667 | 21.03 | 12 | 23.09 | 3.767 | 100 | 41 | 432000 | 1627344 | 367911.59 | 1259432.41 | 2066 | No data submitted for this date | phpcmw18@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-03-07 | 2025 | 3 | 7 | Reshun HPS | 4.2 | 3.24 | 1.22 | 25000 | 24400 | 1.41 | 1.53 | 51 | 13.48 | 47 | 45 | 47376 | 638628.48 | 328912 | 309716.48 | 600 | Low Hydrology | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-07 | 2025 | 3 | 7 | Shishi HPS | 1.8 | 0.71 | 0.43 | 10251 | 10050 | 0.81 | 3 | 100 | 2.47 | 27 | 49 | 11664 | 28810.08 | 24823.5 | 3986.58 | 201 | The load varies as per the load demand of the local feeder, plain load shedding | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-08 | 2025 | 3 | 8 | Daral Khwar HPS | 36.6 | 9 | 7.22 | 173190 | 173190 | 4.76 | 2.9 | 96.67 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1431986.88 | 5830887.84 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-08 | 2025 | 3 | 8 | Machai HPS | 2.6 | 1.26 | 1.12 | 26608 | 25784 | 16.2 | 17.1 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 120437.06 | 171033.34 | 824 | The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 1802Hrs dated 08.03.2025 due to the tripping of 11KV Machai-HPS feeder as 132KV line Mardan tripped.Unit synchronized with the system at 1816Hrs as 11KV Machai-HPS line energized at 1810Hrs . | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-08 | 2025 | 3 | 8 | Malakand-3 HPS | 81 | 23 | 21.3 | 511113 | 505510 | 47.34 | 13.95 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1447123.48 | 4117965.32 | 5603 | Unit # 01 is bar while Unit # 02,03 kept standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-08 | 2025 | 3 | 8 | Pehur HPS | 18 | 4.03 | 3.79 | 90850 | 89000 | 22.55 | 11 | 21.03 | 3.767 | 100 | 41 | 432000 | 1627344 | 335263 | 1292081 | 1850 | No data submitted for this date | phpcmw18@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-03-08 | 2025 | 3 | 8 | Reshun HPS | 4.2 | 3.13 | 1.06 | 23000 | 22411 | 1.41 | 1.5 | 49.93 | 13.48 | 47 | 45 | 47376 | 638628.48 | 302100.28 | 336528.2 | 589 | (I). outgoing breaker tripping (II) low hydrology | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-08 | 2025 | 3 | 8 | Shishi HPS | 1.8 | 0.86 | 0.35 | 8354 | 8190 | 0.94 | 3 | 100 | 2.47 | 31.33 | 49 | 13536 | 33433.92 | 20229.3 | 13204.62 | 164 | Un force loadshedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-09 | 2025 | 3 | 9 | Daral Khwar HPS | 36.6 | 9 | 7.89 | 189410 | 189410 | 4.76 | 3.17 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1566098.7 | 5696776.02 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-09 | 2025 | 3 | 9 | Machai HPS | 2.6 | 1.18 | 0.55 | 14916 | 14344 | 16.2 | 16 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 67000.82 | 224469.58 | 572 | 1.Unit being on bar delivering power to National Grid as per available water inflow and system conditions, precautionary shut down at 0946Hrs dated 09-03-2025 on the request of GSO staff (Katlang Grid) as PTW#557 was issued to Operation staff (PESCO) on KATLANG Grid.11KV Machai-HPS line re-energized at 1123Hrs as PTW canceled by Operation staff (PESCO). Unit synchronized with the system at 1200Hrs and load gradually increased according to available inflow and system condition. 2.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 1416Hrs and 2102Hrs dated 09.03.2025 due to the tripping of 11KV Machai-HPS feeder as 132KV line Mardan tripped.Unit synchronized with the system at 1502Hrs and 2150Hrs respectively as 11KV Machai-HPS line energized at 1434Hrs and 2142Hrs. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-09 | 2025 | 3 | 9 | Malakand-3 HPS | 81 | 25 | 21.84 | 524138 | 524138 | 47.34 | 14.26 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1500449.85 | 4064638.95 | 0 | As per available hydrology from Irrigation Department One Unit at Malakand- III Power House is running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-09 | 2025 | 3 | 9 | Pehur HPS | 18 | 3.63 | 3.42 | 81967 | 80333 | 24.07 | 10 | 18.97 | 3.767 | 100 | 41 | 432000 | 1627344 | 302614.41 | 1324729.59 | 1634 | No data submitted for this date | phpcmw18@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-03-09 | 2025 | 3 | 9 | Reshun HPS | 4.2 | 3.2 | 1.32 | 26000 | 25414 | 1.41 | 1.59 | 53.03 | 13.48 | 47 | 45 | 47376 | 638628.48 | 342580.72 | 296047.76 | 586 | Low hydrology and outgoing Breaker Line fault | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-09 | 2025 | 3 | 9 | Shishi HPS | 1.8 | 0.84 | 0.41 | 9823 | 9630 | 0.91 | 3 | 100 | 2.47 | 30.33 | 49 | 13104 | 32366.88 | 23786.1 | 8580.78 | 193 | The load varies as per the load demand of the local feeder, plain load shedding | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-10 | 2025 | 3 | 10 | Daral Khwar HPS | 36.6 | 11.5 | 9.23 | 221420 | 221420 | 4.76 | 3.7 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1830766.99 | 5432107.73 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-10 | 2025 | 3 | 10 | Machai HPS | 2.6 | 1.29 | 1 | 25052 | 24288 | 16.2 | 16.1 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 113449.25 | 178021.15 | 764 | The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 1650Hrs dated 10.03.2025 due to the tripping of 11KV Machai-HPS feeder as 132KV line Mardan tripped.Unit synchronized with the system at 1706Hrs as 11KV Machai-HPS line energized at 1701Hrs. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-10 | 2025 | 3 | 10 | Malakand-3 HPS | 81 | 25 | 23.39 | 561328 | 555220 | 47.34 | 15.47 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1589428.29 | 3975660.51 | 6108 | As per available hydrology from Irrigation Department One Unit at Malakand- III Power House is running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-10 | 2025 | 3 | 10 | Pehur HPS | 18 | 3.24 | 3.05 | 73083 | 71667 | 25.58 | 9 | 16.92 | 3.767 | 100 | 41 | 432000 | 1627344 | 269969.59 | 1357374.41 | 1416 | No data submitted for this date | phpcmw18@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-03-10 | 2025 | 3 | 10 | Reshun HPS | 4.2 | 3.13 | 1.17 | 26000 | 25418 | 1.41 | 1.59 | 53.03 | 13.48 | 47 | 45 | 47376 | 638628.48 | 342634.64 | 295993.84 | 582 | (I). Outgoing Breaker tripped 02 time due to line fault (II) Low hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-10 | 2025 | 3 | 10 | Shishi HPS | 1.8 | 0.78 | 0.44 | 10526 | 10320 | 0.86 | 3 | 100 | 2.47 | 28.67 | 49 | 12384 | 30588.48 | 25490.4 | 5098.08 | 206 | The load varies as per the load demand of the local feeder, plain load shedding | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-11 | 2025 | 3 | 11 | Daral Khwar HPS | 36.6 | 11.4 | 10.4 | 249590 | 249590 | 4.76 | 4.17 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2063685 | 5199189.72 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-11 | 2025 | 3 | 11 | Machai HPS | 2.6 | 1.27 | 1.08 | 26336 | 25432 | 16.2 | 17 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 118792.87 | 172677.53 | 904 | Unit remained on bar delivering the power to National Grid as per available inflow and system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-11 | 2025 | 3 | 11 | Malakand-3 HPS | 81 | 25 | 21.61 | 518655 | 518655 | 47.34 | 14.43 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1484753.67 | 4080335.13 | 0 | Not reported | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-11 | 2025 | 3 | 11 | Pehur HPS | 18 | 5.04 | 2.67 | 64200 | 63000 | 27.1 | 8 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 237321 | 1390023 | 1200 | plant remained operational since 1253 hrs | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-11 | 2025 | 3 | 11 | Reshun HPS | 4.2 | 3.08 | 1.2 | 26000 | 25419 | 1.41 | 1.59 | 53.03 | 13.48 | 47 | 45 | 47376 | 638628.48 | 342648.12 | 295980.36 | 581 | Low hydrology, | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-11 | 2025 | 3 | 11 | Shishi HPS | 1.8 | 0.72 | 0.43 | 10312 | 10110 | 0.81 | 3 | 100 | 2.47 | 27 | 49 | 11664 | 28810.08 | 24971.7 | 3838.38 | 202 | The load varies as per the load demand of the local feeder, plain load shedding | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-12 | 2025 | 3 | 12 | Daral Khwar HPS | 36.6 | 13.5 | 12.11 | 290670 | 290670 | 4.76 | 4.86 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2403346.76 | 4859527.96 | 0 | Unit No.02, on bar delivering load according to available hydrology | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-12 | 2025 | 3 | 12 | Jabori HPS | 10.2 | 5 | 5 | 212750 | 212250 | 6.7 | 6.93 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 1211777.7 | 185834.46 | 500 | The O&M team is carrying out restricted operation of the plant due to severe issues both in SCADA and local control.PD Jabori has already been informed about the exact status of the plant but till now no representative from EPC Contractor or Management Consultant reached at site. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median | Link_Generation_Data_Summary.xlsx
2025-03-12 | 2025 | 3 | 12 | Machai HPS | 2.6 | 1.2 | 0.92 | 21736 | 20944 | 16.2 | 15.6 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 97829.42 | 193640.98 | 792 | Unit being on bar delivering power to National Grid as per available water inflow and system conditions, precautionary shut down at 1302Hrs dated 12-03-2025 on the request of GSO staff (Katlang Grid) as PTW was issued to Operation staff (PESCO) on KATLANG Grid. Unit synchronized with the system at 1456Hrs as 11KV Machai-HPS line re-energized and load gradually increased according to available inflow and system condition. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-12 | 2025 | 3 | 12 | Malakand-3 HPS | 81 | 22 | 21.06 | 505413 | 499560 | 47.34 | 14.28 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1430090.41 | 4134998.39 | 5853 | As per available hydrology from Irrigation Department One Unit at Malakand- III Power House is running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-12 | 2025 | 3 | 12 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 16.35 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | Plant remained shut down due to nil irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-12 | 2025 | 3 | 12 | Reshun HPS | 4.2 | 2.13 | 1.21 | 25000 | 24390 | 1.41 | 1.53 | 51 | 13.48 | 47 | 45 | 47376 | 638628.48 | 328777.2 | 309851.28 | 610 | Load shedding due to low hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-12 | 2025 | 3 | 12 | Shishi HPS | 1.8 | 0.64 | 0.39 | 9272 | 9090 | 0.77 | 3 | 100 | 2.47 | 25.67 | 49 | 11088 | 27387.36 | 22452.3 | 4935.06 | 182 | The load varies as per the load demand of the local feeder, plain load shedding | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-13 | 2025 | 3 | 13 | Daral Khwar HPS | 36.6 | 12.5 | 11.51 | 276230 | 276230 | 4.76 | 4.62 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2283952.51 | 4978922.21 | 0 | Nil | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-13 | 2025 | 3 | 13 | Jabori HPS | 10.2 | 7 | 4.84 | 118570 | 116070 | 6.7 | 3.79 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 662666.84 | 734945.32 | 2500 | The O&M team is carrying out restricted operation of the plant due to severe issues both in SCADA and local control.PD Jabori has already been informed about the exact status of the plant but till now no representative from EPC Contractor or Management Consultant reached at site. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median | Link_Generation_Data_Summary.xlsx
2025-03-13 | 2025 | 3 | 13 | Machai HPS | 2.6 | 1.12 | 0.95 | 23092 | 22264 | 16.2 | 16 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 103995.14 | 187475.26 | 828 | The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 0712Hrs,1729Hr and 1751Hrs dated 13.03.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault.Unit synchronized with the system at 0731Hrs,1746Hr and 1759Hrs respectively as 11KV Machai-HPS line energized at 0718Hrs,1739Hr and 1754Hrs. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-13 | 2025 | 3 | 13 | Malakand-3 HPS | 81 | 24 | 21.17 | 508146 | 502370 | 47.34 | 14.88 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1438134.6 | 4126954.2 | 5776 | As per available hydrology from Irrigation Department One Unit at Malakand- III Power House is running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-13 | 2025 | 3 | 13 | Pehur HPS | 18 | 5.08 | 5 | 41000 | 39000 | 16.35 | 6 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 146913 | 1480431 | 2000 | Plant remained shut down till 1546 hrs, due to nil irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-13 | 2025 | 3 | 13 | Reshun HPS | 4.2 | 2.81 | 1.3 | 27000 | 26390 | 1.41 | 1.65 | 55 | 13.48 | 47 | 45 | 47376 | 638628.48 | 355737.2 | 282891.28 | 610 | due to low inflow of water load shedding is observed. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-13 | 2025 | 3 | 13 | Shishi HPS | 1.8 | 0.56 | 0.4 | 9547 | 9360 | 0.68 | 3 | 100 | 2.47 | 22.67 | 49 | 9792 | 24186.24 | 23119.2 | 1067.04 | 187 | Un force loadshedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-14 | 2025 | 3 | 14 | Daral Khwar HPS | 36.6 | 11.2 | 10.39 | 249260 | 249260 | 4.76 | 4.17 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2060956.46 | 5201918.26 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-14 | 2025 | 3 | 14 | Jabori HPS | 10.2 | 7 | 5.32 | 130070 | 127570 | 6.7 | 4.17 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 728322.64 | 669289.52 | 2500 | The O&M team is carrying out restricted operation of the plant due to severe issues both in SCADA and local control.PD Jabori has already been informed about the exact status of the plant but till now no representative from EPC Contractor or Management Consultant reached at site. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median | Link_Generation_Data_Summary.xlsx
2025-03-14 | 2025 | 3 | 14 | Machai HPS | 2.6 | 1.12 | 0.89 | 21220 | 20416 | 16.2 | 15.5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 95363.14 | 196107.26 | 804 | Unit remained on bar delivering the power to National Grid as per available inflow and system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-14 | 2025 | 3 | 14 | Malakand-3 HPS | 81 | 24 | 21.22 | 509342 | 503810 | 47.34 | 14.06 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1442256.89 | 4122831.91 | 5532 | As per available hydrology from Irrigation Department One Unit at Malakand- III Power House is running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-14 | 2025 | 3 | 14 | Pehur HPS | 18 | 5.13 | 5.03 | 120800 | 119000 | 16.35 | 16 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 448273 | 1179071 | 1800 | Plant remained operational throughout 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-14 | 2025 | 3 | 14 | Reshun HPS | 4.2 | 3.07 | 1.25 | 26000 | 25404 | 1.41 | 1.59 | 53.03 | 13.48 | 47 | 45 | 47376 | 638628.48 | 342445.92 | 296182.56 | 596 | Low hydrology/load shedding | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-14 | 2025 | 3 | 14 | Shishi HPS | 1.8 | 0.66 | 0.39 | 9333 | 9150 | 0.79 | 3 | 100 | 2.47 | 26.33 | 49 | 11376 | 28098.72 | 22600.5 | 5498.22 | 183 | Power house Off loaded for replacement of T/F on LT line | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-15 | 2025 | 3 | 15 | Daral Khwar HPS | 36.6 | 9.7 | 9.14 | 219260 | 219260 | 4.76 | 3.67 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1812907.46 | 5449967.26 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-15 | 2025 | 3 | 15 | Jabori HPS | 10.2 | 7.5 | 5.1 | 124780 | 122280 | 6.7 | 3.99 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 698120.98 | 699491.18 | 2500 | Plant is in Operation as per available hydrology via manual control as both SCADA and remote control of both units not working.EPC Contractor and Management Consultant representatives may kindly be directed to reach site and rectify issues in SACDA and remote control. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with overall median | Link_Generation_Data_Summary.xlsx
2025-03-15 | 2025 | 3 | 15 | Machai HPS | 2.6 | 1.24 | 1.12 | 26812 | 26044 | 16.2 | 17 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 121651.52 | 169818.88 | 768 | The Unit remained on bar delivering the power to National Grid as per available inflow and system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-15 | 2025 | 3 | 15 | Malakand-3 HPS | 81 | 24 | 22.53 | 540726 | 535150 | 47.34 | 14.68 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1531973.9 | 4033114.9 | 5576 | As per available hydrology from Irrigation Department One Unit at Malakand- III Power House is running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-15 | 2025 | 3 | 15 | Pehur HPS | 18 | 5.1 | 5.03 | 120700 | 120700 | 16.35 | 16 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 454676.9 | 1172667.1 | 0 | plant remained operational as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-15 | 2025 | 3 | 15 | Reshun HPS | 4.2 | 3.11 | 1.1 | 23000 | 22410 | 1.41 | 1.41 | 46.93 | 13.48 | 47 | 45 | 47376 | 638628.48 | 302086.8 | 336541.68 | 590 | load shedding has been observed due to low hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-15 | 2025 | 3 | 15 | Shishi HPS | 1.8 | 0.88 | 0.43 | 10220 | 10020 | 0.95 | 3 | 100 | 2.47 | 31.67 | 49 | 13680 | 33789.6 | 24749.4 | 9040.2 | 200 | The load varies as per the load demand of the local feeder, plain load shedding | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-16 | 2025 | 3 | 16 | Daral Khwar HPS | 36.6 | 11.5 | 9.51 | 228270 | 228270 | 4.76 | 3.82 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1887404.84 | 5375469.88 | 0 | 1: Unit No. 02 was on bar delivering an average load equal to 9.51 MW according to available hydrology. 2: Unit No. 01 and 03 standby due to low hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-16 | 2025 | 3 | 16 | Jabori HPS | 10.2 | 7.4 | 4.92 | 120480 | 117980 | 6.7 | 3.85 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 673571.42 | 724040.74 | 2500 | The O&M team is carrying out restricted operation of the plant due to severe issues both in SCADA and local control.PD Jabori has already been informed about the exact status of the plant but till now no representative from EPC Contractor or Management Consultant reached at site. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median | Link_Generation_Data_Summary.xlsx
2025-03-16 | 2025 | 3 | 16 | Machai HPS | 2.6 | 1.15 | 1.05 | 25704 | 24820 | 16.2 | 16.7 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 115934.22 | 175536.18 | 884 | Unit remained on bar delivering the power to National Grid as per available inflow and system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-16 | 2025 | 3 | 16 | Malakand-3 HPS | 81 | 24 | 21.39 | 513332 | 508180 | 47.34 | 14.52 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1454766.89 | 4110321.91 | 5152 | As per available hydrology from Irrigation Department One Unit at Malakand- III Power House is running. | malakand03hpc@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-03-16 | 2025 | 3 | 16 | Pehur HPS | 18 | 5.13 | 5.03 | 120600 | 119000 | 16.35 | 16 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 448273 | 1179071 | 1600 | Plant remained operational throughout 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-16 | 2025 | 3 | 16 | Reshun HPS | 4.2 | 3.24 | 1.21 | 24000 | 23398 | 1.41 | 1.47 | 48.97 | 13.48 | 47 | 45 | 47376 | 638628.48 | 315405.04 | 323223.44 | 602 | Load shedding/storage of water. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-16 | 2025 | 3 | 16 | Shishi HPS | 1.8 | 0.67 | 0.38 | 9211 | 9030 | 0.78 | 3 | 100 | 2.47 | 26 | 49 | 11232 | 27743.04 | 22304.1 | 5438.94 | 181 | Un force loadshedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-17 | 2025 | 3 | 17 | Daral Khwar HPS | 36.6 | 12.3 | 10.64 | 255450 | 255450 | 4.76 | 4.27 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2112137.24 | 5150737.49 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-17 | 2025 | 3 | 17 | Jabori HPS | 10.2 | 8 | 5.39 | 131930 | 129430 | 6.7 | 4.23 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 738941.76 | 658670.4 | 2500 | The O&M team is carrying out restricted operation of the plant due to severe issues both in SCADA and local control.PD Jabori has already been informed about the exact status of the plant but till now no representative from EPC Contractor or Management Consultant reached at site. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median | Link_Generation_Data_Summary.xlsx
2025-03-17 | 2025 | 3 | 17 | Machai HPS | 2.6 | 0.96 | 0.76 | 18548 | 17776 | 16.2 | 16 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 83031.7 | 208438.7 | 772 | The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 1740Hrs dated 17.03.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault.Unit synchronized with the system at 1804Hrs as 11KV Machai-HPS line energized at 1757Hrs. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-17 | 2025 | 3 | 17 | Malakand-3 HPS | 81 | 24 | 21.5 | 515961 | 510650 | 47.34 | 14.6 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1461837.76 | 4103251.04 | 5311 | As per available hydrology from Irrigation Department One Unit at Malakand- III Power House is running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-17 | 2025 | 3 | 17 | Pehur HPS | 18 | 5.15 | 4.9 | 118600 | 116000 | 16.35 | 16 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 436972 | 1190372 | 2600 | Plant operational 24 hrs as per available hydrology | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-17 | 2025 | 3 | 17 | Reshun HPS | 4.2 | 2.99 | 1.24 | 25000 | 24388 | 1.41 | 1.53 | 51 | 13.48 | 47 | 45 | 47376 | 638628.48 | 328750.24 | 309878.24 | 612 | Low Hydrology and load shedding. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-17 | 2025 | 3 | 17 | Shishi HPS | 1.8 | 0.69 | 0.44 | 10649 | 10440 | 0.79 | 3 | 100 | 2.47 | 26.33 | 49 | 11376 | 28098.72 | 25786.8 | 2311.92 | 209 | The load varies as per the load demand of the local feeder, plain load shedding | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-18 | 2025 | 3 | 18 | Daral Khwar HPS | 36.6 | 12.3 | 11.06 | 265430 | 265430 | 4.76 | 4.44 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2194654.87 | 5068219.85 | 0 | Unit No.2 was on bar delivering an average load equal to 11.06 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-18 | 2025 | 3 | 18 | Jabori HPS | 10.2 | 6.4 | 5.53 | 135230 | 132730 | 6.7 | 4.34 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 757782.12 | 639830.04 | 2500 | The O&M team is carrying out restricted operation of the plant due to severe issues both in SCADA and local control.PD Jabori has already been informed about the exact status of the plant but till now no representative from EPC Contractor or Management Consultant reached at site. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median | Link_Generation_Data_Summary.xlsx
2025-03-18 | 2025 | 3 | 18 | Machai HPS | 2.6 | 0.67 | 0.31 | 8264 | 7920 | 16.2 | 9 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 36994.32 | 254476.08 | 344 | Unit being on bar delivering power to National Grid as per available water inflow and system conditions, precautionary shut down at 1420Hrs dated 18-03-2025 due to the drop in head race level which was recorded up to 6cumecs as water diverted by irrigation department at 0700Hrs Dated 18-03-2025 as per weekly diversion schedule of water . | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-18 | 2025 | 3 | 18 | Malakand-3 HPS | 81 | 24 | 22.2 | 532699 | 527210 | 47.34 | 14.96 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1509244.07 | 4055844.73 | 5489 | As per available hydrology from Irrigation Department One Unit at Malakand- III Power House is running | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-18 | 2025 | 3 | 18 | Pehur HPS | 18 | 5.06 | 4.74 | 113700 | 112000 | 16.35 | 16 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 421904 | 1205440 | 1700 | Plant remained operational through out 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-18 | 2025 | 3 | 18 | Reshun HPS | 4.2 | 2.93 | 1.1 | 25000 | 24410 | 1.41 | 1.53 | 51 | 13.48 | 47 | 45 | 47376 | 638628.48 | 329046.8 | 309581.68 | 590 | Storage of water in Reservoir due to low hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-18 | 2025 | 3 | 18 | Shishi HPS | 1.8 | 0.64 | 0.34 | 8231 | 8070 | 0.75 | 3 | 100 | 2.47 | 25 | 49 | 10800 | 26676 | 19932.9 | 6743.1 | 161 | Un force loadshedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-19 | 2025 | 3 | 19 | Daral Khwar HPS | 36.6 | 13 | 10.52 | 252470 | 252470 | 4.76 | 4.22 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2087497.7 | 5175377.02 | 0 | 1. Unit No.2 was on bar delivering an average load equal to 10.52 MW according to the available hydrology. 2. 132KV supply failed at 1530Hrs and was restored at 1535Hrs. Subsequently Unit#2 was synchronized with national grid at 1545Hrs. 3. 132KV supply failed at 1605Hrs and was restored at 1639Hrs. At 1651Hrs Unit#2 was synchronized with national grid. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-19 | 2025 | 3 | 19 | Jabori HPS | 10.2 | 6.5 | 5.62 | 134880 | 132080 | 6.7 | 4.41 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 754071.14 | 643541.02 | 2800 | Not reported | shahmunir00@gmail.com | Original | Avg Historical Hydrology filled with overall median | Link_Generation_Data_Summary.xlsx
2025-03-19 | 2025 | 3 | 19 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 16.2 | 6 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Unit is standby/stand still since 1420Hrs dated 18-03-2025 due to less hydrology as the water diverted by irrigation department at 0500Hrs dated 25-12-2024 from Machai Canal to Aba Zai Canal as per weekly diversion schedule of water. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-03-19 | 2025 | 3 | 19 | Malakand-3 HPS | 81 | 22 | 21.22 | 509323 | 503730 | 47.34 | 13.99 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1442027.87 | 4123060.93 | 5593 | Not reported | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-19 | 2025 | 3 | 19 | Pehur HPS | 18 | 4.94 | 4.87 | 116800 | 115000 | 16.35 | 15.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 433205 | 1194139 | 1800 | plant remained operational since 24 hrs as per available head. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-19 | 2025 | 3 | 19 | Reshun HPS | 4.2 | 2.87 | 1.17 | 24000 | 23400 | 1.41 | 1.47 | 48.97 | 13.48 | 47 | 45 | 47376 | 638628.48 | 315432 | 323196.48 | 600 | Storage of in the Reservoir/load shedding. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-19 | 2025 | 3 | 19 | Shishi HPS | 1.8 | 0.62 | 0.35 | 8446 | 8280 | 0.73 | 3 | 100 | 2.47 | 24.33 | 49 | 10512 | 25964.64 | 20451.6 | 5513.04 | 166 | Un force loadshedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-20 | 2025 | 3 | 20 | Daral Khwar HPS | 36.6 | 13.5 | 10.78 | 258620 | 258620 | 4.76 | 4.33 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2138347.75 | 5124526.97 | 0 | Unit No.2 was on bar delivering an average load equal to 10.78 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-20 | 2025 | 3 | 20 | Jabori HPS | 10.2 | 7.3 | 6.1 | 146150 | 143350 | 6.7 | 4.77 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 818413.82 | 579198.34 | 2800 | Unit 01 & 02 are bar delivering an average load equals to 6.1 MW according to available hydrology. Plant is in operation via manual control as SCADA and local control of both units are not working. No EPC or MC representative present at site despite of the fact that plant is in defect liability period (DLP) | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median | Link_Generation_Data_Summary.xlsx
2025-03-20 | 2025 | 3 | 20 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 16.2 | 6 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Unit is standby/stand still since 1420Hrs dated 18-03-2025 due to less hydrology as the water diverted by irrigation department at 0500Hrs dated 25-12-2024 from Machai Canal to Aba Zai Canal as per weekly diversion schedule of water. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-03-20 | 2025 | 3 | 20 | Malakand-3 HPS | 81 | 24 | 21.55 | 517203 | 511890 | 47.34 | 14.64 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1465387.5 | 4099701.3 | 5313 | Not reported | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-20 | 2025 | 3 | 20 | Pehur HPS | 18 | 4.95 | 4.13 | 99000 | 98000 | 16.35 | 13 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 369166 | 1258178 | 1000 | Plant remained shutdown for 3:30 Hrs in search of dead body in the canal as per instruction of irrigation sub engineer. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-20 | 2025 | 3 | 20 | Reshun HPS | 4.2 | 2 | 1.16 | 3 | 24296 | 1.41 | 1.53 | 51 | 13.48 | 47 | 45 | 47376 | 638628.48 | 327510.08 | 311118.4 | 24293.25 | Outgoing Feeder Breaker has been remained Off for storage of water in Reservoir. | zafar.src@gmail.com | Original | CHECK: Net > Units (source me verify karein) | Link_Generation_Data_Summary.xlsx
2025-03-20 | 2025 | 3 | 20 | Shishi HPS | 1.8 | 0.6 | 0.34 | 8078 | 7920 | 0.7 | 3 | 100 | 2.47 | 23.33 | 49 | 10080 | 24897.6 | 19562.4 | 5335.2 | 158 | Un force loadshedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-21 | 2025 | 3 | 21 | Daral Khwar HPS | 36.6 | 15.3 | 12.64 | 303960 | 303960 | 4.76 | 5.08 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2513232.47 | 4749642.25 | 0 | Unit #2 was on bar delivering an average load equal to 12.64MW. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-21 | 2025 | 3 | 21 | Jabori HPS | 10.2 | 9 | 6.08 | 146000 | 143200 | 6.7 | 4.77 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 817557.44 | 580054.72 | 2800 | Unit 01 and 02 on bar delivering an average load equals to 6.08 MW according to available hydrology. Issues related to SCADA, local control and unit overspending still persists. Neither EPC contractor nor MC representative present at site despite of the fact that plant is in defect liability period (DLP) | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median | Link_Generation_Data_Summary.xlsx
2025-03-21 | 2025 | 3 | 21 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 16.2 | 6 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Unit is standby/stand still since 1420Hrs dated 18-03-2025 due to less hydrology as the water diverted by irrigation department at 0500Hrs dated 25-12-2024 from Machai Canal to Aba Zai Canal as per weekly diversion schedule of water. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-03-21 | 2025 | 3 | 21 | Malakand-3 HPS | 81 | 25 | 21.53 | 516658 | 511120 | 47.34 | 14.65 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1463183.22 | 4101905.58 | 5538 | Not reported | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-21 | 2025 | 3 | 21 | Pehur HPS | 18 | 4.92 | 4.68 | 111400 | 110000 | 16.35 | 15.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 414370 | 1212974 | 1400 | Plant remained operational 24 hrs as per available hydrology | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-21 | 2025 | 3 | 21 | Reshun HPS | 4.2 | 2.98 | 1.17 | 25000 | 24404 | 1.41 | 1.53 | 51 | 13.48 | 47 | 45 | 47376 | 638628.48 | 328965.92 | 309662.56 | 596 | Low Hydrology, load shedding | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-21 | 2025 | 3 | 21 | Shishi HPS | 1.8 | 0.6 | 0.35 | 8446 | 8280 | 0.71 | 3 | 100 | 2.47 | 23.67 | 49 | 10224 | 25253.28 | 20451.6 | 4801.68 | 166 | Un force loadshedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-22 | 2025 | 3 | 22 | Daral Khwar HPS | 36.6 | 20.5 | 15.17 | 364040 | 364040 | 4.76 | 6.09 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3009991.93 | 4252882.79 | 0 | 1. Unit#2 and Unit #3 were on bar delivering an average load equal to 15.17 MW. 2. Unit #3 synchronized with the national grid at 1945Hrs. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-22 | 2025 | 3 | 22 | Jabori HPS | 10.2 | 9.2 | 7.01 | 168250 | 165450 | 6.7 | 5.5 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 944587.14 | 453025.02 | 2800 | Unit 01 and 02 synchronised with the national grid delivering an average load equals to 7.01 MW according to available hydrology. Issues related to SCADA and local control still exists. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median | Link_Generation_Data_Summary.xlsx
2025-03-22 | 2025 | 3 | 22 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 16.2 | 5 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Unit is standby/stand still since 1420Hrs dated 18-03-2025 due to less hydrology as the water diverted by irrigation department at 0500Hrs dated 18-03-2025 from Machai Canal to Aba Zai Canal as per weekly diversion schedule of water. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-03-22 | 2025 | 3 | 22 | Malakand-3 HPS | 81 | 25 | 23.28 | 558682 | 553290 | 47.34 | 15.3 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1583903.28 | 3981185.52 | 5392 | As per available hydrology from Irrigation Department One Unit at Malakand- III Power House is running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-22 | 2025 | 3 | 22 | Pehur HPS | 18 | 4.54 | 4.48 | 107400 | 105000 | 16.35 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 395535 | 1231809 | 2400 | Plant remained operational through out 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-22 | 2025 | 3 | 22 | Reshun HPS | 4.2 | 2.96 | 1.21 | 25000 | 24399 | 1.41 | 1.53 | 51 | 13.48 | 47 | 45 | 47376 | 638628.48 | 328898.52 | 309729.96 | 601 | Water shortage. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-22 | 2025 | 3 | 22 | Shishi HPS | 1.8 | 0.78 | 0.33 | 7864 | 7710 | 0.85 | 3 | 100 | 2.47 | 28.33 | 49 | 12240 | 30232.8 | 19043.7 | 11189.1 | 154 | Un force loadshedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-23 | 2025 | 3 | 23 | Daral Khwar HPS | 36.6 | 28.3 | 20.21 | 484960 | 484960 | 4.76 | 8.11 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 4009794.77 | 3253079.95 | 0 | Unit No.2 and 03 were on bar delivering an average load equal to 20.21 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-23 | 2025 | 3 | 23 | Jabori HPS | 10.2 | 9.2 | 6.04 | 144880 | 142080 | 6.7 | 4.73 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 811163.14 | 586449.02 | 2800 | Unit 01 and 02 operated through manual process as Control of unit 1 and 2 through SCADA and local control panel not working. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median | Link_Generation_Data_Summary.xlsx
2025-03-23 | 2025 | 3 | 23 | Machai HPS | 2.6 | 0.9 | 0.5 | 11392 | 11000 | 16.2 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 51381 | 240089.4 | 392 | The Unit after all preliminary checks and started at 1100Hrs Dated 23-03-2025 as rated head was restored due to increase in canal discharge as per new indent of Swabi Irrigation Sub Division. The water diverted to Machai Canal at 0600Hrs dated 23-03-2025 by irrigation department. Unit kept on FSNL for an half hour to carryout heat run test and finding everything normal then synchronized with the system at 1130Hrs and load gradually increased according to available inflow and system condition | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-23 | 2025 | 3 | 23 | Malakand-3 HPS | 81 | 25 | 22.38 | 537031 | 531210 | 47.34 | 14.54 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1520694.87 | 4044393.93 | 5821 | As per available hydrology from Irrigation Department One Unit at Malakand- III Power House is running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-23 | 2025 | 3 | 23 | Pehur HPS | 18 | 4.55 | 4.34 | 104300 | 103000 | 16.35 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 388001 | 1239343 | 1300 | plant remained operational since 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-23 | 2025 | 3 | 23 | Reshun HPS | 4.2 | 2.45 | 0.99 | 25000 | 24410 | 1.41 | 1.53 | 51 | 13.48 | 47 | 45 | 47376 | 638628.48 | 329046.8 | 309581.68 | 590 | Storage of water in Reservoir. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-23 | 2025 | 3 | 23 | Shishi HPS | 1.8 | 0.76 | 0.38 | 9241 | 9060 | 0.85 | 3 | 100 | 2.47 | 28.33 | 49 | 12240 | 30232.8 | 22378.2 | 7854.6 | 181 | Power house Off loaded for replacement of T/F on LT line | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-24 | 2025 | 3 | 24 | Daral Khwar HPS | 36.6 | 26.5 | 21.73 | 521500 | 521500 | 4.76 | 8.72 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 4311918.45 | 2950956.27 | 0 | Unit No.2 and 03 were on bar delivering an average load equal to 21.73 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-24 | 2025 | 3 | 24 | Jabori HPS | 10.2 | 9 | 5.44 | 130620 | 127820 | 6.7 | 4.27 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 729749.94 | 667862.22 | 2800 | Unit 01 and 02 were on bar delivering an average load equals to 5.44 MW according to available hydrology. Both units are unable to operate on AUTO due to severe issues in SCADA.Further local operating systems of units are also not working due to which O&M team is bound to operate the plant manually which may affect the machine efficiency.Project authorities have been informed but till now neither any representative of EPC Contractor contacted nor arrived at site. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median | Link_Generation_Data_Summary.xlsx
2025-03-24 | 2025 | 3 | 24 | Machai HPS | 2.6 | 1.4 | 0.99 | 23150 | 22323 | 16.2 | 16 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 104270.73 | 187199.67 | 827 | Unit remained on bar delivering power to National Grid as per available inflow and system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-24 | 2025 | 3 | 24 | Malakand-3 HPS | 81 | 38 | 27.42 | 657970 | 651000 | 47.34 | 18.17 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1863617.7 | 3701471.1 | 6970 | As per available hydrology from Irrigation Department Two Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-24 | 2025 | 3 | 24 | Pehur HPS | 18 | 4.4 | 4 | 95500 | 93000 | 16.35 | 13 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 350331 | 1277013 | 2500 | Plant remanined Operational throughout 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-24 | 2025 | 3 | 24 | Reshun HPS | 4.2 | 2.61 | 1.18 | 27000 | 26398 | 1.41 | 1.65 | 55 | 13.48 | 47 | 45 | 47376 | 638628.48 | 355845.04 | 282783.44 | 602 | Storage of water in Reservoir. Load shedding observed. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-24 | 2025 | 3 | 24 | Shishi HPS | 1.8 | 0.68 | 0.38 | 9027 | 8850 | 0.76 | 3 | 100 | 2.47 | 25.33 | 49 | 10944 | 27031.68 | 21859.5 | 5172.18 | 177 | Power house Off loaded for replacement of T/F on LT line | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-25 | 2025 | 3 | 25 | Daral Khwar HPS | 36.6 | 30.6 | 21.86 | 524540 | 524540 | 4.76 | 8.77 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 4337054.08 | 2925820.64 | 0 | 1. Unit No.2 and 03 were on bar delivering an average load equal to 21.86 MW according to the available hydrology. 2. 132KV supply failed at 2216Hrs and was restored at 2227Hrs. 3. Unit No.03 & 02 were synchronized with national grid at 2234Hrs and 2311Hrs. 4. 132KV supply failed at 1605Hrs and was restored at 1639Hrs. At 1651Hrs Unit#2 was synchronized with national grid. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-25 | 2025 | 3 | 25 | Jabori HPS | 10.2 | 6.7 | 5.09 | 122260 | 119460 | 6.7 | 4 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 682021.03 | 715591.13 | 2800 | Unit 01 and 02 were on bar delivering an average load equals to 5.1 MW according to available hydrology and system conditions. Both units are unable to operate on AUTO due to severe issues in SCADA. Further local operating systems of units are also not working due to which O&M team is bound to operate the plant manually which may affect the machine efficiency. Project authorities have been informed but till now neither any representative of EPC Contractor contacted nor arrived at site. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median | Link_Generation_Data_Summary.xlsx
2025-03-25 | 2025 | 3 | 25 | Machai HPS | 2.6 | 1.4 | 1.05 | 25125 | 24312 | 16.2 | 16.5 | 40.26 | 4.671 | 100 | 70 | 62400 | 291470.4 | 113561.35 | 177909.05 | 813 | No data submitted for this date | engr.atifwazir@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-03-25 | 2025 | 3 | 25 | Malakand-3 HPS | 81 | 37 | 34.99 | 839691 | 831430 | 47.34 | 23.35 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2380134.66 | 3184954.14 | 8261 | As per available hydrology from Irrigation Department Two Unit at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-25 | 2025 | 3 | 25 | Pehur HPS | 18 | 4.36 | 4.02 | 96600 | 95000 | 16.35 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 357865 | 1269479 | 1600 | Plant remained operational througout 24 hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-25 | 2025 | 3 | 25 | Reshun HPS | 4.2 | 2.51 | 1.21 | 28000 | 27388 | 1.41 | 1.71 | 57 | 13.48 | 47 | 45 | 47376 | 638628.48 | 369190.24 | 269438.24 | 612 | Load shedding due to low hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-25 | 2025 | 3 | 25 | Shishi HPS | 1.8 | 0.59 | 0.37 | 8874 | 8700 | 0.72 | 3 | 100 | 2.47 | 24 | 49 | 10368 | 25608.96 | 21489 | 4119.96 | 174 | Un force loadshedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-26 | 2025 | 3 | 26 | Daral Khwar HPS | 36.6 | 36.6 | 33.5 | 803910 | 803910 | 4.76 | 13.44 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6646969.05 | 615905.67 | 0 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 33.5 MW according to the available hydrology. 2. Unit No.01 was synchronized with national grid at 05:02Hrs. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-26 | 2025 | 3 | 26 | Jabori HPS | 10.2 | 6.5 | 5.17 | 124150 | 121350 | 6.7 | 4.06 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 692811.42 | 704800.74 | 2800 | Unit 01 and 02 were on bar delivering an average load equals to 5.17 MW according to available hydrology and system conditions. Tripping of unit 02 occurs frequently due to fault in governor oil pressure. Unit 02 shutdown at 1644 Hrs upon direction of RE so that the efficiency of machine may not be compromised due to frequent tripping. Both units are unable to operate on AUTO due to severe issues in SCADA. Further local operating systems of units are also not working due to which O&M team is bound to operate the plant manually which may affect the machine efficiency. Project authorities have been informed but till now neither any representative of EPC Contractor contacted nor arrived at site. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median | Link_Generation_Data_Summary.xlsx
2025-03-26 | 2025 | 3 | 26 | Machai HPS | 2.6 | 1.5 | 1.1 | 27100 | 26300 | 16.2 | 17 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 122847.3 | 168623.1 | 800 | Unit remained on bar delivering power to National Grid as per available inflow and system conditions | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-26 | 2025 | 3 | 26 | Malakand-3 HPS | 81 | 48 | 39.22 | 941201 | 932990 | 47.34 | 25.67 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2670870.47 | 2894218.33 | 8211 | As per available hydrology from Irrigation Department Two Unit at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-26 | 2025 | 3 | 26 | Pehur HPS | 18 | 4.47 | 4.35 | 104500 | 103000 | 16.35 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 388001 | 1239343 | 1500 | Plant remained operational through out 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-26 | 2025 | 3 | 26 | Reshun HPS | 4.2 | 1.85 | 1.23 | 29000 | 28420 | 1.41 | 1 | 33.33 | 13.48 | 47 | 45 | 47376 | 638628.48 | 383101.6 | 255526.88 | 580 | 770 | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-26 | 2025 | 3 | 26 | Shishi HPS | 1.8 | 0.68 | 0.4 | 9486 | 9300 | 0.77 | 3 | 100 | 2.47 | 25.67 | 49 | 11088 | 27387.36 | 22971 | 4416.36 | 186 | Power house Off loaded for replacement of T/F on LT line | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-27 | 2025 | 3 | 27 | Daral Khwar HPS | 36.6 | 36.6 | 35.37 | 848770 | 848770 | 4.76 | 14.19 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7017884.99 | 244989.73 | 0 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 35.37 MW according to the available hydrology. 2. 132KV supply failed at 1439Hrs and was restored at 1448Hrs. 3. Unit No.01, 02 and 03 were synchronized with national grid at 15:01 Hrs, 15:02 Hrs and 15:04 Hrs respectively. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-27 | 2025 | 3 | 27 | Jabori HPS | 10.2 | 6.3 | 4.12 | 101770 | 98970 | 6.7 | 3.23 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 565039.52 | 832572.64 | 2800 | Both units of the plant were operated manually as per available hydrology.Still SACDA and local control of the plant are not working.Unit # 02 tripped multiple times during the day specially when system voltage and frequency varies. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with overall median | Link_Generation_Data_Summary.xlsx
2025-03-27 | 2025 | 3 | 27 | Machai HPS | 2.6 | 1.73 | 1.48 | 36340 | 35440 | 16.2 | 22 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 165540.24 | 125930.16 | 900 | Unit remained on bar delivering power to National Grid as per available inflow and system conditions | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-27 | 2025 | 3 | 27 | Malakand-3 HPS | 81 | 47 | 41.68 | 1000238 | 991910 | 47.34 | 27.81 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2839540.76 | 2725548.04 | 8328 | As per available hydrology from Irrigation Department Two Unit at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-27 | 2025 | 3 | 27 | Pehur HPS | 18 | 4.63 | 4.37 | 105000 | 103000 | 16.35 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 388001 | 1239343 | 2000 | plant remained operational throughout 24 Hrs as per availabe hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-27 | 2025 | 3 | 27 | Reshun HPS | 4.2 | 1.33 | 0.24 | 4000 | 3428 | 1.41 | 0.24 | 8.13 | 13.48 | 47 | 45 | 47376 | 638628.48 | 46209.44 | 592419.04 | 572 | HT and LT lines faults due to heavy snowfall occurred. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-27 | 2025 | 3 | 27 | Shishi HPS | 1.8 | 0.73 | 0.36 | 8721 | 8550 | 3 | 0.79 | 26.33 | 2.47 | 100 | 49 | 43200 | 106704 | 21118.5 | 85585.5 | 171 | The load varies as per the load demand of the local feeder. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-28 | 2025 | 3 | 28 | Daral Khwar HPS | 36.6 | 36.6 | 29.76 | 714260 | 714260 | 4.76 | 11.94 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 5905715.96 | 1357158.76 | 0 | 1: Unit No. 01, 02 & 03 were on bar delivering an average load equal to 29.76 MW according to the available hydrology. 2: Unit No. 1 stopped due to low hydrology at 1645 Hrs. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-28 | 2025 | 3 | 28 | Jabori HPS | 10.2 | 4.35 | 2.79 | 67080 | 64280 | 6.7 | 2.19 | 73 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 366987.38 | 1030624.78 | 2800 | Both units are being operated manually through Governor as SACADA and local control of both units are still not working.Further after heavy rain hydrology decreased as both main and sand trap trash rack was completely choaked.Without Powerhouse shut down cleaning of Trash racks was not possible,therefore for purpose of trash racks cleaning power house was shut down for 04 hours (approximately).After cleaning activity units were synchronized again as per available hydrology. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with overall median | Link_Generation_Data_Summary.xlsx
2025-03-28 | 2025 | 3 | 28 | Machai HPS | 2.6 | 2.35 | 1.58 | 35780 | 34848 | 16.2 | 23 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 162775.01 | 128695.39 | 932 | Unit remained on bar delivering power to National Grid as per available inflow and system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-28 | 2025 | 3 | 28 | Malakand-3 HPS | 81 | 49 | 40.34 | 968230 | 960310 | 47.34 | 27.32 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2749079.44 | 2816009.36 | 7920 | As per available hydrology from Irrigation Department Two Unit at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-28 | 2025 | 3 | 28 | Pehur HPS | 18 | 4.56 | 3.61 | 86800 | 85000 | 16.35 | 12 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 320195 | 1307149 | 1800 | plant remained shutdown for 04:32 Hrs in serach of dead body in the canal. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-28 | 2025 | 3 | 28 | Reshun HPS | 4.2 | 1.38 | 0.52 | 12000 | 11420 | 1.41 | 0.73 | 24.47 | 13.48 | 47 | 45 | 47376 | 638628.48 | 153941.6 | 484686.88 | 580 | HT/LT Line faults due to heavy snowfall. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-28 | 2025 | 3 | 28 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 0 | 3 | 100 | 2.47 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | The last 5 Days its raining and on the request of local community the power house was shutdown due to danger of land sliding. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-29 | 2025 | 3 | 29 | Daral Khwar HPS | 36.6 | 23.3 | 21.36 | 512560 | 512560 | 4.76 | 8.57 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 4237999.85 | 3024874.87 | 0 | 1: Unit No. 02 & 03 were on bar delivering an average load equal to 21.36 MW according to the available hydrology. 2: Unit No. 1 standby due to low hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-29 | 2025 | 3 | 29 | Jabori HPS | 10.2 | 5 | 2.79 | 67100 | 64300 | 6.7 | 2.19 | 73 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 367101.56 | 1030510.6 | 2800 | Plant was operated manually as per available hydrology.A remote access of site was given to the SCADA expert of EPC Contractor to look into the issues of SCADA control as agreed in the online meeting held on 29.03.2025. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with overall median | Link_Generation_Data_Summary.xlsx
2025-03-29 | 2025 | 3 | 29 | Machai HPS | 2.6 | 2.33 | 1.74 | 41784 | 40744 | 16.2 | 26.6 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 190315.22 | 101155.18 | 1040 | Unit remained on bar delivering the power to National Grid as par available inflow and system conditions. | engr.atifwazir@gmail.com | Original | Avg load = Units / 24h | Link_Generation_Data_Summary.xlsx
2025-03-29 | 2025 | 3 | 29 | Malakand-3 HPS | 81 | 48 | 45.18 | 1084323 | 1077060 | 47.34 | 28.53 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3083299.66 | 2481789.14 | 7263 | As per available hydrology from Irrigation Department Two Unit at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-29 | 2025 | 3 | 29 | Pehur HPS | 18 | 5.05 | 4.4 | 105900 | 104000 | 16.35 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 391768 | 1235576 | 1900 | plant remained operational 24 hrs as per available hydrology | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-29 | 2025 | 3 | 29 | Reshun HPS | 4.2 | 1.68 | 1.09 | 24000 | 23400 | 1.49 | 1.47 | 48.97 | 13.48 | 49.67 | 45 | 50064 | 674862.72 | 315432 | 359430.72 | 600 | (I). Tariff rate PESCO's Slab wise prevailing rates starting from basic slab of Rs. 13.48/kwh. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-29 | 2025 | 3 | 29 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The last 6 Days its raining and on the request of local community the power house was shutdown due to danger of land sliding. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-30 | 2025 | 3 | 30 | Daral Khwar HPS | 36.6 | 21.7 | 19.69 | 472470 | 472470 | 4.76 | 7.9 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3906523.7 | 3356351.02 | 0 | Units #2 and #3 are on bar. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-30 | 2025 | 3 | 30 | Jabori HPS | 10.2 | 5.1 | 2.77 | 66600 | 63960 | 6.7 | 2.17 | 72.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 365160.43 | 1032451.73 | 2640 | Plant was operated manually as per available hydrology. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with overall median | Link_Generation_Data_Summary.xlsx
2025-03-30 | 2025 | 3 | 30 | Machai HPS | 2.6 | 2.31 | 1.2 | 28828 | 28120 | 16.2 | 16.2 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 131348.52 | 160121.88 | 708 | 18 | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-30 | 2025 | 3 | 30 | Malakand-3 HPS | 81 | 48 | 44.84 | 1076054 | 1069130 | 47.34 | 28.44 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3060598.45 | 2504490.35 | 6924 | As per available hydrology from Irrigation Department Two Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-30 | 2025 | 3 | 30 | Pehur HPS | 18 | 4.5 | 4.28 | 102600 | 101000 | 16.35 | 13.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 380467 | 1246877 | 1600 | Plant remained operational through out 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-30 | 2025 | 3 | 30 | Reshun HPS | 4.2 | 2.29 | 1.34 | 32000 | 31398 | 1.89 | 1.8 | 60 | 13.48 | 63 | 45 | 63504 | 856033.92 | 423245.04 | 432788.88 | 602 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-30 | 2025 | 3 | 30 | Shishi HPS | 1.8 | 0.7 | 0.33 | 7956 | 7800 | 3 | 0.9 | 30 | 2.47 | 100 | 49 | 43200 | 106704 | 19266 | 87438 | 156 | Force loadshedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-31 | 2025 | 3 | 31 | Daral Khwar HPS | 36.6 | 24 | 19.97 | 479300 | 479300 | 4.76 | 8.02 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3962996.19 | 3299878.53 | 0 | Units #2 and 3 are on bar. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-31 | 2025 | 3 | 31 | Jabori HPS | 10.2 | 4.8 | 3.29 | 79028 | 76380 | 6.7 | 2.58 | 86 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 436068.7 | 961543.46 | 2648 | Plant is operational manually as per available hydrology. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with overall median | Link_Generation_Data_Summary.xlsx
2025-03-31 | 2025 | 3 | 31 | Machai HPS | 2.6 | 1.84 | 1.58 | 38856 | 37968 | 16.2 | 25.8 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 177348.53 | 114121.87 | 888 | Unit tripped at 1644Hrs Dated 31.03.2025 due to the tripping of 11KV Machai-HPS feeder as 132KV lines Mardan tripped. Unit synchronized with the system at 1701Hrs as line re-energized. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-31 | 2025 | 3 | 31 | Malakand-3 HPS | 81 | 47 | 40.13 | 963126 | 956830 | 47.34 | 28.06 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2739117.24 | 2825971.56 | 6296 | unit # 01 & 03 are on bar while unit # 02 kept standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-31 | 2025 | 3 | 31 | Pehur HPS | 18 | 4.57 | 4.5 | 108400 | 106000 | 16.35 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 399302 | 1228042 | 2400 | plant remained operational 24 hrs as per available hydrology | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-03-31 | 2025 | 3 | 31 | Reshun HPS | 4.2 | 2.6 | 1.06 | 24000 | 24404 | 1.49 | 1.47 | 48.97 | 13.48 | 49.67 | 45 | 50064 | 674862.72 | 328965.92 | 345896.8 | 404 | Line faults. | zafar.src@gmail.com | Original | CHECK: Net > Units (source me verify karein) | Link_Generation_Data_Summary.xlsx
2025-03-31 | 2025 | 3 | 31 | Shishi HPS | 1.8 | 0.86 | 0.44 | 10557 | 10350 | 3 | 0.98 | 32.67 | 2.47 | 100 | 49 | 43200 | 106704 | 25564.5 | 81139.5 | 207 | The load varies as per the load demand of the local feeder, plan load shedding | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-01 | 2025 | 4 | 1 | Daral Khwar HPS | 36.6 | 30.6 | 23.4 | 561570 | 561570 | 14.71 | 9.39 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 4643229.23 | 2619645.49 | 0 | Units No. 2 & 3 have reached full capacity today and are on bar. Unit No. 1 on standby. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-01 | 2025 | 4 | 1 | Jabori HPS | 10.2 | 5 | 3.41 | 81979 | 79330 | 0.39 | 2.67 | 89 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 452910.84 | 944701.32 | 2649 | Plant was operational manually as per available Hydrology and circumstances. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-04-01 | 2025 | 4 | 1 | Machai HPS | 2.6 | 1.64 | 1.49 | 35584 | 34760 | 23.8 | 23 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 162363.96 | 129106.44 | 824 | Unit remained on the bar delivering the power to National Grid as par available inflow and system conditions | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-01 | 2025 | 4 | 1 | Malakand-3 HPS | 81 | 45 | 41.45 | 994880 | 987840 | 51 | 26.82 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2827889.57 | 2737199.23 | 7040 | Unit # 01 & 03 are on bar while Unit # 02 stand by due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-01 | 2025 | 4 | 1 | Pehur HPS | 18 | 4.62 | 4.56 | 109500 | 108000 | 14.44 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 406836 | 1220508 | 1500 | Plant remained operational for 24 Hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-01 | 2025 | 4 | 1 | Reshun HPS | 4.2 | 1.55 | 1 | 24000 | 23404 | 1.5 | 1.47 | 48.97 | 13.48 | 50 | 45 | 50400 | 679392 | 315485.92 | 363906.08 | 596 | (I). Tariff rate PESCO's Slab wise prevailing rates starting from basic slab of Rs. 13.48/kwh. Line faults | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-01 | 2025 | 4 | 1 | Shishi HPS | 1.8 | 0.96 | 0.33 | 7803 | 7650 | 3 | 1.05 | 35 | 2.47 | 100 | 49 | 43200 | 106704 | 18895.5 | 87808.5 | 153 | Force loadshedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-02 | 2025 | 4 | 2 | Daral Khwar HPS | 36.6 | 35.6 | 28.06 | 673360 | 673360 | 14.71 | 11.26 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 5567542.49 | 1695332.23 | 0 | Unit#1 was synchronized with the national grid at 1855hrs due to increasing summer hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-02 | 2025 | 4 | 2 | Jabori HPS | 10.2 | 4.7 | 3.24 | 77954 | 75470 | 0.39 | 2.54 | 84.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 430873.32 | 966738.84 | 2484 | Plant was operated manually as per available Hydrology and existing circumstances. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-04-02 | 2025 | 4 | 2 | Machai HPS | 2.6 | 1.5 | 1.32 | 32512 | 31680 | 23.8 | 21 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 147977.28 | 143493.12 | 832 | Unit remained on bar delivering the Power to National Grid as par available inflow and the system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-02 | 2025 | 4 | 2 | Malakand-3 HPS | 81 | 47 | 41.75 | 1001951 | 996620 | 51 | 27.2 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2853024.07 | 2712064.73 | 5331 | unit # 01 & 03 are on bar while unit # 02 kept standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-02 | 2025 | 4 | 2 | Pehur HPS | 18 | 4.62 | 4.58 | 109800 | 108000 | 12.12 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 406836 | 1220508 | 1800 | Plant remained operational through out 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-02 | 2025 | 4 | 2 | Reshun HPS | 4.2 | 1.58 | 1.02 | 24000 | 23415 | 1.5 | 1.47 | 48.97 | 13.48 | 50 | 45 | 50400 | 679392 | 315634.2 | 363757.8 | 585 | Line faults | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-02 | 2025 | 4 | 2 | Shishi HPS | 1.8 | 0.56 | 0.23 | 5630 | 5520 | 0.66 | 3 | 100 | 2.47 | 22 | 49 | 9504 | 23474.88 | 13634.4 | 9840.48 | 110 | The load varies as per the load demand of the local feeder, plan load shedding | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-03 | 2025 | 4 | 3 | Daral Khwar HPS | 36.6 | 34.3 | 27.17 | 652170 | 652170 | 14.71 | 10.91 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 5392337.21 | 1870537.51 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-03 | 2025 | 4 | 3 | Jabori HPS | 10.2 | 4.2 | 3.63 | 87134 | 84460 | 0.39 | 2.84 | 94.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 482199.03 | 915413.13 | 2673.6 | Plant was operational as per available hydrology and existing circumstances. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-04-03 | 2025 | 4 | 3 | Machai HPS | 2.6 | 1.49 | 1.5 | 36580 | 35760 | 23.8 | 23.5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 167034.96 | 124435.44 | 820 | Unit remained on bar delivering the power to National Grid as par available inflow and the system conditions | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-03 | 2025 | 4 | 3 | Malakand-3 HPS | 81 | 47 | 43.08 | 1034010 | 1025240 | 51 | 27.86 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2934954.55 | 2630134.25 | 8770 | As per available hydrology from Irrigation Department Two Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-03 | 2025 | 4 | 3 | Pehur HPS | 18 | 4.64 | 4.56 | 110300 | 108000 | 12.12 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 406836 | 1220508 | 2300 | Plant remained operational 24 hrs as per available hydrology | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-03 | 2025 | 4 | 3 | Reshun HPS | 4.2 | 1.51 | 1.09 | 25000 | 24411 | 1.59 | 1.53 | 51 | 13.48 | 53 | 45 | 53424 | 720155.52 | 329060.28 | 391095.24 | 589 | Line faults due to snowfall damages. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-03 | 2025 | 4 | 3 | Shishi HPS | 1.8 | 0.51 | 0.28 | 6824 | 6690 | 3 | 0.62 | 20.67 | 2.47 | 100 | 49 | 43200 | 106704 | 16524.3 | 90179.7 | 134 | The load varies as per the load demand of the local feeder, plan load shedding | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-04 | 2025 | 4 | 4 | Daral Khwar HPS | 36.6 | 26 | 21.89 | 525250 | 525250 | 14.71 | 8.78 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 4342924.58 | 2919950.14 | 0 | Units No.01,02 and 03 were on bar delivering an average load equal to 21.89 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-04 | 2025 | 4 | 4 | Jabori HPS | 10.2 | 4.3 | 3.05 | 73276 | 70730 | 0.39 | 2.39 | 79.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 403811.72 | 993800.44 | 2546 | Plant was operational manually as per available hydrology and existing circumstances. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-04-04 | 2025 | 4 | 4 | Machai HPS | 2.6 | 1.62 | 0.96 | 35280 | 34364 | 23.8 | 23.5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 160514.24 | 130956.16 | 916 | The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 1957Hrs and 2251Hrs dated 04.03.2025 due to the tripping of 11KV Machai-HPS feeder as 132KV line Mardan tripped.Unit synchronized with the system at 2021Hrs and 0214Hrs dated 05.03.2025 respectively as 11KV Machai-HPS line energized at 2015Hrs and 0124Hrs dated 05.03.2025 respectively. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-04 | 2025 | 4 | 4 | Malakand-3 HPS | 81 | 47 | 41.15 | 987574 | 978390 | 51 | 27.36 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2800837.05 | 2764251.75 | 9184 | As per available hydrology from Irrigation Department Two Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-04 | 2025 | 4 | 4 | Pehur HPS | 18 | 4.65 | 4.58 | 109900 | 108000 | 12.12 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 406836 | 1220508 | 1900 | Plant remained operational throughout 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-04 | 2025 | 4 | 4 | Reshun HPS | 4.2 | 2 | 1.27 | 29000 | 28418 | 1.8 | 1.77 | 59 | 13.48 | 60 | 45 | 60480 | 815270.4 | 383074.64 | 432195.76 | 582 | Low Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-04 | 2025 | 4 | 4 | Shishi HPS | 1.8 | 0.64 | 0.35 | 8446 | 8280 | 3 | 0.74 | 24.67 | 2.47 | 100 | 49 | 43200 | 106704 | 20451.6 | 86252.4 | 166 | The load varies as per the load demand of the local feeder, plan load shedding | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-05 | 2025 | 4 | 5 | Daral Khwar HPS | 36.6 | 36.6 | 27.91 | 669800 | 669800 | 14.71 | 11.2 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 5538107.34 | 1724767.38 | 0 | Units No.01,02 and 03 were on bar delivering an average load equal to 27.91 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-05 | 2025 | 4 | 5 | Jabori HPS | 10.2 | 3.9 | 2.66 | 63848 | 61490 | 0.39 | 2 | 66.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 351058.71 | 1046553.45 | 2358 | Plant was operated as per available hydrology and existing circumstances. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-04-05 | 2025 | 4 | 5 | Machai HPS | 2.6 | 1.57 | 0.88 | 21772 | 21164 | 23.8 | 16 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 98857.04 | 192613.36 | 608 | The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 0551Hrs dated 05.04.2025 due to the tripping of 11KV Machai-HPS feeder as 132KV line Mardan tripped.Unit synchronized with the system at 0648Hrs as 11KV Machai-HPS line energized at 0638Hrs . | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-05 | 2025 | 4 | 5 | Malakand-3 HPS | 81 | 44 | 39.02 | 936511 | 928610 | 51 | 25.64 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2658331.85 | 2906756.95 | 7901 | As per available Hydrology from Irrigation department two Units at Malakand III HPC are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-05 | 2025 | 4 | 5 | Pehur HPS | 18 | 4.66 | 4.55 | 109300 | 108000 | 14.44 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 406836 | 1220508 | 1300 | plant remained operational as per available head. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-05 | 2025 | 4 | 5 | Reshun HPS | 4.2 | 2.26 | 1.27 | 31000 | 30420 | 1.98 | 1.9 | 63.33 | 13.48 | 66 | 45 | 66528 | 896797.44 | 410061.6 | 486735.84 | 580 | Tripping due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-05 | 2025 | 4 | 5 | Shishi HPS | 1.8 | 0.81 | 0.29 | 7007 | 6870 | 3 | 0.85 | 28.33 | 2.47 | 100 | 49 | 43200 | 106704 | 16968.9 | 89735.1 | 137 | The load varies as per the load demand of the local feeder, plan load shedding. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-06 | 2025 | 4 | 6 | Daral Khwar HPS | 36.6 | 36.6 | 34.83 | 835830 | 835830 | 14.71 | 13.98 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6910893.19 | 351981.53 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-06 | 2025 | 4 | 6 | Jabori HPS | 10.2 | 4.3 | 2.97 | 71345 | 68750 | 0.39 | 2.33 | 77.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 392507.5 | 1005104.66 | 2595 | Plant was operational manually as per available hydrology and existing circumstances. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-04-06 | 2025 | 4 | 6 | Machai HPS | 2.6 | 1.37 | 1.13 | 27920 | 27148 | 23.8 | 17.8 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 126808.31 | 164662.09 | 772 | Unit remained on bar delivering power to National Grid as par available inflow and the system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-06 | 2025 | 4 | 6 | Malakand-3 HPS | 81 | 47 | 42.67 | 1024016 | 1016290 | 51 | 27.68 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2909333.38 | 2655755.42 | 7726 | As per available hydrology from Irrigation Department Two Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-06 | 2025 | 4 | 6 | Pehur HPS | 18 | 4.58 | 4.51 | 108300 | 107000 | 10.04 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 403069 | 1224275 | 1300 | Plant remained operational throughout 24 hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-06 | 2025 | 4 | 6 | Reshun HPS | 4.2 | 2.23 | 1.29 | 32000 | 31417 | 1.98 | 1.95 | 65 | 13.48 | 66 | 45 | 66528 | 896797.44 | 423501.16 | 473296.28 | 583 | Low Hydrology | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-06 | 2025 | 4 | 6 | Shishi HPS | 1.8 | 0.61 | 0.34 | 8048 | 7890 | 3 | 0.7 | 23.33 | 2.47 | 100 | 49 | 43200 | 106704 | 19488.3 | 87215.7 | 158 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-07 | 2025 | 4 | 7 | Daral Khwar HPS | 36.6 | 36.6 | 36.22 | 869370 | 869370 | 14.71 | 14.54 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7188211.97 | 74662.75 | 0 | Units No.01,02 and 03 were on bar delivering. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-07 | 2025 | 4 | 7 | Jabori HPS | 10.2 | 6.9 | 3.11 | 74620 | 72140 | 0.39 | 2.44 | 81.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 411861.69 | 985750.47 | 2480 | Plant was operated manually as per available hydrology and circumstances. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-04-07 | 2025 | 4 | 7 | Machai HPS | 2.6 | 1.43 | 1.33 | 32560 | 31592 | 23.8 | 21 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 147566.23 | 143904.17 | 968 | Unit remained on bar delivering power to National Grid as par available inflow and the system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-07 | 2025 | 4 | 7 | Malakand-3 HPS | 81 | 48 | 43.54 | 1044957 | 1036720 | 51 | 28.17 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2967818.34 | 2597270.46 | 8237 | As per available hydrology from Irrigation Department Two Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-07 | 2025 | 4 | 7 | Pehur HPS | 18 | 4.5 | 3.66 | 88300 | 86000 | 12.12 | 12.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 323962 | 1303382 | 2300 | Plant remained shut down since 1946 hrs for search of dead body in the canal as per irrigation SDO intruction. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-07 | 2025 | 4 | 7 | Reshun HPS | 4.2 | 2.31 | 1.26 | 31000 | 30170 | 1.98 | 1.89 | 63 | 13.48 | 66 | 45 | 66528 | 896797.44 | 406691.6 | 490105.84 | 830 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-07 | 2025 | 4 | 7 | Shishi HPS | 1.8 | 0.62 | 0.33 | 7864 | 7710 | 3 | 0.7 | 23.33 | 2.47 | 100 | 49 | 43200 | 106704 | 19043.7 | 87660.3 | 154 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-08 | 2025 | 4 | 8 | Daral Khwar HPS | 36.6 | 36.6 | 33.87 | 812820 | 812820 | 14.71 | 13.59 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6720639.61 | 542235.11 | 0 | 1: Units No.01,02 and 03 were on bar delivering an average load equal to 33.87 MW according to the available hydrology. 2: 132kV Supply line was tripped at 18:52Hrs and was restored at 20:06Hrs. 3: Unit No. 02,03 and 01 were successfully synchronized with national Grid at 20:21Hrs,20:22Hrs and 20:30 respectively. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-08 | 2025 | 4 | 8 | Jabori HPS | 10.2 | 7 | 3.97 | 95280 | 92780 | 0.39 | 3.11 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 529699.58 | 867912.58 | 2500 | Plant was operational manually as per available hydrology and circumstances. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-04-08 | 2025 | 4 | 8 | Machai HPS | 2.6 | 1.94 | 1.55 | 36644 | 35640 | 23.8 | 23.5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 166474.44 | 124995.96 | 1004 | Unit remained on bar delivering power to National Grid as par available inflow and the system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-08 | 2025 | 4 | 8 | Malakand-3 HPS | 81 | 54 | 48.47 | 1163214 | 1154660 | 51 | 31.84 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3305445.18 | 2259643.62 | 8554 | As per available hydrology from Irrigation Department Two Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-08 | 2025 | 4 | 8 | Pehur HPS | 18 | 4.8 | 1.32 | 31700 | 31000 | 14.44 | 5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 116777 | 1510567 | 700 | plant remained sutdown for 17:20 Hrs in search of dead bodies in the canal as per instruction of irrigation SDO. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-08 | 2025 | 4 | 8 | Reshun HPS | 4.2 | 2.26 | 1.3 | 30000 | 29390 | 1.93 | 1.83 | 61 | 13.48 | 64.33 | 45 | 64848 | 874151.04 | 396177.2 | 477973.84 | 610 | Outgoing feeder Breaker tripped 2 time due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-08 | 2025 | 4 | 8 | Shishi HPS | 1.8 | 0.72 | 0.3 | 7313 | 7170 | 3 | 0.77 | 25.67 | 2.47 | 100 | 49 | 43200 | 106704 | 17709.9 | 88994.1 | 143 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-09 | 2025 | 4 | 9 | Daral Khwar HPS | 36.6 | 36.6 | 36.26 | 870350 | 870350 | 14.71 | 14.56 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7196314.9 | 66559.82 | 0 | 1. Units No.01, 02 and 03 were on bar delivering an average load equal to 36.26MW according to available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-09 | 2025 | 4 | 9 | Jabori HPS | 10.2 | 10.2 | 5.63 | 135180 | 132540 | 0.39 | 4.42 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 756697.37 | 640914.79 | 2640 | Plant was operated manually as per available hydrology and existing circumstances. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-04-09 | 2025 | 4 | 9 | Machai HPS | 2.6 | 1.89 | 1.64 | 40116 | 39284 | 23.8 | 26 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 183495.56 | 107974.84 | 832 | Unit remained on bar delivering power to National Grid as par available inflow and the system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-09 | 2025 | 4 | 9 | Malakand-3 HPS | 81 | 52 | 49.33 | 1183852 | 1175040 | 51 | 32 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3363787.01 | 2201301.79 | 8812 | As per available hydrology from Irrigation Department Two Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-09 | 2025 | 4 | 9 | Pehur HPS | 18 | 4.74 | 4.35 | 104500 | 102000 | 10.04 | 14.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 384234 | 1243110 | 2500 | plant remained shutdown for 01:10 Hrs due to tripping of 132 kv line gadoon grid. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-09 | 2025 | 4 | 9 | Reshun HPS | 4.2 | 2.2 | 1.26 | 33000 | 32388 | 1.89 | 1.8 | 60 | 13.48 | 63 | 45 | 63504 | 856033.92 | 436590.24 | 419443.68 | 612 | Low load | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-09 | 2025 | 4 | 9 | Shishi HPS | 1.8 | 0.7 | 0.22 | 5324 | 5220 | 3 | 0.74 | 24.67 | 2.47 | 100 | 49 | 43200 | 106704 | 12893.4 | 93810.6 | 104 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO P/H shutdown for duration of 4 hours due to Gravel Spill Flashing of Intake. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-10 | 2025 | 4 | 10 | Daral Khwar HPS | 36.6 | 36.6 | 36.19 | 868530 | 868530 | 14.71 | 14.52 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7181266.6 | 81608.12 | 0 | 1. Units No. 01, 02 and 03 were on bar delivering an average load equal to 36.19 MW according to available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-10 | 2025 | 4 | 10 | Jabori HPS | 10.2 | 8 | 5.1 | 122082 | 119480 | 0.39 | 3.99 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 682135.22 | 715476.94 | 2602 | Both units were operational manually as per available hydrology and existing circumstances. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-04-10 | 2025 | 4 | 10 | Machai HPS | 2.6 | 2.22 | 1.46 | 33312 | 32336 | 23.8 | 21 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 151041.46 | 140428.94 | 976 | Not reported | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-10 | 2025 | 4 | 10 | Malakand-3 HPS | 81 | 52 | 49.28 | 1182605 | 1173680 | 51 | 31.51 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3359893.74 | 2205195.06 | 8925 | As per available hydrology from Irrigation Department Two Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-10 | 2025 | 4 | 10 | Pehur HPS | 18 | 4.61 | 4.44 | 106600 | 970000 | 11.88 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 3653990 | -2026646 | 863400 | plant remained operational as per available head. | phpcmw18@gmail.com | Original | CHECK: Net > Units (source me verify karein) | Link_Generation_Data_Summary.xlsx
2025-04-10 | 2025 | 4 | 10 | Reshun HPS | 4.2 | 1.58 | 1.12 | 23000 | 22421 | 1.59 | 1.49 | 49.67 | 13.48 | 53 | 45 | 53424 | 720155.52 | 302235.08 | 417920.44 | 579 | HT line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-10 | 2025 | 4 | 10 | Shishi HPS | 1.8 | 0.57 | 0.34 | 8231 | 8070 | 3 | 0.64 | 21.33 | 2.47 | 100 | 49 | 43200 | 106704 | 19932.9 | 86771.1 | 161 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-11 | 2025 | 4 | 11 | Daral Khwar HPS | 36.6 | 36.6 | 36.18 | 868380 | 868380 | 14.71 | 14.52 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7180026.35 | 82848.37 | 0 | 1. Units No. 01, 02 and 03 were on bar delivering an average load equal to 36.18 MW according to available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-11 | 2025 | 4 | 11 | Jabori HPS | 10.2 | 7.5 | 5.44 | 130520 | 127880 | 0.39 | 4.26 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 730092.5 | 667519.66 | 2640 | Both units were on bar manually as per available hydrology and existing circumstances. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-04-11 | 2025 | 4 | 11 | Machai HPS | 2.6 | 2.23 | 1.76 | 40472 | 39560 | 23.8 | 26 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 184784.76 | 106685.64 | 912 | Unit remained on bar delivering power to National Grid as par available inflow and the system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-11 | 2025 | 4 | 11 | Malakand-3 HPS | 81 | 52 | 48.64 | 1167414 | 1158460 | 51 | 31.5 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3316323.44 | 2248765.36 | 8954 | As per available hydrology from Irrigation Department Two Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-11 | 2025 | 4 | 11 | Pehur HPS | 18 | 4.71 | 4.6 | 110500 | 109000 | 11.88 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 410603 | 1216741 | 1500 | Plant remained operational throughout 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-11 | 2025 | 4 | 11 | Reshun HPS | 4.2 | 1.92 | 1.21 | 28000 | 27402 | 1.81 | 1.71 | 57.13 | 13.48 | 60.33 | 45 | 60816 | 819799.68 | 369378.96 | 450420.72 | 598 | Line faults | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-11 | 2025 | 4 | 11 | Shishi HPS | 1.8 | 0.54 | 0.31 | 7436 | 7290 | 0.61 | 3 | 100 | 2.47 | 20.33 | 49 | 8784 | 21696.48 | 18006.3 | 3690.18 | 146 | The load varies as per the load demand of the local feeder. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-12 | 2025 | 4 | 12 | Daral Khwar HPS | 36.6 | 36.6 | 36.26 | 870350 | 870350 | 14.71 | 14.56 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7196314.9 | 66559.82 | 0 | All Units are on bar. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-12 | 2025 | 4 | 12 | Jabori HPS | 10.2 | 7.5 | 4.71 | 115930 | 113130 | 0.39 | 3.69 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 645881.8 | 751730.36 | 2800 | Both units were operational as per available hydrology.Further SCADA team deputed by O&M is also working on the system for last 01 week. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-04-12 | 2025 | 4 | 12 | Machai HPS | 2.6 | 1.86 | 1.44 | 33832 | 32956 | 23.8 | 21.7 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 153937.48 | 137532.92 | 876 | Not reported | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-12 | 2025 | 4 | 12 | Malakand-3 HPS | 81 | 52 | 49.6 | 1190366 | 1181710 | 51 | 32.12 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3382881.22 | 2182207.58 | 8656 | As per available hydrology from Irrigation Department Two Units at Malakand- III Power House are running | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-12 | 2025 | 4 | 12 | Pehur HPS | 18 | 4.81 | 4.7 | 112800 | 111000 | 12.12 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 418137 | 1209207 | 1800 | Plant remained operational 24 hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-12 | 2025 | 4 | 12 | Reshun HPS | 4.2 | 1.84 | 1.2 | 27000 | 26399 | 1.78 | 1.65 | 55 | 13.48 | 59.33 | 45 | 59808 | 806211.84 | 355858.52 | 450353.32 | 601 | Low Load | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-12 | 2025 | 4 | 12 | Shishi HPS | 1.8 | 0.67 | 0.35 | 8384 | 8220 | 3 | 0.71 | 23.67 | 2.47 | 100 | 49 | 43200 | 106704 | 20303.4 | 86400.6 | 164 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-13 | 2025 | 4 | 13 | Daral Khwar HPS | 36.6 | 36.6 | 36.14 | 867380 | 867380 | 14.71 | 14.51 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7171758.05 | 91116.67 | 0 | Not reported | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-13 | 2025 | 4 | 13 | Jabori HPS | 10.2 | 7 | 3.97 | 95300 | 92660 | 0.39 | 3.11 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 529014.47 | 868597.69 | 2640 | Plant was operational manually as per available hydrology.Further SCADA team deputed by EPC Contractor is working on the system from 07.04.2025 to look into the POST COD issues. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-04-13 | 2025 | 4 | 13 | Machai HPS | 2.6 | 2.02 | 1.61 | 38240 | 37268 | 23.8 | 24.6 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 174078.83 | 117391.57 | 972 | Not reported | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-13 | 2025 | 4 | 13 | Malakand-3 HPS | 81 | 52 | 49.94 | 1198464 | 1190050 | 51 | 32.48 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3406756.14 | 2158332.66 | 8414 | As per available hydrology from Irrigation Department Two Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-13 | 2025 | 4 | 13 | Pehur HPS | 18 | 4.81 | 4.72 | 113300 | 111000 | 12.12 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 418137 | 1209207 | 2300 | Plant remained operational 24 hrs as per available hydrology | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-13 | 2025 | 4 | 13 | Reshun HPS | 4.2 | 2 | 1.32 | 31000 | 30390 | 2.01 | 1.9 | 63.33 | 13.48 | 67 | 45 | 67536 | 910385.28 | 409657.2 | 500728.08 | 610 | Outgoing line feeder tripping. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-13 | 2025 | 4 | 13 | Shishi HPS | 1.8 | 0.55 | 0.29 | 7007 | 6870 | 3 | 0.61 | 20.33 | 2.47 | 100 | 49 | 43200 | 106704 | 16968.9 | 89735.1 | 137 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-14 | 2025 | 4 | 14 | Daral Khwar HPS | 36.6 | 36.6 | 36.2 | 868800 | 868800 | 14.71 | 14.53 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7183499.04 | 79375.68 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.20 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-14 | 2025 | 4 | 14 | Jabori HPS | 10.2 | 7.5 | 1.95 | 46800 | 44130 | 0.39 | 1.53 | 51 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 251947 | 1145665.16 | 2670 | Post COD issues of SCADA were being addressed by the team deputed by the EPC Contractor.O&M is operating and shutting down the units as per instructions of SCADA team. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-04-14 | 2025 | 4 | 14 | Machai HPS | 2.6 | 1.8 | 1.44 | 35884 | 34936 | 23.8 | 23.2 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 163186.06 | 128284.34 | 948 | Unit remained on bar delivering power to National Grid as par available inflow and the system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-14 | 2025 | 4 | 14 | Malakand-3 HPS | 81 | 52 | 49.84 | 1196175 | 1187220 | 51 | 32.36 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3398654.69 | 2166434.11 | 8955 | As per available hydrology from Irrigation Department Two Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-14 | 2025 | 4 | 14 | Pehur HPS | 18 | 5.3 | 4.77 | 114700 | 113000 | 11.88 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 425671 | 1201673 | 1700 | Plant remained operational throughout 24 hrs as per availabe hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-14 | 2025 | 4 | 14 | Reshun HPS | 4.2 | 2.39 | 1.47 | 24000 | 23606 | 1.56 | 1.47 | 48.97 | 13.48 | 52 | 45 | 52416 | 706567.68 | 318208.88 | 388358.8 | 394 | Outgoing line feeder tripping. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-14 | 2025 | 4 | 14 | Shishi HPS | 1.8 | 0.66 | 0.35 | 8415 | 8250 | 3 | 0.66 | 22 | 2.47 | 100 | 49 | 43200 | 106704 | 20377.5 | 86326.5 | 165 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-15 | 2025 | 4 | 15 | Daral Khwar HPS | 36.6 | 36.6 | 36.18 | 868300 | 868300 | 14.71 | 14.52 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7179364.89 | 83509.83 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.18 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-15 | 2025 | 4 | 15 | Jabori HPS | 10.2 | 7.3 | 3.33 | 79906 | 78510 | 0.39 | 2.66 | 88.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 448229.29 | 949382.87 | 1396 | Due to tripping issue Plant was shut down at 11.45 AM as instructed by CEO PEDO.Further unit # 02 was not taking load beyond 02 MW. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-04-15 | 2025 | 4 | 15 | Machai HPS | 2.6 | 2.02 | 1.12 | 26664 | 26004 | 23.8 | 23.4 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 121464.68 | 170005.72 | 660 | Unit being on bar delivering power to National Grid as per available water inflow and system conditions, precautionary shut down at 0837Hrs dated 15-04-2025 on the request of GSO staff (Katlang Grid) as PTW issued to Operation staff (PESCO) on KATLANG Grid.11KV Machai-HPS line re-energized at 1520Hrs as PTW canceled by Operation staff (PESCO). Unit synchronized with the system at 1547Hrs and load gradually increased according to available inflow and system condition. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-15 | 2025 | 4 | 15 | Malakand-3 HPS | 81 | 52 | 49.17 | 1179983 | 1170920 | 51 | 31.46 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3351992.68 | 2213096.12 | 9063 | As per available hydrology from Irrigation Department Two Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-15 | 2025 | 4 | 15 | Pehur HPS | 18 | 5.07 | 4.8 | 115200 | 113000 | 11.88 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 425671 | 1201673 | 2200 | Plant remained operational throughout 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-15 | 2025 | 4 | 15 | Reshun HPS | 4.2 | 2.06 | 1.15 | 28000 | 27410 | 1.82 | 1.71 | 57 | 13.48 | 60.67 | 45 | 61152 | 824328.96 | 369486.8 | 454842.16 | 590 | (I). Tariff rate PESCO's Slab wise prevailing rates starting from basic slab of Rs. 13.48/kwh.(2). Low load | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-15 | 2025 | 4 | 15 | Shishi HPS | 1.8 | 0.52 | 0.22 | 5324 | 0 | 0.6 | 3 | 100 | 2.47 | 20 | 49 | 8640 | 21340.8 | 0 | 21340.8 | 5324 | The load varies as per the load demand of the local feeder, un plan load shedding by PESCO | ibrarahmadmkd@gmail.com | Original | Net = Units - Aux | Link_Generation_Data_Summary.xlsx
2025-04-16 | 2025 | 4 | 16 | Daral Khwar HPS | 36.6 | 36.6 | 36.13 | 867150 | 867150 | 14.71 | 14.5 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7169856.34 | 93018.38 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.13 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-16 | 2025 | 4 | 16 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 0 | 0 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | Both units were shut down on 15.04.2024 at 11:45 AM as per instructions of CEO PEDO. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-04-16 | 2025 | 4 | 16 | Machai HPS | 2.6 | 1.87 | 1.44 | 34120 | 33264 | 23.8 | 22 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 155376.14 | 136094.26 | 856 | Not reported | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-16 | 2025 | 4 | 16 | Malakand-3 HPS | 81 | 52 | 46.51 | 1116129 | 1107770 | 51 | 31.94 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3171213.18 | 2393875.62 | 8359 | As per available hydrology from Irrigation Department Two Units at Malakand- III Power House are running | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-16 | 2025 | 4 | 16 | Pehur HPS | 18 | 5.16 | 4.91 | 117900 | 116000 | 11.88 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 436972 | 1190372 | 1900 | Plant remained operational throughout 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-16 | 2025 | 4 | 16 | Reshun HPS | 4.2 | 1.99 | 1.2 | 26000 | 25404 | 1.7 | 1.59 | 53.03 | 13.48 | 56.7 | 45 | 57153.6 | 770430.53 | 342445.92 | 427984.61 | 596 | Low load. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-16 | 2025 | 4 | 16 | Shishi HPS | 1.8 | 0.53 | 0.44 | 10618 | 10410 | 3 | 0.63 | 21 | 2.47 | 100 | 49 | 43200 | 106704 | 25712.7 | 80991.3 | 208 | The load varies as per the load demand of the local feeder. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-17 | 2025 | 4 | 17 | Daral Khwar HPS | 36.6 | 36.6 | 36.25 | 869980 | 869980 | 14.71 | 14.55 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7193255.63 | 69619.09 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.25 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-17 | 2025 | 4 | 17 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 0 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | Plant remains shut down due to SACDA issues as instructed by PEDO Management. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-04-17 | 2025 | 4 | 17 | Machai HPS | 2.6 | 2.1 | 1.28 | 31852 | 31152 | 23.8 | 20.4 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 145510.99 | 145959.41 | 700 | Unit remained on bar delivering power to National Grid as par available inflow and system conditions | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-17 | 2025 | 4 | 17 | Malakand-3 HPS | 81 | 54 | 50.64 | 1215453 | 1206790 | 51 | 32.24 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3454677.73 | 2110411.07 | 8663 | As per available hydrology from Irrigation Department Two Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-17 | 2025 | 4 | 17 | Pehur HPS | 18 | 5.49 | 5.03 | 120900 | 11900 | 11.88 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 44827.3 | 1582516.7 | 109000 | plant remained operational throughout 24 hrs as per available hudrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-17 | 2025 | 4 | 17 | Reshun HPS | 4.2 | 2.14 | 1.23 | 30000 | 29390 | 1.95 | 1.83 | 61 | 13.48 | 65 | 45 | 65520 | 883209.6 | 396177.2 | 487032.4 | 610 | Outgoing line feeder tripping due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-17 | 2025 | 4 | 17 | Shishi HPS | 1.8 | 0.55 | 0.24 | 5814 | 5700 | 3 | 0.63 | 21 | 2.47 | 100 | 49 | 43200 | 106704 | 14079 | 92625 | 114 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO, less generation due to p/h shutdown for 5 hours due to gravel spill flashing on Forbay side. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-18 | 2025 | 4 | 18 | Daral Khwar HPS | 36.6 | 36.6 | 36.24 | 869780 | 869780 | 14.71 | 14.55 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7191601.97 | 71272.75 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.24 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-18 | 2025 | 4 | 18 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7092 | 0 | 79.57 | 0 | 0 | 0 | 0 | 0 | Both units were shut down as instructed by the managment till the rectification of SCADA. | hassanmushtaq2014@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-18 | 2025 | 4 | 18 | Machai HPS | 2.6 | 1.91 | 1.22 | 30896 | 30184 | 23.8 | 24 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 140989.46 | 150480.94 | 712 | Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 1742Hrs Dated 18-04-2025 with the tripping of 11 KV MACHAI-HPS feeder on earth and instantaneous fault .Call made to Katlang Grid for the inquiry of tripping and power restoration as per their response the line could not be restored as the fault still persist while we have informed operation staff(PESCO) regarding the fault.LS-Operation PESCO, Mardan) was informed, with a request for doing the needful, so as to energize the feeder, at the earliest. Communicated again with line Superintendent (PESCO) for the inquiry of 11 KV Machai HPC line fault, as per his response fault still exists and they are still in progress and trying to rectify the existing fault on line .The fault was cleared by operation staff(PESCO) as removed the tree branches from 11KV Machai-HPC line.11KV Machai-HPC line energized at 1513Hrs Dated 19-04-2025 and Unit synchronized with the system at 1713Hrs. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-18 | 2025 | 4 | 18 | Malakand-3 HPS | 81 | 54 | 39.91 | 957901 | 949220 | 51 | 32.72 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2717332.09 | 2847756.71 | 8681 | Unit # 02 & 03 are on bar while Unit # 01 shutdown having fault in closed loop water system | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-18 | 2025 | 4 | 18 | Pehur HPS | 18 | 5.34 | 5.13 | 123200 | 121000 | 11.88 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 455807 | 1171537 | 2200 | plant operational for 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-18 | 2025 | 4 | 18 | Reshun HPS | 4.2 | 2.1 | 1.21 | 27000 | 26400 | 1.77 | 1.65 | 55 | 13.48 | 59 | 45 | 59472 | 801682.56 | 355872 | 445810.56 | 600 | Line faults | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-18 | 2025 | 4 | 18 | Shishi HPS | 1.8 | 0.7 | 0.27 | 6548 | 6420 | 3 | 0.73 | 24.33 | 2.47 | 100 | 49 | 43200 | 106704 | 15857.4 | 90846.6 | 128 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO, | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-19 | 2025 | 4 | 19 | Daral Khwar HPS | 36.6 | 36.6 | 35.07 | 841630 | 841630 | 14.71 | 14.08 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6958849.33 | 304025.39 | 0 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.24 MW according to the available hydrology. 2. 132 KV supply tripped at 15:35 Hrs and was restored at 15:56 Hrs. 3. Unit No.01, 02 and 03 were synchronised with national grid at 16:04 Hrs, 16:19 Hrs and 16:26 Hrs respectively. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-19 | 2025 | 4 | 19 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | Both units were shut down as instructed by the managment till the rectification of SCADA. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-04-19 | 2025 | 4 | 19 | Machai HPS | 2.6 | 1.62 | 0.4 | 9220 | 8944 | 23.8 | 24 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 41777.42 | 249692.98 | 276 | Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 1742Hrs Dated 18-04-2025 with the tripping of 11 KV MACHAI-HPS feeder on earth and instantaneous fault .Call made to Katlang Grid for the inquiry of tripping and power restoration as per their response the line could not be restored as the fault still persist while we have informed operation staff(PESCO) regarding the fault.LS-Operation PESCO, Mardan) was informed, with a request for doing the needful, so as to energize the feeder, at the earliest. Communicated again with line Superintendent (PESCO) for the inquiry of 11 KV Machai HPC line fault, as per his response fault still exists and they are still in progress and trying to rectify the existing fault on line .The fault was cleared by operation staff(PESCO) as removed the tree branches from 11KV Machai-HPC line.11KV Machai-HPC line energized at 1513Hrs Dated 19-04-2025 and Unit synchronized with the system at 1713Hrs. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-19 | 2025 | 4 | 19 | Malakand-3 HPS | 81 | 60 | 46.92 | 1126102 | 1117540 | 51 | 34.61 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3199181.76 | 2365907.04 | 8562 | Unit # 02 & 03 was already on bar while Unit # 01 synchronized with the system at 20:56Hrs. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-19 | 2025 | 4 | 19 | Pehur HPS | 18 | 5.53 | 4.57 | 109900 | 108000 | 11.88 | 13 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 406836 | 1220508 | 1900 | plant remained operational throughout 24 hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-19 | 2025 | 4 | 19 | Reshun HPS | 4.2 | 1.72 | 1.24 | 27000 | 26388 | 1.78 | 1.65 | 55 | 13.48 | 59.33 | 45 | 59808 | 806211.84 | 355710.24 | 450501.6 | 612 | Line faults | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-19 | 2025 | 4 | 19 | Shishi HPS | 1.8 | 0.76 | 0.37 | 8905 | 8730 | 3 | 0.76 | 25.33 | 2.47 | 100 | 49 | 43200 | 106704 | 21563.1 | 85140.9 | 175 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-20 | 2025 | 4 | 20 | Daral Khwar HPS | 36.6 | 36.6 | 36.42 | 874100 | 874100 | 14.71 | 14.62 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7227321.03 | 35553.69 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.42 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-20 | 2025 | 4 | 20 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0.58 | 100 | 5.7092 | 0 | 79.57 | 0 | 0 | 0 | 0 | 0 | Both units were shut down as instructed by the managment till the rectification of issues in SCADA by the EPC Contractor. | hassanmushtaq2014@gmail.com | Original | Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-04-20 | 2025 | 4 | 20 | Machai HPS | 2.6 | 1.56 | 1.49 | 35208 | 34240 | 23.8 | 22.7 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 159935.04 | 131535.36 | 968 | Unit remained on bar delivering power to National Grid as par available inflow and system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-20 | 2025 | 4 | 20 | Malakand-3 HPS | 81 | 55 | 51 | 1223881 | 1213740 | 51 | 32.6 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3474573.5 | 2090515.3 | 10141 | As per available hydrology from Irrigation Department all Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-20 | 2025 | 4 | 20 | Pehur HPS | 18 | 5.68 | 5.41 | 129900 | 128000 | 12.12 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 482176 | 1145168 | 1900 | plant operational 24 hrs | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-20 | 2025 | 4 | 20 | Reshun HPS | 4.2 | 2.08 | 1.34 | 29000 | 28395 | 1.89 | 1.77 | 59 | 13.48 | 63 | 45 | 63504 | 856033.92 | 382764.6 | 473269.32 | 605 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-20 | 2025 | 4 | 20 | Shishi HPS | 1.8 | 0.53 | 0.2 | 4865 | 4770 | 3 | 0.58 | 19.33 | 2.47 | 100 | 49 | 43200 | 106704 | 11781.9 | 94922.1 | 95 | The load varies as per the load demand of the local feeder. 1.Plan load shedding by PESCO. 2.The power house shutdown due to HT line fault at 5:00 pm 19/4/2025, power house load at 1pm 20/4/2025 on bar 530 kw after replacement of HT line cross with new one. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-21 | 2025 | 4 | 21 | Daral Khwar HPS | 36.6 | 36.6 | 36.28 | 870620 | 870620 | 14.71 | 14.56 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7198547.35 | 64327.37 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.28 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-21 | 2025 | 4 | 21 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.15 | 1.15 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | Both units remain shut down due to SCADA issues.SACDA team deputed by EPC Contractor arrived at site for rectification of issues. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-04-21 | 2025 | 4 | 21 | Machai HPS | 2.6 | 1.97 | 1.47 | 32326 | 32452 | 23.8 | 20.6 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 151583.29 | 139887.11 | 126 | Not reported | engr.atifwazir@gmail.com | Original | CHECK: Net > Units (source me verify karein) | Link_Generation_Data_Summary.xlsx
2025-04-21 | 2025 | 4 | 21 | Malakand-3 HPS | 81 | 71 | 59.82 | 1435593 | 1425110 | 51 | 38.68 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4079662.4 | 1485426.4 | 10483 | As per available hydrology from Irrigation Department all Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-21 | 2025 | 4 | 21 | Pehur HPS | 18 | 5.63 | 5.5 | 132200 | 130000 | 12.12 | 14.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 489710 | 1137634 | 2200 | plant operational 24 hrs | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-21 | 2025 | 4 | 21 | Reshun HPS | 4.2 | 2.38 | 1.21 | 28000 | 27450 | 1.82 | 1.71 | 57 | 13.48 | 60.67 | 45 | 61152 | 824328.96 | 370026 | 454302.96 | 550 | (I). Tariff rate PESCO's Slab wise prevailing rates starting from basic slab of Rs. 13.48/kwh. (II) Low load. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-21 | 2025 | 4 | 21 | Shishi HPS | 1.8 | 0.52 | 0.21 | 5018 | 4920 | 3 | 0.63 | 21 | 2.47 | 100 | 49 | 43200 | 106704 | 12152.4 | 94551.6 | 98 | The power house shutdown due to HT line fault at 5:00 pm 19/4/2025, power house load at 1pm 20/4/2025 on bar 530 kw after replacement of HT line cross with new one. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-22 | 2025 | 4 | 22 | Daral Khwar HPS | 36.6 | 36.6 | 36.19 | 868500 | 868500 | 14.71 | 14.52 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7181018.55 | 81856.17 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.19 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-22 | 2025 | 4 | 22 | Jabori HPS | 10.2 | 7.22 | 2.22 | 52938 | 51420 | 0.31 | 1.73 | 57.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 293567.06 | 1104045.1 | 1518 | Only Unit # 02 was operated smoothly on auto .EPC Contractor's team is working to rectify issue in unit #01. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-04-22 | 2025 | 4 | 22 | Machai HPS | 2.6 | 1.5 | 1.33 | 32760 | 31812 | 23.8 | 21.5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 148593.85 | 142876.55 | 948 | The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 2201Hrs dated 22.04.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault.Unit synchronized with the system at 2221Hrs as 11KV Machai-HPS line energized at 2210Hrs. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-22 | 2025 | 4 | 22 | Malakand-3 HPS | 81 | 71 | 67.07 | 1609799 | 1598970 | 51 | 44.67 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4577371.42 | 987717.38 | 10829 | As per available hydrology from Irrigation Department all Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-22 | 2025 | 4 | 22 | Pehur HPS | 18 | 5.58 | 5.39 | 129300 | 127000 | 12.12 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 478409 | 1148935 | 2300 | plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-22 | 2025 | 4 | 22 | Reshun HPS | 4.2 | 1.91 | 1.23 | 28000 | 27470 | 1.86 | 1.71 | 57 | 13.48 | 62 | 45 | 62496 | 842446.08 | 370295.6 | 472150.48 | 530 | Low load | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-22 | 2025 | 4 | 22 | Shishi HPS | 1.8 | 0.55 | 0.3 | 7222 | 7080 | 3 | 0.61 | 20.33 | 2.47 | 100 | 49 | 43200 | 106704 | 17487.6 | 89216.4 | 142 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-23 | 2025 | 4 | 23 | Daral Khwar HPS | 36.6 | 36.6 | 36.02 | 864380 | 864380 | 14.71 | 14.46 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7146953.15 | 115921.57 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.02 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-23 | 2025 | 4 | 23 | Jabori HPS | 10.2 | 5.3 | 4.4 | 111990 | 109250 | 0.46 | 3.6 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 623730.1 | 773882.06 | 2740 | Plant was operational as per available hydrology. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-04-23 | 2025 | 4 | 23 | Machai HPS | 2.6 | 1.32 | 1.15 | 27372 | 26620 | 23.8 | 18.5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 124342.02 | 167128.38 | 752 | Not reported | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-23 | 2025 | 4 | 23 | Malakand-3 HPS | 81 | 70 | 64.88 | 1557158 | 1546670 | 51 | 43.06 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4427652.21 | 1137436.59 | 10488 | As per available hydrology from Irrigation Department all Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-23 | 2025 | 4 | 23 | Pehur HPS | 18 | 5.53 | 5.28 | 126800 | 125000 | 10.04 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 470875 | 1156469 | 1800 | Plant remained operational throughout 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-23 | 2025 | 4 | 23 | Reshun HPS | 4.2 | 2.84 | 1.33 | 29000 | 28460 | 1.88 | 1.77 | 59 | 13.48 | 62.67 | 45 | 63168 | 851504.64 | 383640.8 | 467863.84 | 540 | Low load. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-23 | 2025 | 4 | 23 | Shishi HPS | 1.8 | 0.58 | 0.26 | 6304 | 6180 | 3 | 0.61 | 20.33 | 2.47 | 100 | 49 | 43200 | 106704 | 15264.6 | 91439.4 | 124 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-24 | 2025 | 4 | 24 | Daral Khwar HPS | 36.6 | 36.6 | 35.57 | 853700 | 853700 | 14.71 | 14.28 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7058647.71 | 204227.01 | 0 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 35.57 MW according to the available hydrology. 2. 132KV supply tripped at 17:33 Hrs and was restored at 17:43 Hrs. 3. Unit No.03, 02 and 01 were synchronized with national grid at 18:01 Hrs, 18:03 Hrs and 18:10 Hrs respectively. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-24 | 2025 | 4 | 24 | Jabori HPS | 10.2 | 49.53 | 5.05 | 121261 | 118370 | 0.62 | 3.9 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 675798 | 721814.16 | 2891 | Unit was operating on full load of 5.10 MW whereas unit # 02 was shut down due to digital input signals testing and some maintenance work. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-04-24 | 2025 | 4 | 24 | Machai HPS | 2.6 | 1.25 | 0.67 | 14714 | 14252 | 23.8 | 24 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 66571.09 | 224899.31 | 462 | 1.Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 0944Hrs,1624Hrs and 1852Hrs dated 24-04-2025 as PTW issued to Operation staff (PESCO) on KATLANG Grid.11KV Machai-HPS line re-energized at 1501Hrs, 1721Hrs and 1952Hrs respectively as PTW canceled by Operation staff (PESCO). Unit synchronized with the system at 1512Hrs,1726Hrs and 2006Hrs respectively and load gradually increased according to available inflow and system condition. 2.The Unit being on bar delivering The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 2055Hrs and 2339Hrs dated 24.04.2025 due to the tripping of 11KV Machai-HPS feeder as 132KV line Mardan tripped.Unit synchronized with the system at 2200Hrs and 2356Hrs respectively as 11KV Machai-HPS line energized at 2123Hrs and 2350Hrs. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-24 | 2025 | 4 | 24 | Malakand-3 HPS | 81 | 70 | 65.59 | 1574212 | 1563670 | 51 | 42.47 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4476318.11 | 1088770.69 | 10542 | As per available hydrology from Irrigation Department all Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-24 | 2025 | 4 | 24 | Pehur HPS | 18 | 5.49 | 5.32 | 127600 | 126000 | 12.12 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 474642 | 1152702 | 1600 | plant operational 24 hrs | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-24 | 2025 | 4 | 24 | Reshun HPS | 4.2 | 2.96 | 1.22 | 29000 | 28470 | 1.89 | 1.77 | 59 | 13.48 | 63.03 | 45 | 63537.6 | 856486.85 | 383775.6 | 472711.25 | 530 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-24 | 2025 | 4 | 24 | Shishi HPS | 1.8 | 0.53 | 0.28 | 6793 | 6660 | 3 | 0.59 | 19.67 | 2.47 | 100 | 49 | 43200 | 106704 | 16450.2 | 90253.8 | 133 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-25 | 2025 | 4 | 25 | Daral Khwar HPS | 36.6 | 36.6 | 36.34 | 872090 | 872090 | 14.71 | 14.58 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7210701.75 | 52172.97 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.34 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-25 | 2025 | 4 | 25 | Jabori HPS | 10.2 | 7.65 | 5.23 | 125661 | 122750 | 0.77 | 4.1 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 700804.3 | 696807.86 | 2911 | Unit # 01 was operational on full load of 5.10 MW ,whereas Unit # 02 was operational on partial load of 02 MW due to ongoing rectification work by SCADA team. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-04-25 | 2025 | 4 | 25 | Machai HPS | 2.6 | 1.3 | 0.9 | 25202 | 24380 | 23.8 | 20 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 113878.98 | 177591.42 | 822 | Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 1223Hrs and 1614Hrs dated 25-04-2025 as PTW issued to Operation staff (PESCO) on KATLANG Grid.11KV Machai-HPS line re-energized at 1253Hrs and 1706Hrs respectively as PTW canceled by Operation staff (PESCO). Unit synchronized with the system at 1317Hrs and 1714 Hrs respectively and load gradually increased according to available inflow and system condition. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-25 | 2025 | 4 | 25 | Malakand-3 HPS | 81 | 72 | 66.57 | 1597598 | 1587490 | 51 | 43.15 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4544507.62 | 1020581.18 | 10108 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-25 | 2025 | 4 | 25 | Pehur HPS | 18 | 5.91 | 5.42 | 130200 | 127000 | 10.04 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 478409 | 1148935 | 3200 | plant remained operational througout 24 hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-25 | 2025 | 4 | 25 | Reshun HPS | 4.2 | 2.16 | 1.27 | 30000 | 29397 | 1.98 | 1.83 | 61 | 13.48 | 66 | 45 | 66528 | 896797.44 | 396271.56 | 500525.88 | 603 | Low load | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-25 | 2025 | 4 | 25 | Shishi HPS | 1.8 | 0.53 | 0.29 | 7038 | 6900 | 3 | 0.6 | 20 | 2.47 | 100 | 49 | 43200 | 106704 | 17043 | 89661 | 138 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-26 | 2025 | 4 | 26 | Daral Khwar HPS | 36.6 | 36.6 | 36.36 | 872710 | 872710 | 14.71 | 14.59 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7215828.09 | 47046.63 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.36 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-26 | 2025 | 4 | 26 | Jabori HPS | 10.2 | 8.06 | 6.39 | 153383 | 150600 | 0.93 | 5.01 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 859805.52 | 537806.64 | 2783 | Unit # 01 of the Plant was operational on full load(5.10 MW) whereas unit # 02 was not taking load beyond 02 MW due to some technical issue.SCADA team is trying to trace out the fault. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-04-26 | 2025 | 4 | 26 | Machai HPS | 2.6 | 1.02 | 0.97 | 23636 | 22748 | 23.8 | 18 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 106255.91 | 185214.49 | 888 | Unit remained on bar delivering power to National Grid as per available inflow and system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-26 | 2025 | 4 | 26 | Malakand-3 HPS | 81 | 71 | 66.58 | 1598023 | 1587480 | 51 | 43.11 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4544479 | 1020609.8 | 10543 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-26 | 2025 | 4 | 26 | Pehur HPS | 18 | 5.63 | 5.2 | 125000 | 123000 | 16.35 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 463341 | 1164003 | 2000 | plant remained operational for 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-26 | 2025 | 4 | 26 | Reshun HPS | 4.2 | 1.86 | 1.19 | 27000 | 26404 | 1.78 | 1.65 | 55 | 13.48 | 59.33 | 45 | 59808 | 806211.84 | 355925.92 | 450285.92 | 596 | Low Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-26 | 2025 | 4 | 26 | Shishi HPS | 1.8 | 0.59 | 0.33 | 7834 | 7680 | 3 | 0.64 | 21.33 | 2.47 | 100 | 49 | 43200 | 106704 | 18969.6 | 87734.4 | 154 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-27 | 2025 | 4 | 27 | Daral Khwar HPS | 36.6 | 36.6 | 35.37 | 848860 | 848860 | 14.71 | 14.2 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7018629.14 | 244245.58 | 0 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 35.37 MW according to the available hydrology. 2. 132KV supply tripped at 09:05 Hrs and was restored at 09:33 Hrs. 3. Unit No.03, 01 and 02 were synchronized with national grid at 09:42 Hrs, 09:48 Hrs and 09:53 Hrs respectively. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-27 | 2025 | 4 | 27 | Jabori HPS | 10.2 | 7.2 | 5.4 | 129679 | 127010 | 1.08 | 4.2 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 725125.49 | 672486.67 | 2669 | Plant was delivering power as per available hydrology. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-04-27 | 2025 | 4 | 27 | Machai HPS | 2.6 | 1.16 | 1.01 | 24192 | 23496 | 23.8 | 18 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 109749.82 | 181720.58 | 696 | Unit remained on bar delivering power to National Grid as per available inflow and system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-27 | 2025 | 4 | 27 | Malakand-3 HPS | 81 | 71 | 66.58 | 1598023 | 1587480 | 51 | 43.79 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4544479 | 1020609.8 | 10543 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-27 | 2025 | 4 | 27 | Pehur HPS | 18 | 5.35 | 5.29 | 127100 | 125000 | 10.04 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 470875 | 1156469 | 2100 | Plant remained operational throughout 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-27 | 2025 | 4 | 27 | Reshun HPS | 4.2 | 2.01 | 1.33 | 32000 | 31411 | 2.22 | 1.96 | 65.3 | 13.48 | 73.87 | 45 | 74457.6 | 1003688.45 | 423420.28 | 580268.17 | 589 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-27 | 2025 | 4 | 27 | Shishi HPS | 1.8 | 0.51 | 0.3 | 7313 | 7170 | 3 | 0.6 | 20 | 2.47 | 100 | 49 | 43200 | 106704 | 17709.9 | 88994.1 | 143 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-28 | 2025 | 4 | 28 | Daral Khwar HPS | 36.6 | 36.6 | 36.63 | 879120 | 879120 | 14.71 | 14.7 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7268827.9 | -5953.18 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.63 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-28 | 2025 | 4 | 28 | Jabori HPS | 10.2 | 8 | 4.5 | 107332 | 104800 | 0.39 | 3.51 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 598324.16 | 799288 | 2532 | Both units were operational as per available hydrology.Testing of SCADA parameters/input signals are also in process. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-04-28 | 2025 | 4 | 28 | Machai HPS | 2.6 | 1.08 | 0.9 | 22984 | 22164 | 23.8 | 19 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 103528.04 | 187942.36 | 820 | Unit tripped at 1046Hrs and 1559Hrs dated 28-04-2025 due to the tripping of 11KV Machai-HPS feeder as 132KV line Mardan tripped.Unit synchronized with the system at 1111Hrs and 1619Hrs as 11KV Machai-HPS line re-energized . | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-28 | 2025 | 4 | 28 | Malakand-3 HPS | 81 | 70 | 67.53 | 1620607 | 1610160 | 51 | 44.41 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4609405.03 | 955683.77 | 10447 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-28 | 2025 | 4 | 28 | Pehur HPS | 18 | 5.33 | 5.28 | 126800 | 125000 | 10.08 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 470875 | 1156469 | 1800 | Plant remained operational throughout 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-28 | 2025 | 4 | 28 | Reshun HPS | 4.2 | 2.04 | 1.13 | 26000 | 25415 | 1.67 | 1.59 | 53.03 | 13.48 | 55.67 | 45 | 56112 | 756389.76 | 342594.2 | 413795.56 | 585 | Line faults | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-28 | 2025 | 4 | 28 | Shishi HPS | 1.8 | 0.65 | 0.3 | 7313 | 7170 | 3 | 0.7 | 23.33 | 2.47 | 100 | 49 | 43200 | 106704 | 17709.9 | 88994.1 | 143 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-29 | 2025 | 4 | 29 | Daral Khwar HPS | 36.6 | 36.6 | 36.55 | 877130 | 877130 | 14.71 | 14.67 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7252373.98 | 10500.74 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.55 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-29 | 2025 | 4 | 29 | Jabori HPS | 10.2 | 10 | 3.86 | 92724 | 90480 | 0.39 | 3.03 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 516568.42 | 881043.74 | 2244 | Both units were operational as per available hydrology.Further units were shut down from time to time as instructed by EPC Contractor team for sake of testing after issuing PTW. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-04-29 | 2025 | 4 | 29 | Machai HPS | 2.6 | 1.17 | 0.86 | 20643 | 20032 | 23.8 | 19 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 93569.47 | 197900.93 | 611 | Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 1105Hrs Dated 29-04-2025 with the Reverse system power due to high system voltage i-e 11.6KV VS 11KV.A call was made to the Katlang Grid to inquire about the high system voltage and request stabilization, as the machine could not be synchronized due to the elevated voltage. However, their response was that they could neither reduce the voltage nor change the tap setting, as per the Grid Incharge's directives.Unit synchronized with the system at 1439Hrs as system voltage stabilize . | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-29 | 2025 | 4 | 29 | Malakand-3 HPS | 81 | 70 | 67.12 | 1610859 | 1600170 | 51 | 43.98 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4580806.66 | 984282.14 | 10689 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-29 | 2025 | 4 | 29 | Pehur HPS | 18 | 5.36 | 5.3 | 127200 | 125000 | 10.04 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 470875 | 1156469 | 2200 | plant remained operational since 24 hrs as per available head. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-29 | 2025 | 4 | 29 | Reshun HPS | 4.2 | 1.97 | 1.19 | 29000 | 28410 | 1.89 | 1.78 | 59.17 | 13.48 | 63 | 45 | 63504 | 856033.92 | 382966.8 | 473067.12 | 590 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-29 | 2025 | 4 | 29 | Shishi HPS | 1.8 | 0.72 | 0.33 | 7834 | 7680 | 3 | 0.79 | 26.33 | 2.47 | 100 | 49 | 43200 | 106704 | 18969.6 | 87734.4 | 154 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO, less generation is due to p/h shutdown for 4 hours for gravel spill flashing on Forbay side. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-30 | 2025 | 4 | 30 | Daral Khwar HPS | 36.6 | 36.6 | 36.53 | 876700 | 876700 | 14.71 | 14.66 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7248818.61 | 14056.11 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.53 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-30 | 2025 | 4 | 30 | Jabori HPS | 10.2 | 5.1 | 2.65 | 63545 | 61620 | 0.39 | 2.1 | 70 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 351800.9 | 1045811.26 | 1925 | Both units were operated as per available hydrology.Meanwhile testing/fault rectification by EPC Contractor SCADA team is also in progress due to which smooth plant Operation is not possible. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-04-30 | 2025 | 4 | 30 | Machai HPS | 2.6 | 1.54 | 0.68 | 16301 | 15620 | 23.8 | 20 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 72961.02 | 218509.38 | 681 | Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 0439Hrs Dated 30-04-2025 with the Reverse system power due to high system voltage i-e 11.6KV VS 11KV.A call was made to the Katlang Grid to inquire about the high system voltage and request stabilization, as the machine could not be synchronized due to the elevated voltage. However, their response was that they could neither reduce the voltage nor change the tap setting, as per the Grid Incharge's directives.11KV Machai-HPS line de-energized at 1056Hrs as PTW issued to Operation staff (PESCO) on KATLANG Grid.11KV Machai-HPS line re-energized at 1318Hrs as PTW canceled by Operation staff (PESCO) and Unit synchronized with the system at 1325Hrs as system voltage stabilize . | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-30 | 2025 | 4 | 30 | Malakand-3 HPS | 81 | 71 | 66.68 | 1600355 | 1589790 | 51 | 43.42 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4551091.83 | 1013996.97 | 10565 | As per available hydrology from Irrigation Department all Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-30 | 2025 | 4 | 30 | Pehur HPS | 18 | 5.56 | 5.43 | 130300 | 128000 | 10.04 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 482176 | 1145168 | 2300 | Plant remained operational for 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-30 | 2025 | 4 | 30 | Reshun HPS | 4.2 | 1.82 | 1.1 | 26000 | 25417 | 1.7 | 1.59 | 53.03 | 13.48 | 56.67 | 45 | 57120 | 769977.6 | 342621.16 | 427356.44 | 583 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-04-30 | 2025 | 4 | 30 | Shishi HPS | 1.8 | 0.61 | 0.37 | 8905 | 8730 | 3 | 0.69 | 23 | 2.47 | 100 | 49 | 43200 | 106704 | 21563.1 | 85140.9 | 175 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-01 | 2025 | 5 | 1 | Daral Khwar HPS | 36.6 | 36.6 | 22.43 | 538210 | 538210 | 27.14 | 9 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 4450081.74 | 2812792.98 | 0 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 22.43 MW according to the available hydrology. 2. 132KV supply tripped at 14:46 Hrs and has not been restored yet. RCC reported that the delay in restoring 132KV PESCO Supply line is due to issue with the opening and closing of Swat breaker-3 | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-01 | 2025 | 5 | 1 | Jabori HPS | 10.2 | 10 | 6.6 | 159576 | 156960 | 8.54 | 5.2 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 896116.03 | 501496.13 | 2616 | Both units were delivering power as per available hydrology. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-01 | 2025 | 5 | 1 | Machai HPS | 2.6 | 1.67 | 1.39 | 34624 | 33572 | 31.6 | 22.2 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 156814.81 | 134655.59 | 1052 | Unit remained on bar delivering power to National Grid as per available inflow and system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-01 | 2025 | 5 | 1 | Malakand-3 HPS | 81 | 73 | 65.42 | 1570105 | 1560270 | 51 | 42.87 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4466584.93 | 1098503.87 | 9835 | All three units are on bar. (132KV supply failed at 10:48Hrs & restored at 11:04Hrs dated 01-05-2025, after that all the three units were synchronized). | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-01 | 2025 | 5 | 1 | Pehur HPS | 18 | 5.97 | 5.43 | 130400 | 127000 | 14.72 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 478409 | 1148935 | 3400 | Plant remained operational for 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-01 | 2025 | 5 | 1 | Reshun HPS | 4.2 | 1.74 | 1.2 | 28000 | 27396 | 1.89 | 1.71 | 57.13 | 13.48 | 63.03 | 45 | 63537.6 | 856486.85 | 369298.08 | 487188.77 | 604 | Low load | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-01 | 2025 | 5 | 1 | Shishi HPS | 1.8 | 0.59 | 0.39 | 9364 | 9180 | 3 | 0.68 | 22.67 | 2.47 | 100 | 49 | 43200 | 106704 | 22674.6 | 84029.4 | 184 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-02 | 2025 | 5 | 2 | Daral Khwar HPS | 36.6 | 36.6 | 22.08 | 530040 | 530040 | 27.14 | 8.86 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 4382529.73 | 2880344.99 | 0 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 22.08 MW according to the available hydrology. 2. 132 KV Supply line was restored at 09:15 Hrs. 3. Unit No.02, 03 and 01 were synchronized with national grid at 09:24 Hrs, 09:25 Hrs and 09:28 Hrs respectively. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-02 | 2025 | 5 | 2 | Jabori HPS | 10.2 | 9 | 7.3 | 175468 | 172850 | 8.54 | 5.73 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 986835.22 | 410776.94 | 2618 | Both units were in operation as per available hydrology. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-02 | 2025 | 5 | 2 | Machai HPS | 2.6 | 1.76 | 1.39 | 33716 | 32780 | 31.6 | 22 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 153115.38 | 138355.02 | 936 | Unit remained on bar and delivering power to National Grid, got tripped at 2241Hrs dated 02-05-2025 due to the tripping of 11KV Machai-HPS feeder as 132KV line Mardan tripped.Unit synchronized with the system at 2340Hrs as 11KV Machai-HPS line energized at 2335Hrs. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-02 | 2025 | 5 | 2 | Malakand-3 HPS | 81 | 72 | 67.51 | 1620199 | 1610100 | 51 | 43.6 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4609233.27 | 955855.53 | 10099 | All three units are on bar as per available hydrology from irrigation department. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-02 | 2025 | 5 | 2 | Pehur HPS | 18 | 5.65 | 5.56 | 133400 | 131000 | 14.72 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 493477 | 1133867 | 2400 | plant remained operational since 24 hrs as per available head. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-02 | 2025 | 5 | 2 | Reshun HPS | 4.2 | 2.01 | 1.19 | 26000 | 26400 | 1.72 | 1.59 | 53.03 | 13.48 | 57.4 | 45 | 57859.2 | 779942.02 | 355872 | 424070.02 | 400 | Low load | zafar.src@gmail.com | Original | CHECK: Net > Units (source me verify karein) | Link_Generation_Data_Summary.xlsx
2025-05-02 | 2025 | 5 | 2 | Shishi HPS | 1.8 | 0.63 | 0.33 | 7895 | 7740 | 3 | 0.72 | 24 | 2.47 | 100 | 49 | 43200 | 106704 | 19117.8 | 87586.2 | 155 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-03 | 2025 | 5 | 3 | Daral Khwar HPS | 36.6 | 36.6 | 36.39 | 873440 | 873440 | 27.14 | 14.61 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7221863.95 | 41010.77 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.39 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-03 | 2025 | 5 | 3 | Jabori HPS | 10.2 | 7 | 5.7 | 136661 | 134200 | 8.54 | 4.46 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 766174.64 | 631437.52 | 2461 | Unit # 01 of the plant was delivering power as per available hydrology whereas unit # 02 tripped at 11: 05 and remains shut down till now. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-03 | 2025 | 5 | 3 | Machai HPS | 2.6 | 1.76 | 1.55 | 37396 | 36476 | 31.6 | 24 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 170379.4 | 121091 | 920 | Unit remained on bar delivering power to National Grid, got tripped at 0217Hrs dated 03-05-2025 due to the tripping of 11KV Machai-HPS feeder as 132KV line Mardan tripped.Unit synchronized with the system at 0243Hrs as 11KV Machai-HPC line re-energized at 0239Hrs. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-03 | 2025 | 5 | 3 | Malakand-3 HPS | 81 | 78 | 78 | 1661647 | 1651790 | 51 | 45.22 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4728579.23 | 836509.57 | 9857 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-03 | 2025 | 5 | 3 | Pehur HPS | 18 | 5.69 | 5.42 | 130000 | 127000 | 14.72 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 478409 | 1148935 | 3000 | plant remained operational since 24 hrs as per available head. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-03 | 2025 | 5 | 3 | Reshun HPS | 4.2 | 1.91 | 1.11 | 26000 | 25388 | 1.67 | 1.59 | 53.03 | 13.48 | 55.67 | 45 | 56112 | 756389.76 | 342230.24 | 414159.52 | 612 | Low load. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-03 | 2025 | 5 | 3 | Shishi HPS | 1.8 | 0.63 | 0.35 | 8476 | 8310 | 3 | 0.67 | 22.33 | 2.47 | 100 | 49 | 43200 | 106704 | 20525.7 | 86178.3 | 166 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-04 | 2025 | 5 | 4 | Daral Khwar HPS | 36.6 | 36.6 | 36.25 | 869990 | 869990 | 27.14 | 14.55 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7193338.32 | 69536.4 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.25 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-04 | 2025 | 5 | 4 | Jabori HPS | 10.2 | 5.1 | 4.76 | 115131 | 112800 | 8.54 | 3.76 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 643997.76 | 753614.4 | 2331 | Unit # 01 was in operation on full load whereas unit # 02 was shut down by EPC Contractor team due to tripping issue. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-04 | 2025 | 5 | 4 | Machai HPS | 2.6 | 1.46 | 1.42 | 34828 | 33788 | 31.6 | 22.7 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 157823.75 | 133646.65 | 1040 | Unit remained on bar delivering power to National Grid as per available inflow and system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-04 | 2025 | 5 | 4 | Malakand-3 HPS | 81 | 72 | 68.66 | 1647728 | 1637940 | 51 | 44.74 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4688930.84 | 876157.96 | 9788 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-04 | 2025 | 5 | 4 | Pehur HPS | 18 | 5.59 | 5.52 | 132500 | 130000 | 14.72 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 489710 | 1137634 | 2500 | plant remained operational since 24 hrs as per available head. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-04 | 2025 | 5 | 4 | Reshun HPS | 4.2 | 2.1 | 1.23 | 28000 | 27225 | 1.88 | 1.71 | 57.13 | 13.48 | 62.8 | 45 | 63302.4 | 853316.35 | 366993 | 486323.35 | 775 | Low load. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-04 | 2025 | 5 | 4 | Shishi HPS | 1.8 | 0.62 | 0.15 | 3703 | 3630 | 3 | 0.67 | 22.33 | 2.47 | 100 | 49 | 43200 | 106704 | 8966.1 | 97737.9 | 73 | The power house connected with the local feeder again on bar 631kw at 12:20 pm, after cleaning of silt, gravels through diversion gates. (a) Less generation is due to the total outage of power house 23 hours 5 minutes. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-05 | 2025 | 5 | 5 | Daral Khwar HPS | 36.6 | 36.6 | 36.3 | 871210 | 871210 | 27.14 | 14.57 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7203425.64 | 59449.08 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.3 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-05 | 2025 | 5 | 5 | Jabori HPS | 10.2 | 5.1 | 4.99 | 119696 | 117360 | 8.54 | 3.91 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 670031.71 | 727580.45 | 2336 | Unit # 01 is delivering power on full load whereas unit # 02 is shut down due to 100% Stator Earth Fault. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-05 | 2025 | 5 | 5 | Machai HPS | 2.6 | 1.68 | 1.44 | 35128 | 34236 | 31.6 | 22.7 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 159916.36 | 131554.04 | 892 | Unit remained on bar delivering power to National Grid as per available inflow and system conditions . | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-05 | 2025 | 5 | 5 | Malakand-3 HPS | 81 | 74 | 69.61 | 1670703 | 1660330 | 51 | 45.39 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4753026.69 | 812062.11 | 10373 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-05 | 2025 | 5 | 5 | Pehur HPS | 18 | 5.77 | 5.55 | 133300 | 131000 | 14.72 | 14.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 493477 | 1133867 | 2300 | Plant remained operational throughout 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-05 | 2025 | 5 | 5 | Reshun HPS | 4.2 | 1.77 | 1.13 | 27000 | 26400 | 1.78 | 1.65 | 55 | 13.48 | 59.17 | 45 | 59640 | 803947.2 | 355872 | 448075.2 | 600 | Low load. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-05 | 2025 | 5 | 5 | Shishi HPS | 1.8 | 0.63 | 0.38 | 9180 | 9000 | 3 | 0.73 | 24.33 | 2.47 | 100 | 49 | 43200 | 106704 | 22230 | 84474 | 180 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-06 | 2025 | 5 | 6 | Daral Khwar HPS | 36.6 | 36.6 | 36.52 | 876480 | 876480 | 27.14 | 14.66 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7246999.58 | 15875.14 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.52 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-06 | 2025 | 5 | 6 | Jabori HPS | 10.2 | 5.1 | 5.02 | 120396 | 118080 | 8.54 | 3.93 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 674142.34 | 723469.82 | 2316 | Unit # 01 was delivering power on full load whereas unit # 02 is still shut down. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-06 | 2025 | 5 | 6 | Machai HPS | 2.6 | 1.66 | 1.07 | 24496 | 23804 | 31.6 | 22.7 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 111188.48 | 180281.92 | 692 | 1. Unit being on bar delivering power to National Grid as per available water inflow and system conditions, precautionary shut down at 0845Hrs dated 06-05-2025 on the request of GSO staff (Katlang Grid) as PTW issued to Operation staff (PESCO) on KATLANG Grid.11KV Machai-HPS line re-energized at 1420Hrs as PTW canceled by Operation staff (PESCO). Unit synchronized with the system at 1436Hrs and load gradually increased according to available inflow and system condition. 2.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 1456Hrs dated 06.05.2025 due to the tripping of 11KV Machai-HPS feeder as 132KV line Mardan tripped.Unit synchronized with the system at 1510Hrs as 11KV Machai-HPS line energized at 1502Hrs | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-06 | 2025 | 5 | 6 | Malakand-3 HPS | 81 | 74 | 68.98 | 1655583 | 1645040 | 51 | 44.28 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4709256.01 | 855832.79 | 10543 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-06 | 2025 | 5 | 6 | Pehur HPS | 18 | 5.9 | 5.73 | 137500 | 135000 | 15.33 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 508545 | 1118799 | 2500 | plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-06 | 2025 | 5 | 6 | Reshun HPS | 4.2 | 1.92 | 1.11 | 23000 | 22500 | 1.55 | 1.41 | 46.93 | 13.48 | 51.73 | 45 | 52147.2 | 702944.26 | 303300 | 399644.26 | 500 | Low load | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-06 | 2025 | 5 | 6 | Shishi HPS | 1.8 | 0.58 | 0.42 | 10190 | 9990 | 3 | 0.68 | 22.67 | 2.47 | 100 | 49 | 43200 | 106704 | 24675.3 | 82028.7 | 200 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-07 | 2025 | 5 | 7 | Daral Khwar HPS | 36.6 | 36.6 | 36.68 | 880410 | 880410 | 27.14 | 14.72 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7279494 | -16619.28 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.68 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-07 | 2025 | 5 | 7 | Jabori HPS | 10.2 | 5.1 | 5.1 | 122501 | 122180 | 8.54 | 4 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 697550.06 | 700062.1 | 321 | Unit # 01 was delivering power on full load whereas unit # 02 was shut down due to Fault. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-07 | 2025 | 5 | 7 | Machai HPS | 2.6 | 1.55 | 1.39 | 33516 | 32516 | 31.6 | 21.6 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 151882.24 | 139588.16 | 1000 | The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 1409Hrs dated 07.05.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault.Unit synchronized with the system at 1427Hrs as 11KV Machai-HPS line energized at 1414Hrs. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-07 | 2025 | 5 | 7 | Malakand-3 HPS | 81 | 73 | 67.77 | 1626379 | 1615860 | 51 | 44.62 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4625722.42 | 939366.38 | 10519 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-07 | 2025 | 5 | 7 | Pehur HPS | 18 | 6.84 | 5.82 | 139800 | 137000 | 14.72 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 516079 | 1111265 | 2800 | Unit#01 taken on bar at 1550 Hrs dt. 07-05-2025 in parallel with unit#03 because minimum operating head was achieved. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-07 | 2025 | 5 | 7 | Reshun HPS | 4.2 | 1.42 | 1.01 | 24000 | 23270 | 1.62 | 1.47 | 48.97 | 13.48 | 54 | 45 | 54432 | 733743.36 | 313679.6 | 420063.76 | 730 | Low load | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-07 | 2025 | 5 | 7 | Shishi HPS | 1.8 | 0.58 | 0.38 | 9149 | 8970 | 3 | 0.71 | 23.67 | 2.47 | 100 | 49 | 43200 | 106704 | 22155.9 | 84548.1 | 179 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-08 | 2025 | 5 | 8 | Daral Khwar HPS | 36.6 | 36.6 | 36.01 | 864250 | 864250 | 27.14 | 14.45 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7145878.28 | 116996.44 | 0 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.01 MW according to the available hydrology. 2. 132 KV Supply line failed at 14:29 Hrs and was restored at 14:45 Hrs. 3. Unit No.02, 03 and 01 were synchronized with national grid at 14:50 Hrs, 14:53 Hrs and 14:56 Hrs respectively. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-08 | 2025 | 5 | 8 | Jabori HPS | 10.2 | 5.17 | 5.05 | 121378 | 119050 | 8.54 | 3.96 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 679680.26 | 717931.9 | 2328 | Unit # 01 was delivering power into the national grid on full load whereas unit # 02 still shut down due to some maintenance issues. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-08 | 2025 | 5 | 8 | Machai HPS | 2.6 | 1.45 | 1.36 | 32808 | 31988 | 31.6 | 21.2 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 149415.95 | 142054.45 | 820 | Unit remained on bar delivering power to National Grid as per available inflow and system conditions | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-08 | 2025 | 5 | 8 | Malakand-3 HPS | 81 | 70 | 65.97 | 1583282 | 1573370 | 51 | 43.97 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4504086.3 | 1061002.5 | 9912 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-08 | 2025 | 5 | 8 | Pehur HPS | 18 | 6.74 | 6.55 | 157300 | 154000 | 14.72 | 17 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 580118 | 1047226 | 3300 | Plant remained operational for 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-08 | 2025 | 5 | 8 | Reshun HPS | 4.2 | 1.73 | 1.07 | 25000 | 24388 | 1.67 | 1.53 | 51 | 13.48 | 55.73 | 45 | 56179.2 | 757295.62 | 328750.24 | 428545.38 | 612 | Low load. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-08 | 2025 | 5 | 8 | Shishi HPS | 1.8 | 0.61 | 0.41 | 9761 | 9570 | 3 | 0.74 | 24.67 | 2.47 | 100 | 49 | 43200 | 106704 | 23637.9 | 83066.1 | 191 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-09 | 2025 | 5 | 9 | Daral Khwar HPS | 36.6 | 36.6 | 34.51 | 828120 | 828120 | 27.14 | 13.85 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6847144.6 | 415730.12 | 0 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 34.51 MW according to the available hydrology. 2. 132 KV Supply line failed at 0752 Hrs and was restored at 0901 Hrs. 3. Unit No.02, 03 and 01 were synchronized with national grid at 0910 Hrs, 0915 Hrs and 0920 Hrs respectively | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-09 | 2025 | 5 | 9 | Jabori HPS | 10.2 | 5.16 | 3.99 | 95894 | 93890 | 8.54 | 3.13 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 536036.79 | 861575.37 | 2004 | Only unit # 01 was operational on full load.Unit # 02 shut down due to maintenance. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-09 | 2025 | 5 | 9 | Machai HPS | 2.6 | 1.37 | 1.16 | 29032 | 28116 | 31.6 | 18.7 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 131329.84 | 160140.56 | 916 | Unit remained on bar delivering power to National Grid as per available inflow and system conditions | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-09 | 2025 | 5 | 9 | Malakand-3 HPS | 81 | 73 | 64.75 | 1554048 | 1543850 | 51 | 43.08 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4419579.39 | 1145509.4 | 10198 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-09 | 2025 | 5 | 9 | Pehur HPS | 18 | 7.37 | 6.49 | 155800 | 153000 | 14.72 | 17 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 576351 | 1050993 | 2800 | plant remained shutdown for 00:59 Min in search of dead body in the canal as per instructions of irrigation Sub Engineer. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-09 | 2025 | 5 | 9 | Reshun HPS | 4.2 | 1.74 | 1.16 | 26000 | 25385 | 1.68 | 1.59 | 53.03 | 13.48 | 56 | 45 | 56448 | 760919.04 | 342189.8 | 418729.24 | 615 | (I). Tariff rate PESCO's Slab wise prevailing rates starting from basic slab of Rs. 13.48/kwh. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-09 | 2025 | 5 | 9 | Shishi HPS | 1.8 | 0.71 | 0.29 | 6946 | 6810 | 3 | 0.82 | 27.33 | 2.47 | 100 | 49 | 43200 | 106704 | 16820.7 | 89883.3 | 136 | 1.less generation is due the condition of inflow is not suitable for operation. 2.flushing of sand and debris through flushing valve is in progress. Issues it Shishi HPS a. leakage of unit no3 runner assembly. b. loss of hydrology in unit no.1 due to damaged runner blades need to repair as soon as possible. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-10 | 2025 | 5 | 10 | Daral Khwar HPS | 36.6 | 36.6 | 36.71 | 880990 | 880990 | 27.14 | 14.73 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7284289.62 | -21414.9 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.71 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-10 | 2025 | 5 | 10 | Jabori HPS | 10.2 | 5.16 | 5.1 | 121320 | 119020 | 8.54 | 4 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 679508.98 | 718103.18 | 2300 | Unit # 01 was operational on full load whereas unit # 02 was shut down due to forced maintenance. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-10 | 2025 | 5 | 10 | Machai HPS | 2.6 | 1.11 | 0.94 | 23184 | 22352 | 31.6 | 16 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 104406.19 | 187064.21 | 832 | Unit remained on bar delivering power to National Grid as per available inflow and system conditions | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-10 | 2025 | 5 | 10 | Malakand-3 HPS | 81 | 70 | 65.91 | 1581953 | 1571830 | 51 | 43.29 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4499677.74 | 1065411.06 | 10123 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-10 | 2025 | 5 | 10 | Pehur HPS | 18 | 7.37 | 4 | 134200 | 131000 | 15.33 | 13.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 493477 | 1133867 | 3200 | Plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-10 | 2025 | 5 | 10 | Reshun HPS | 4.2 | 1.6 | 1.16 | 27000 | 26380 | 1.78 | 1.65 | 55 | 13.48 | 59.2 | 45 | 59673.6 | 804400.13 | 355602.4 | 448797.73 | 620 | Low load | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-10 | 2025 | 5 | 10 | Shishi HPS | 1.8 | 0.41 | 0.33 | 7956 | 7800 | 3 | 0.87 | 29 | 2.47 | 100 | 49 | 43200 | 106704 | 19266 | 87438 | 156 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-11 | 2025 | 5 | 11 | Daral Khwar HPS | 36.6 | 36.6 | 36.61 | 878710 | 878710 | 27.14 | 14.7 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7265437.89 | -2563.17 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.61 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-11 | 2025 | 5 | 11 | Jabori HPS | 10.2 | 5.2 | 5.1 | 124480 | 122000 | 8.54 | 4 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 696522.4 | 701089.76 | 2480 | Unit # 01 was operational on full load of 5.20 MW whereas unit # 02 remained shut down due to maintenance. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-11 | 2025 | 5 | 11 | Machai HPS | 2.6 | 1.42 | 0.96 | 23740 | 22924 | 31.6 | 17.5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 107078 | 184392.4 | 816 | 1.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 1813Hrs and 1936Hrs dated 11.05.2025 due to the tripping of 11KV Machai-HPS feeder as 132KV line Mardan tripped.Unit synchronized with the system at 1909Hrs and 1941Hrs respectively as 11KV Machai-HPS line energized at 1820Hrs and 1938Hrs . 2.Unit being on bar delivering power to National Grid as per available water inflow and system conditions, precautionary shut down at 2050Hrs dated 11-05-2025 on the request of GSO staff (Katlang Grid) as PTW issued to Operation staff (PESCO) on KATLANG Grid.11KV Machai-HPS line re-energized at 2145Hrs as PTW canceled by Operation staff (PESCO). Unit synchronized with the system at 2217Hrs and load gradually increased according to available inflow and system condition. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-11 | 2025 | 5 | 11 | Malakand-3 HPS | 81 | 70 | 65.96 | 1582934 | 1572800 | 51 | 43.1 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4502454.56 | 1062634.24 | 10134 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-11 | 2025 | 5 | 11 | Pehur HPS | 18 | 6.29 | 5.6 | 126300 | 122000 | 15.33 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 459574 | 1167770 | 4300 | Plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-11 | 2025 | 5 | 11 | Reshun HPS | 4.2 | 1.92 | 1.21 | 29000 | 28402 | 1.88 | 1.77 | 59 | 13.48 | 62.8 | 45 | 63302.4 | 853316.35 | 382858.96 | 470457.39 | 598 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-11 | 2025 | 5 | 11 | Shishi HPS | 1.8 | 0.62 | 0.38 | 9241 | 9060 | 3 | 0.75 | 25 | 2.47 | 100 | 49 | 43200 | 106704 | 22378.2 | 84325.8 | 181 | Less generation is due to 1.PESCO announced a scheduled electricity blackout on dated 11/5/2025 from 1:00 AM to 5:00 AM in Drosh and surrounding Chitral areas the previous night due to security concerns. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-12 | 2025 | 5 | 12 | Daral Khwar HPS | 36.6 | 36.6 | 36.66 | 879840 | 879840 | 27.14 | 14.71 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7274781.07 | -11906.35 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.66 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-12 | 2025 | 5 | 12 | Jabori HPS | 10.2 | 5.2 | 5.1 | 122490 | 120000 | 8.54 | 4 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 685104 | 712508.16 | 2490 | Unit # 01 was operation on full load whereas unit # 02 is still shut down due to maintenance. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-12 | 2025 | 5 | 12 | Machai HPS | 2.6 | 1.71 | 1.35 | 32860 | 31944 | 31.6 | 31 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 149210.42 | 142259.98 | 916 | The load could not be increased in accordance with the available inflow due to high system voltage, which led to elevated stator temperatures. The unit remained synchronized, delivering power to the National Grid as per system conditions | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-12 | 2025 | 5 | 12 | Malakand-3 HPS | 81 | 70 | 60.46 | 1450972 | 1440560 | 51 | 42.96 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4123891.11 | 1441197.69 | 10412 | As per available hydrology from Irrigation Department all the Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-12 | 2025 | 5 | 12 | Pehur HPS | 18 | 5.95 | 5.51 | 132300 | 128000 | 14.92 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 482176 | 1145168 | 4300 | Plant operational for 24 Hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-12 | 2025 | 5 | 12 | Reshun HPS | 4.2 | 1.9 | 1.16 | 27000 | 26410 | 1.78 | 1.65 | 55 | 13.48 | 59.17 | 45 | 59640 | 803947.2 | 356006.8 | 447940.4 | 590 | Low load | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-12 | 2025 | 5 | 12 | Shishi HPS | 1.8 | 0.7 | 0.37 | 8843 | 8670 | 3 | 0.82 | 27.33 | 2.47 | 100 | 49 | 43200 | 106704 | 21414.9 | 85289.1 | 173 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-13 | 2025 | 5 | 13 | Daral Khwar HPS | 36.6 | 36.6 | 36.65 | 879600 | 879600 | 27.14 | 14.71 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7272796.68 | -9921.96 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.65 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-13 | 2025 | 5 | 13 | Jabori HPS | 10.2 | 5.2 | 4.97 | 119510 | 117000 | 8.54 | 3.9 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 667976.4 | 729635.76 | 2510 | Unit was operational on full load whereas unit # 02 is still shut down due to maintenance.A team hired by EPC Contractor for testing of generator's windings of unit # 02 not yet mobilize at site. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-13 | 2025 | 5 | 13 | Machai HPS | 2.6 | 1.6 | 1.44 | 34848 | 33836 | 31.6 | 31.5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 158047.96 | 133422.44 | 1012 | 1.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 0331Hrs dated 13.05.2025 due to the tripping of 11KV Machai-HPS feeder as 132KV line Mardan tripped.Unit synchronized with the system at 0345Hrs as 11KV Machai-HPS line energized at 0343Hrs . 2.The load could not be increased in accordance with the available inflow due to high system voltage, which led to elevated stator temperatures. The unit remained on bar, delivering power to the National Grid as per system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-13 | 2025 | 5 | 13 | Malakand-3 HPS | 81 | 75 | 63.25 | 1517986 | 1507050 | 51 | 44.38 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4314232.04 | 1250856.76 | 10936 | All the three units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-13 | 2025 | 5 | 13 | Pehur HPS | 18 | 5.94 | 5.8 | 137600 | 133000 | 15.33 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 501011 | 1126333 | 4600 | Plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-13 | 2025 | 5 | 13 | Reshun HPS | 4.2 | 1.5 | 1.13 | 25000 | 24420 | 1.67 | 1.53 | 51 | 13.48 | 55.67 | 45 | 56112 | 756389.76 | 329181.6 | 427208.16 | 580 | Low load | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-13 | 2025 | 5 | 13 | Shishi HPS | 1.8 | 0.6 | 0.44 | 10649 | 10440 | 3 | 0.72 | 24 | 2.47 | 100 | 49 | 43200 | 106704 | 25786.8 | 80917.2 | 209 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-14 | 2025 | 5 | 14 | Daral Khwar HPS | 36.6 | 36.6 | 36.65 | 879660 | 879660 | 27.14 | 14.71 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7273292.78 | -10418.06 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.65 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-14 | 2025 | 5 | 14 | Jabori HPS | 10.2 | 5.12 | 5.12 | 122951 | 120600 | 8.54 | 4 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 688529.52 | 709082.64 | 2351 | Unit # 01 was delivering power on full Load whereas unit # 02 was shut down due to maintenance. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-14 | 2025 | 5 | 14 | Machai HPS | 2.6 | 1.53 | 1.1 | 27344 | 26400 | 31.6 | 32 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 123314.4 | 168156 | 944 | 1.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 0545Hrs dated 14.05.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault.Unit synchronized with the system at 0612Hrs as 11KV Machai-HPS line energized at 0548Hrs . 2.The load could not be increased in accordance with the available inflow due to high system voltage, which led to elevated stator temperatures. The unit remained on bar, delivering power to the National Grid as per system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-14 | 2025 | 5 | 14 | Malakand-3 HPS | 81 | 72 | 68.27 | 1638423 | 1627290 | 51 | 43.86 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4658443.08 | 906645.72 | 11133 | All units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-14 | 2025 | 5 | 14 | Pehur HPS | 18 | 6.39 | 5.93 | 142500 | 138000 | 14.92 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 519846 | 1107498 | 4500 | plant remained operational throughout 24 hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-14 | 2025 | 5 | 14 | Reshun HPS | 4.2 | 1.62 | 1.17 | 27000 | 26470 | 1.78 | 1.65 | 55 | 13.48 | 59.37 | 45 | 59841.6 | 806664.77 | 356815.6 | 449849.17 | 530 | Load load. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-14 | 2025 | 5 | 14 | Shishi HPS | 1.8 | 0.69 | 0.29 | 6946 | 6810 | 3 | 0.8 | 26.67 | 2.47 | 100 | 49 | 43200 | 106704 | 16820.7 | 89883.3 | 136 | Less generation due to On May 13, 2025, the power house was shut down for routine flushing of the forebay due to excessive sand and silt accumulation. Flushing commenced at 9:00 AM and concluded at 12:00 PM. After thoroughly flushing through the sand trap flushing gates, the power plant was loaded to 666 kW, meeting the required feeder load. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-15 | 2025 | 5 | 15 | Daral Khwar HPS | 36.6 | 36.6 | 36.63 | 879190 | 879190 | 27.14 | 14.7 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7269406.68 | -6531.96 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.63 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-15 | 2025 | 5 | 15 | Jabori HPS | 10.2 | 5.1 | 5.1 | 122403 | 120050 | 8.54 | 4 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 685389.46 | 712222.7 | 2353 | Unit# 01 was operational on full load whereas unit # 02 was shut down due to some necessary maintenance. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-15 | 2025 | 5 | 15 | Machai HPS | 2.6 | 2 | 1.37 | 33000 | 32032 | 31.6 | 32 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 149621.47 | 141848.93 | 968 | The load could not be increased in accordance with the available inflow due to high system voltage, which led to elevated stator temperatures. The unit remained synchronized, delivering power to the National Grid as per system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-15 | 2025 | 5 | 15 | Malakand-3 HPS | 81 | 75 | 69.83 | 1675863 | 1664210 | 51 | 45.49 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4764133.97 | 800954.83 | 11653 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-15 | 2025 | 5 | 15 | Pehur HPS | 18 | 6.11 | 6 | 143500 | 139000 | 15.33 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 523613 | 1103731 | 4500 | Plant operational 24 hrs | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-15 | 2025 | 5 | 15 | Reshun HPS | 4.2 | 1.69 | 1.05 | 24000 | 23490 | 1.66 | 1.47 | 48.97 | 13.48 | 55.37 | 45 | 55809.6 | 752313.41 | 316645.2 | 435668.21 | 510 | Low load | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-15 | 2025 | 5 | 15 | Shishi HPS | 1.8 | 0.63 | 0.48 | 11536 | 11310 | 3 | 0.76 | 25.33 | 2.47 | 100 | 49 | 43200 | 106704 | 27935.7 | 78768.3 | 226 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-16 | 2025 | 5 | 16 | Daral Khwar HPS | 36.6 | 36.6 | 36.59 | 878230 | 878230 | 27.14 | 14.69 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7261469.11 | 1405.61 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.59 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-16 | 2025 | 5 | 16 | Jabori HPS | 10.2 | 5.1 | 5.07 | 121739 | 119400 | 8.54 | 3.97 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 681678.48 | 715933.68 | 2339 | Unit # 01 was operational on full load whereas unit # 02 is under maintenance. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-16 | 2025 | 5 | 16 | Machai HPS | 2.6 | 2.33 | 1.45 | 34488 | 33396 | 31.6 | 32 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 155992.72 | 135477.68 | 1092 | The load could not be increased in accordance with the available inflow due to high system voltage, which led to elevated stator temperatures. The unit remained synchronized, delivering power to the National Grid as per system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-16 | 2025 | 5 | 16 | Malakand-3 HPS | 81 | 74 | 71.06 | 1705362 | 1693640 | 51 | 45.17 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4848383.23 | 716705.57 | 11722 | All units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-16 | 2025 | 5 | 16 | Pehur HPS | 18 | 6.3 | 6 | 145100 | 140000 | 15.33 | 14.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 527380 | 1099964 | 5100 | Plant operational 24 hrs | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-16 | 2025 | 5 | 16 | Reshun HPS | 4.2 | 1.77 | 1.2 | 28000 | 27485 | 1.89 | 1.71 | 57.13 | 13.48 | 62.97 | 45 | 63470.4 | 855580.99 | 370497.8 | 485083.19 | 515 | Low load | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-16 | 2025 | 5 | 16 | Shishi HPS | 1.8 | 0.62 | 0.62 | 9486 | 9300 | 3 | 0.77 | 25.67 | 2.47 | 100 | 49 | 43200 | 106704 | 22971 | 83733 | 186 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-17 | 2025 | 5 | 17 | Daral Khwar HPS | 36.6 | 36.6 | 36.42 | 874150 | 874150 | 27.14 | 14.62 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7227734.44 | 35140.28 | 0 | 1: Unit No. 01, 02 & 03 was on bar delivering an average load equal to 36.42 MW according to the available hydrology. 2: 132KV supply line tripped at 11;55Hrs. 3: 132kv supply line still not restored at 24:00hrs plant still under shutdown. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-17 | 2025 | 5 | 17 | Jabori HPS | 10.2 | 5.2 | 5.1 | 122352 | 120000 | 8.54 | 4 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 685104 | 712508.16 | 2352 | Unit # 01 was operational on full load whereas generator of unit # 02 also inspected by a firm hired by EPC Contractor. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-17 | 2025 | 5 | 17 | Machai HPS | 2.6 | 1.71 | 1.59 | 38504 | 37652 | 31.6 | 32 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 175872.49 | 115597.91 | 852 | The load could not be increased in accordance with the available inflow due to high system voltage, which led to elevated stator temperatures. The unit remained synchronized, delivering power to the National Grid as per system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-17 | 2025 | 5 | 17 | Malakand-3 HPS | 81 | 75 | 69.64 | 1671271 | 1660140 | 51 | 44.39 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4752482.78 | 812606.02 | 11131 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-17 | 2025 | 5 | 17 | Pehur HPS | 18 | 6.22 | 6.15 | 146800 | 143000 | 15.33 | 14.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 538681 | 1088663 | 3800 | Plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-17 | 2025 | 5 | 17 | Reshun HPS | 4.2 | 1.65 | 1.14 | 27000 | 26490 | 1.78 | 1.65 | 55 | 13.48 | 59.33 | 45 | 59808 | 806211.84 | 357085.2 | 449126.64 | 510 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-17 | 2025 | 5 | 17 | Shishi HPS | 1.8 | 0.79 | 0.4 | 9486 | 9300 | 3 | 0.91 | 30.33 | 2.47 | 100 | 49 | 43200 | 106704 | 22971 | 83733 | 186 | The load varies as per the load demand of the local feeder, plan load shedding by PESCO | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-18 | 2025 | 5 | 18 | Daral Khwar HPS | 36.6 | 36.6 | 32.89 | 789260 | 789260 | 27.14 | 13.2 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6525838.46 | 737036.26 | 0 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 32.89 MW according to the available hydrology. 2. 132 KV Supply line failed at 0154 Hrs. Unit No.02, 03 and 01 were synchronized with national grid at 0207 Hrs, 0213 Hrs and 0214 Hrs respectively. 3. 132 KV breaker of Auxilliary T/F tripped due to lightening and bad weather at 1934 Hrs. 4. Unit No.02, 03 and 01 were synchronized with national grid at 1956 Hrs, 1959 Hrs and 2006 Hrs respectively. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-18 | 2025 | 5 | 18 | Jabori HPS | 10.2 | 5.2 | 5.1 | 122350 | 120020 | 8.54 | 4 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 685218.18 | 712393.98 | 2330 | Unit # 01 was operational on full load only. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-18 | 2025 | 5 | 18 | Machai HPS | 2.6 | 1.57 | 1.32 | 33164 | 32264 | 31.6 | 28 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 150705.14 | 140765.26 | 900 | The load could not be increased in accordance with the available inflow due to high system voltage, which led to elevated stator temperatures. The unit remained synchronized, delivering power to the National Grid as per system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-18 | 2025 | 5 | 18 | Malakand-3 HPS | 81 | 74 | 63.67 | 1528195 | 1517570 | 42.73 | 51 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4344347.64 | 1220741.16 | 10625 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-18 | 2025 | 5 | 18 | Pehur HPS | 18 | 6.25 | 4.65 | 111700 | 107000 | 14.92 | 10 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 403069 | 1224275 | 4700 | plant remained off the bar due to flooding conditions in generator hall and also nill irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-18 | 2025 | 5 | 18 | Reshun HPS | 4.2 | 1.74 | 0.8 | 18000 | 17510 | 1.77 | 1.1 | 36.73 | 13.48 | 59 | 45 | 59472 | 801682.56 | 236034.8 | 565647.76 | 490 | Feeder No. 3 line work | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-18 | 2025 | 5 | 18 | Shishi HPS | 1.8 | 0.69 | 0.08 | 1897 | 1860 | 3 | 0.84 | 28 | 2.47 | 100 | 49 | 43200 | 106704 | 4594.2 | 102109.8 | 37 | The powerhouse was shut down totally due to damage to the runner bearings of Units 1 and 3. A proposal has been forwarded for the urgent replacement and necessary repairs of the runner assembly. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-19 | 2025 | 5 | 19 | Daral Khwar HPS | 36.6 | 36.6 | 36.66 | 879790 | 879790 | 27.14 | 14.71 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7274367.66 | -11492.94 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.66 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-19 | 2025 | 5 | 19 | Jabori HPS | 10.2 | 5.2 | 5.04 | 121070 | 118750 | 8.54 | 3.95 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 677967.5 | 719644.66 | 2320 | Only unit # 01 was delivering power as per available hydrology. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-19 | 2025 | 5 | 19 | Machai HPS | 2.6 | 1.68 | 1.28 | 31700 | 30672 | 31.6 | 28 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 143268.91 | 148201.49 | 1028 | 1.Unit remained on bar delivering power to National Grid ,got tripped at 1858Hrs dated 19-05-2025 due to the tripping of 11KV Machai-HPS feeder on earth fault.Unit synchronized with the system at 2014Hrs as 11KV Machai-HPS line re-energized at 1907Hrs . 2.The load could not be increased in accordance with the available inflow due to high system voltage, which led to elevated stator temperatures. The unit remained synchronized, delivering power to the National Grid as per system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-19 | 2025 | 5 | 19 | Malakand-3 HPS | 81 | 73 | 68.44 | 1642490 | 1630850 | 51 | 43.12 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4668634.3 | 896454.5 | 11640 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-19 | 2025 | 5 | 19 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 14.72 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | Plant remained emergency shutdown due to floody condition and nil irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-19 | 2025 | 5 | 19 | Reshun HPS | 4.2 | 1.62 | 1.12 | 27000 | 26485 | 1.78 | 1.65 | 55 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 357017.8 | 450099.9 | 515 | Low load | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-19 | 2025 | 5 | 19 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | POWERHOUSE SHUTDOWN REPORT Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is pending for the repair and maintenance work on the runner assemblies. | ibrarahmadmkd@gmail.com | Original | Units = Net + Aux; Plant factor recalculated; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-05-20 | 2025 | 5 | 20 | Daral Khwar HPS | 36.6 | 36.6 | 36.6 | 878300 | 878300 | 27.14 | 14.69 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7262047.89 | 826.83 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.6 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-20 | 2025 | 5 | 20 | Jabori HPS | 10.2 | 5.1 | 5.1 | 122402 | 120060 | 8.54 | 4 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 685446.55 | 712165.61 | 2342 | Only unit # 01 was operational as per available hydrology. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-20 | 2025 | 5 | 20 | Machai HPS | 2.6 | 1.6 | 1.2 | 32192 | 31048 | 31.6 | 29 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 145025.21 | 146445.19 | 1144 | 1.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 0918Hrs dated 20.05.2025 due to the tripping of 11KV Machai-HPS feeder as 132KV line Mardan tripped.Unit synchronized with the system at 1023Hrs as 11KV Machai-HPS line energized at 1004Hrs. 2.The load could not be increased in accordance with the available inflow due to high system voltage, which led to elevated stator temperatures. The unit remained on bar, delivering power to the National Grid as per system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-20 | 2025 | 5 | 20 | Malakand-3 HPS | 81 | 70 | 67.6 | 1622507 | 1610480 | 51 | 43.74 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4610321.1 | 954767.7 | 12027 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-20 | 2025 | 5 | 20 | Pehur HPS | 18 | 3.07 | 1 | 23400 | 22000 | 14.92 | 2 | 66.67 | 3.767 | 100 | 41 | 432000 | 1627344 | 82874 | 1544470 | 1400 | Following the restoration of flooding conditions in the generator hall water ingress was controlled and affected area was dried and cleaned, Unit#01 was thoroughly inspected and all the necessory preparations were carried out. Unit#01 at 1528 Hrs dt. 20-05-25 was subsequently started, synchronized with grid and successfully loaded upto 3 mw without any abnormalities. Unit#02 maintenance is under process. Unit#01 tripped on over frequency protection at 1550 due to isolation of gadoon grid from national grid and taken on bar at1625 Hrs dt.20-05-25 with 3.0 mw load. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-20 | 2025 | 5 | 20 | Reshun HPS | 4.2 | 1.45 | 1.12 | 26000 | 25490 | 1.69 | 1.59 | 53.03 | 13.48 | 56.23 | 45 | 56683.2 | 764089.54 | 343605.2 | 420484.34 | 510 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-20 | 2025 | 5 | 20 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 0 | 3 | 100 | 2.47 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | POWERHOUSE SHUTDOWN REPORT Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is pending for the repair and maintenance work on the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-21 | 2025 | 5 | 21 | Daral Khwar HPS | 36.6 | 36.6 | 36.62 | 878760 | 878760 | 27.14 | 14.7 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7265851.31 | -2976.59 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.62 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-21 | 2025 | 5 | 21 | Jabori HPS | 10.2 | 5.2 | 4.91 | 117750 | 115440 | 8.54 | 3.85 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 659070.05 | 738542.11 | 2310 | Plant was operational as per available hydrology. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-21 | 2025 | 5 | 21 | Machai HPS | 2.6 | 1.62 | 1.2 | 25868 | 24960 | 31.6 | 30 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 116588.16 | 174882.24 | 908 | Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tipped at 0043Hrs & 1309Hrs dated 21-05-2025 due to the tripping of 11KV Machai-HPC feeder as PTW has been issued to Operation staff (PESCO) on KATLANG Grid.11KV Machai-HPS line re-energized at 0223Hrs & 1520Hrs as PTW canceled by Operation staff (PESCO). Unit synchronized with the system at 0228Hrs & 1545Hrs respectively and load gradually increased according to available inflow and prevailing system condition. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-21 | 2025 | 5 | 21 | Malakand-3 HPS | 81 | 74 | 67.53 | 1620758 | 1608750 | 51 | 43.93 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4605368.62 | 959720.18 | 12008 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-21 | 2025 | 5 | 21 | Pehur HPS | 18 | 5.32 | 3.36 | 80700 | 77000 | 16.35 | 8.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 290059 | 1337285 | 3700 | In continuation of the restoration of flooding conditions in the generator hall, the affected area of unit # 02 was dried and cleaned, Unit#02 was thoroughly inspected and all the necessory maintenance was carried out. Unit#02 at 2008 Hrs dt. 21-05-25 was subsequently started, synchronized with grid and successfully loaded upto 2.5 MW along with unit# 01 without any abnormalities. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-21 | 2025 | 5 | 21 | Reshun HPS | 4.2 | 1.66 | 1.16 | 28000 | 27492 | 1.89 | 1.71 | 57.13 | 13.48 | 63.03 | 45 | 63537.6 | 856486.85 | 370592.16 | 485894.69 | 508 | Low load | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-21 | 2025 | 5 | 21 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | POWERHOUSE SHUTDOWN REPORT Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is pending for the repair and maintenance work on the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-22 | 2025 | 5 | 22 | Daral Khwar HPS | 36.6 | 36.6 | 36.64 | 879440 | 879440 | 27.14 | 14.71 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7271473.75 | -8599.03 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.64 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-22 | 2025 | 5 | 22 | Jabori HPS | 10.2 | 5.2 | 4.75 | 114160 | 111860 | 8.54 | 3.73 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 638631.11 | 758981.05 | 2300 | Plant was operational as per available hydrology. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-22 | 2025 | 5 | 22 | Machai HPS | 2.6 | 1.7 | 1.23 | 30972 | 29380 | 31.6 | 29 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 137233.98 | 154236.42 | 1592 | The load could not be increased in accordance with the available inflow due to high system voltage, which led to elevated stator temperatures. The unit remained on bar, delivering power to the National Grid as per system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-22 | 2025 | 5 | 22 | Malakand-3 HPS | 81 | 73 | 68.43 | 1642294 | 1629980 | 51 | 44.36 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4666143.75 | 898945.05 | 12314 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-22 | 2025 | 5 | 22 | Pehur HPS | 18 | 6 | 5.54 | 132900 | 128000 | 16.35 | 13.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 482176 | 1145168 | 4900 | Plant remained operational through out 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-22 | 2025 | 5 | 22 | Reshun HPS | 4.2 | 2.62 | 1.7 | 37000 | 36465 | 2.77 | 2.26 | 75.5 | 13.48 | 92.2 | 45 | 92937.6 | 1252798.85 | 491548.2 | 761250.65 | 535 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-22 | 2025 | 5 | 22 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | POWERHOUSE SHUTDOWN REPORT Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is pending for the repair and maintenance work on the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-23 | 2025 | 5 | 23 | Daral Khwar HPS | 36.6 | 36.6 | 36.62 | 878890 | 878890 | 27.14 | 14.7 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7266926.19 | -4051.47 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.62 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-23 | 2025 | 5 | 23 | Jabori HPS | 10.2 | 5.2 | 4.37 | 105035 | 102690 | 8.54 | 3.43 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 586277.75 | 811334.41 | 2345 | Plant was operational as per available hydrology. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-23 | 2025 | 5 | 23 | Machai HPS | 2.6 | 1.46 | 1.37 | 32532 | 31648 | 31.6 | 30 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 147827.81 | 143642.59 | 884 | The load could not be increased in accordance with the available inflow due to high system voltage, which led to elevated stator temperatures. The unit remained synchronized, delivering power to the National Grid as per system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-23 | 2025 | 5 | 23 | Malakand-3 HPS | 81 | 74 | 70.96 | 1703078 | 1691030 | 51 | 46.07 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4840911.58 | 724177.22 | 12048 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-23 | 2025 | 5 | 23 | Pehur HPS | 18 | 5.53 | 4.91 | 117900 | 113000 | 16 | 11 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 425671 | 1201673 | 4900 | plant remained operational since 24 hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-23 | 2025 | 5 | 23 | Reshun HPS | 4.2 | 42000 | 1.82 | 3 | 41460 | 2.87 | 2.57 | 85.67 | 13.48 | 95.67 | 45 | 96432 | 1299903.36 | 558880.8 | 741022.56 | 41456.69 | Outgoing line feeder Breaker tripping due to line faults. | zafar.src@gmail.com | Original | CHECK: Net > Units (source me verify karein) | Link_Generation_Data_Summary.xlsx
2025-05-23 | 2025 | 5 | 23 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.47 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | POWERHOUSE SHUTDOWN REPORT Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is pending for the repair and maintenance work on the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-24 | 2025 | 5 | 24 | Daral Khwar HPS | 36.6 | 36.6 | 34.33 | 823830 | 823830 | 27.14 | 13.78 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6811673.59 | 451201.13 | 0 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 34.33 MW according to the available hydrology. 2. 132 KV Supply line failed at 1014 Hrs and was restored at 1105 Hrs. 3. Unit No.02, 03 and 01 were synchronized with national grid at 1111 Hrs, 1113 Hrs and 1118 Hrs respectively. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-24 | 2025 | 5 | 24 | Jabori HPS | 10.2 | 5.1 | 3.81 | 91540 | 89080 | 8.54 | 2.99 | 99.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 508575.54 | 889036.62 | 2460 | Plant was operational as per available hydrology. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-24 | 2025 | 5 | 24 | Machai HPS | 2.6 | 1.8 | 0.74 | 16128 | 15532 | 31.6 | 30 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 72549.97 | 218920.43 | 596 | 1. Unit being on bar delivering power to National Grid, got tripped at 1121Hrs dated 24-05-2025 due to the tripping of 11KV Machai-HPS feeder on earth fault dye to heavy rain and windstorms.Unit synchronized with the system at 1915Hrs as 11KV Machai-HPS line re-energized at 1930Hrs 2.The load could not be increased in accordance with the available inflow due to high system voltage, which led to elevated stator temperatures. The unit remained synchronized, delivering power to the National Grid as per system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-24 | 2025 | 5 | 24 | Malakand-3 HPS | 81 | 76 | 60.91 | 1461725 | 1451430 | 51 | 44.35 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4155008.66 | 1410080.14 | 10295 | All units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-24 | 2025 | 5 | 24 | Pehur HPS | 18 | 7.45 | 4.68 | 112400 | 109000 | 16.59 | 11 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 410603 | 1216741 | 3400 | plant remained shutdown from 1010 Hrs to 1520 Hrs dt. 24-05-25 in search of dead body recovry as per instruction of irrigation SDO. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-24 | 2025 | 5 | 24 | Reshun HPS | 4.2 | 2.6 | 1.32 | 30000 | 29485 | 1.99 | 1.84 | 61.2 | 13.48 | 66.2 | 45 | 66729.6 | 899515.01 | 397457.8 | 502057.21 | 515 | Line faults | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-24 | 2025 | 5 | 24 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | POWERHOUSE SHUTDOWN REPORT Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is pending for the repair and maintenance work on the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-25 | 2025 | 5 | 25 | Daral Khwar HPS | 36.6 | 36.6 | 35.89 | 861280 | 861280 | 27.14 | 14.4 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7121321.42 | 141553.3 | 0 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 35.89 MW according to the available hydrology. 2. 132 KV Supply line failed at 1220 Hrs and was restored at 1233 Hrs. 3. Unit No.02, 03 and 01 were synchronized with national grid at 1238 Hrs, 1239 Hrs and 1244 Hrs respectively. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-25 | 2025 | 5 | 25 | Jabori HPS | 10.2 | 5.1 | 4.3 | 103410 | 100960 | 8.54 | 3.37 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 576400.83 | 821211.33 | 2450 | Plant was operational as per available hydrology. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-25 | 2025 | 5 | 25 | Machai HPS | 2.6 | 1.29 | 0.31 | 9424 | 9152 | 31.6 | 30 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 42748.99 | 248721.41 | 272 | 1.Unit being on bar delivering power to National Grid, got tripped at 2353Hrs dated 24-05-2025 due to frequently tripping of the 11 kV Machai-HPS feeder on earth fault, attributed to adverse weather conditions. Although the feeder was subsequently re-energized, the unit remained shutdwown/standby as a precautionary measure in view of the continued instability of the 11 kV line. The unit was resynchronized with the grid at 1100Hrs dated 25-05-2025 following stabilization of the feeder. 2.Unit being on bar delivering power to National Grid, got tripped at 1155Hrs,1239Hrs,1316Hrs,1458Hrs & 1811Hrs dated 25-05-2025 due to frequently tripping of the 11 kV Machai-HPS feeder on earth fault, attributed to adverse weather conditions. Unit synchronized with the system at 1213Hrs, 1309Hrs,1447Hrs,1540Hrs & 1847Hrs respectively as 11KV Machai-HPS line energized at 1201, 1306Hrs, 1329Hrs, 1509Hrs & 1840Hrs. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-25 | 2025 | 5 | 25 | Malakand-3 HPS | 81 | 65 | 60.7 | 1456826 | 1446570 | 51 | 39.92 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4141095.94 | 1423992.86 | 10256 | All units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-25 | 2025 | 5 | 25 | Pehur HPS | 18 | 7.06 | 6.2 | 148800 | 145000 | 16.35 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 546215 | 1081129 | 3800 | plant remained operational throughout 24 hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-25 | 2025 | 5 | 25 | Reshun HPS | 4.2 | 2.98 | 1.87 | 43000 | 42348 | 2.73 | 2.63 | 87.67 | 13.48 | 91 | 45 | 91728 | 1236493.44 | 570851.04 | 665642.4 | 652 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-25 | 2025 | 5 | 25 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | POWERHOUSE SHUTDOWN REPORT Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is pending for the repair and maintenance work on the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-26 | 2025 | 5 | 26 | Daral Khwar HPS | 36.6 | 36.6 | 36.65 | 879650 | 879650 | 27.14 | 14.71 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7273210.1 | -10335.38 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.65 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-26 | 2025 | 5 | 26 | Jabori HPS | 10.2 | 5.1 | 4.35 | 104390 | 102000 | 8.54 | 3.41 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 582338.4 | 815273.76 | 2390 | Plant was operational as per available Hydrology. | hassanmushtaq2014@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-26 | 2025 | 5 | 26 | Machai HPS | 2.6 | 1.59 | 1.07 | 25052 | 24024 | 31.6 | 30 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 112216.1 | 179254.3 | 1028 | The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 2102Hrs dated 26.05.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault.Unit synchronized with the system at 2209Hrs as 11KV Machai-HPS line energized. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-26 | 2025 | 5 | 26 | Malakand-3 HPS | 81 | 68 | 62.53 | 1500638 | 1489300 | 51 | 41.07 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4263419.11 | 1301669.69 | 11338 | All units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-26 | 2025 | 5 | 26 | Pehur HPS | 18 | 6.61 | 6.2 | 150400 | 145000 | 15.33 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 546215 | 1081129 | 5400 | Plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-26 | 2025 | 5 | 26 | Reshun HPS | 4.2 | 3.34 | 2.01 | 42000 | 41390 | 2.87 | 2.57 | 85.67 | 13.48 | 95.73 | 45 | 96499.2 | 1300809.22 | 557937.2 | 742872.02 | 610 | Line faults | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-26 | 2025 | 5 | 26 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | POWERHOUSE SHUTDOWN REPORT Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is pending for the repair and maintenance work on the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-27 | 2025 | 5 | 27 | Daral Khwar HPS | 36.6 | 36.6 | 34.84 | 836230 | 836230 | 27.14 | 13.98 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6914200.51 | 348674.21 | 0 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 34.84 MW according to the available hydrology. 2. 132 KV Supply line failed at 1535 Hrs and was restored at 1634 Hrs. 3. Unit No.02, 03 and 01 were synchronized with national grid at 1642 Hrs, 1645 Hrs and 1648 Hrs respectively. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-27 | 2025 | 5 | 27 | Jabori HPS | 10.2 | 5.1 | 4.5 | 90500 | 88000 | 8.54 | 2.99 | 99.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 502409.6 | 895202.56 | 2500 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-27 | 2025 | 5 | 27 | Machai HPS | 2.6 | 1.53 | 0.83 | 22376 | 21472 | 31.6 | 30 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 100295.71 | 191174.69 | 904 | 1.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 0756Hrs & 1314Hrs dated 27.05.2025 with Reverse power due to high system voltage .Unit synchronized with the system at 0931Hrs & 1339Hrs as system voltage stabilized. 2.Unit being on bar delivering power to National Grid, got tripped at 1430Hrs,1646Hrs,1717Hrs, 1741Hrs, 1838Hrs & 1946Hrs dated 27-05-2025 due to frequently tripping of the 11 kV Machai-HPS feeder on earth fault, attributed to adverse weather conditions. Unit synchronized with the system at 1642Hrs, 1659Hrs,1733Hrs, 1804Hrs,1930Hrs & 2002Hrs respectively as 11KV Machai-HPS line energized at 1621, 1655Hrs, 1728Hrs, 1757Hrs,1924 & 1953Hrs. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-27 | 2025 | 5 | 27 | Malakand-3 HPS | 81 | 72 | 65.31 | 1567516 | 1556410 | 51 | 42.9 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4455534.91 | 1109553.89 | 11106 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-27 | 2025 | 5 | 27 | Pehur HPS | 18 | 7.66 | 4.58 | 109900 | 105000 | 16 | 9 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 395535 | 1231809 | 4900 | Plant remained operational for 1623 Hrs and remained off the bar for 0307 Hrs due to isolation of Gadoon grid and for 0440 Hrs due to blockage of the canal gates after wind storm and nil irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-27 | 2025 | 5 | 27 | Reshun HPS | 4.2 | 3.05 | 1.57 | 35000 | 34396 | 2.34 | 2.14 | 71.4 | 13.48 | 78.13 | 45 | 78758.4 | 1061663.23 | 463658.08 | 598005.15 | 604 | Line faults due to heavy cyclone occurred. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-27 | 2025 | 5 | 27 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | POWERHOUSE SHUTDOWN REPORT Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in procedure for the repair and maintenance work on the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-28 | 2025 | 5 | 28 | Daral Khwar HPS | 36.6 | 36.6 | 36.54 | 877010 | 877010 | 27.14 | 14.67 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7251381.78 | 11492.94 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.54 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-28 | 2025 | 5 | 28 | Jabori HPS | 10.2 | 5.1 | 4.5 | 97450 | 95000 | 8.54 | 3.13 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 542374 | 855238.16 | 2450 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-28 | 2025 | 5 | 28 | Machai HPS | 2.6 | 1.35 | 1 | 25352 | 24420 | 31.6 | 28 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 114065.82 | 177404.58 | 932 | 1.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 1922Hrs and 2306Hrs dated 28.05.2025 due to the tripping of 11KV Machai-HPS feeder ,following the tripping of 132KV line Mardan .Unit synchronized with the system at 2002Hrs and 2348Hrs respectively as 11KV Machai-HPS line energized at 1955Hrs and 2342Hrs . 2.The load could not be increased in accordance with the available inflow due to high system voltage, which led to elevated stator temperatures. The unit remained synchronized, delivering power to the National Grid as per system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-28 | 2025 | 5 | 28 | Malakand-3 HPS | 81 | 71 | 67.26 | 1614298 | 1603400 | 51 | 43.96 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4590053.18 | 975035.62 | 10898 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-28 | 2025 | 5 | 28 | Pehur HPS | 18 | 5.54 | 2.56 | 61400 | 60000 | 16.59 | 5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 226020 | 1401324 | 1400 | Plant remained shutdown since 1925 Hrs dated 27-05-2025 due to blockage in canal gates and on 28-05-2025 Unit# 01 & 02 were taken on bar with 5.20 MW load. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-28 | 2025 | 5 | 28 | Reshun HPS | 4.2 | 3.16 | 1.9 | 42000 | 41388 | 2.87 | 2.57 | 85.67 | 13.48 | 95.63 | 45 | 96398.4 | 1299450.43 | 557910.24 | 741540.19 | 612 | Feeder Tripping due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-28 | 2025 | 5 | 28 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | POWERHOUSE SHUTDOWN REPORT Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in procedure for the repair and maintenance work on the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-29 | 2025 | 5 | 29 | Daral Khwar HPS | 36.6 | 36.6 | 33.6 | 806350 | 806350 | 27.14 | 13.49 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6667143.7 | 595731.02 | 0 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 33.60 MW according to the available hydrology. 2. 132 KV Supply line failed at 1658 Hrs and was restored at 1743 Hrs. 3. Unit No.02, 03 and 01 were synchronized with national grid at 1759 Hrs, 1806 Hrs and 1815 Hrs respectively. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-29 | 2025 | 5 | 29 | Jabori HPS | 10.2 | 5.1 | 4.1 | 99930 | 97490 | 8.54 | 3.26 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 556589.91 | 841022.25 | 2440 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-29 | 2025 | 5 | 29 | Machai HPS | 2.6 | 1.38 | 0.92 | 22076 | 21296 | 31.6 | 30 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 99473.62 | 191996.78 | 780 | Incident Report – Tripping of Unit due to Feeder Fault The unit, which was on bar delivering power to the National Grid as per available water inflow and system conditions, tripped at 1820 hrs on 29-05-2025. The tripping occurred due to a fault on the 11 kV MACHAI-HPS feeder, which experienced an earth fault and instantaneous fault, attributed to adverse weather conditions. An inquiry call was made to Katlang Grid regarding the tripping and possible restoration of power. As per their response, the line could not be restored since the fault still persists. The operation staff of PESCO was informed of the fault. The LS-Operation, PESCO (Mardan) was contacted and requested to take the necessary action to energize the feeder at the earliest. Follow-up communication was made with the Line Superintendent (PESCO) to inquire about the status of the 11 kV Machai-HPS line fault. According to his response, the fault still exists, and the field team is actively working to rectify it. As of now, the unit remains on standby since 1820 hrs on 29-05-2025, as the fault has not yet been cleared by the operation staff (PESCO), due to ongoing adverse weather conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-29 | 2025 | 5 | 29 | Malakand-3 HPS | 81 | 71 | 52.2 | 1252834 | 1243900 | 51 | 43.91 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3560912.53 | 2004176.27 | 8934 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. Unit # 01,02 & 03 tripped due to 132KV supply failed at 18:34hrs dated 29-05-2025. Informed RCC. 132KV supply restored at 02:55hrs dated 30-05-2025.All three Units synchronized with the system. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-29 | 2025 | 5 | 29 | Pehur HPS | 18 | 8.11 | 5.36 | 128600 | 123000 | 16.35 | 12.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 463341 | 1164003 | 5600 | Plant remained shutdown for 04:51 Hrs due to nil irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-29 | 2025 | 5 | 29 | Reshun HPS | 4.2 | 3.12 | 1.68 | 38000 | 37400 | 2.49 | 2.33 | 77.5 | 13.48 | 82.9 | 45 | 83563.2 | 1126431.94 | 504152 | 622279.94 | 600 | Feeder tripping due to heavy cyclone. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-29 | 2025 | 5 | 29 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | POWERHOUSE SHUTDOWN REPORT Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for the repair and maintenance work on the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-30 | 2025 | 5 | 30 | Daral Khwar HPS | 36.6 | 36.6 | 36.61 | 878730 | 878730 | 27.14 | 14.7 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7265603.26 | -2728.54 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.61 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-30 | 2025 | 5 | 30 | Jabori HPS | 10.2 | 5.1 | 4 | 108220 | 106120 | 8.54 | 3.63 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 605860.3 | 791751.86 | 2100 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-30 | 2025 | 5 | 30 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 31.6 | 3 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Update on Unit Status – Post-Fault Clearance and Hydrological Constraint The unit has remained on standby since 1820hrs on 29-05-2025. Although the 11 kV Machai-HPC feeder was subsequently re-energized at 1100hrs on 30-05-2025, following the clearance of the fault by PESCO operation staff (who removed tree branches from the line), the unit remained shutdown/standby due to insufficient hydrology. As per the report from the Sub Engineer, Irrigation Department (Katlang Section), the Trash Rack at RD-75+000 of the Machai Branch Syphon was damaged during the heavy windstorm and rainfall on 29-05-2025 at 1845 hrs. Consequently, the supply to the Machai Branch has been suspended for 24 hours to allow for the urgent restoration of the damaged trash Rack at RD-75+000. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-05-30 | 2025 | 5 | 30 | Malakand-3 HPS | 81 | 70 | 50.82 | 1219611 | 1210670 | 51 | 32.03 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3465785.01 | 2099303.79 | 8941 | All Three units are on bar as per available hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-30 | 2025 | 5 | 30 | Pehur HPS | 18 | 4.11 | 1 | 24300 | 23000 | 15.33 | 2.5 | 83.33 | 3.767 | 100 | 41 | 432000 | 1627344 | 86641 | 1540703 | 1300 | Plant shut down since 29-05-2025. At 1750 hrs u # 01 put on bar. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-30 | 2025 | 5 | 30 | Reshun HPS | 4.2 | 2.94 | 1.92 | 41000 | 40380 | 2.62 | 2.51 | 83.67 | 13.48 | 87.17 | 45 | 87864 | 1184406.72 | 544322.4 | 640084.32 | 620 | Feeder Breaker is tripping due to heavy wind. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-30 | 2025 | 5 | 30 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | POWERHOUSE SHUTDOWN REPORT Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is pending for the repair and maintenance work on the runner assemblies. | ibrarahmadmkd@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Max load estimated from Avg load; Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-05-31 | 2025 | 5 | 31 | Daral Khwar HPS | 36.6 | 36.6 | 36.1 | 866330 | 866330 | 27.14 | 14.49 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7163076.34 | 99798.38 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.10 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-31 | 2025 | 5 | 31 | Jabori HPS | 10.2 | 5.1 | 4.5 | 106235 | 104000 | 8.54 | 3.73 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 593756.8 | 803855.36 | 2235 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-05-31 | 2025 | 5 | 31 | Machai HPS | 2.6 | 1 | 0.03 | 152 | 88 | 33.2 | 23 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 411.05 | 291059.35 | 64 | The Unit after all preliminary checks and started at 2310Hrs Dated 01-06-2025 as rated head was restored due to increase in canal discharge .Unit kept on FSNL for an half hour and finding everything normal then synchronized with the system at 2342Hrs and load gradually increased according to available inflow and system condition. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-31 | 2025 | 5 | 31 | Malakand-3 HPS | 81 | 70 | 66.05 | 1585257 | 1575010 | 51 | 42.91 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4508781.13 | 1056307.67 | 10247 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-31 | 2025 | 5 | 31 | Pehur HPS | 18 | 4.14 | 4 | 96500 | 92000 | 15.33 | 8 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 346564 | 1280780 | 4500 | unit # 01 on bar while unit # 02 off the bar due to less irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-31 | 2025 | 5 | 31 | Reshun HPS | 4.2 | 3.64 | 1.32 | 28000 | 27404 | 2.89 | 2.71 | 90.47 | 13.48 | 96.23 | 45 | 97003.2 | 1307603.14 | 369405.92 | 938197.22 | 596 | Electricity suspended due to tree trimming campaign from 8:00 Am to 5:00Pm. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-05-31 | 2025 | 5 | 31 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | POWERHOUSE SHUTDOWN REPORT Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is process for the repair and maintenance work on the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-01 | 2025 | 6 | 1 | Daral Khwar HPS | 36.6 | 36.6 | 36.44 | 874640 | 874640 | 35.05 | 14.63 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7231785.91 | 31088.81 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.44 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-01 | 2025 | 6 | 1 | Jabori HPS | 10.2 | 5.1 | 4.2 | 100970 | 98650 | 6.7 | 3.29 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 563212.58 | 834399.58 | 2320 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-06-01 | 2025 | 6 | 1 | Machai HPS | 2.6 | 0.46 | 0.35 | 8282 | 8250 | 33.2 | 24.5 | 13.27 | 4.671 | 100 | 70 | 62400 | 291470.4 | 38535.75 | 252934.65 | 32 | No data submitted for this date | engr.atifwazir@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-06-01 | 2025 | 6 | 1 | Malakand-3 HPS | 81 | 67 | 64.25 | 1541970 | 1532030 | 51 | 41.97 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4385742.28 | 1179346.52 | 9940 | All the unit are on bar and flow decrease by irrigation department due to weather condition | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-01 | 2025 | 6 | 1 | Pehur HPS | 18 | 8.16 | 6.09 | 146200 | 141000 | 20.31 | 13 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 531147 | 1096197 | 5200 | Unit#02 taken on bar at 0840 Hrs dt. 01-06-2025 as per irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-01 | 2025 | 6 | 1 | Reshun HPS | 4.2 | 3.25 | 1.44 | 35000 | 34398 | 2.54 | 2.14 | 71.4 | 13.48 | 84.83 | 45 | 85512 | 1152701.76 | 463685.04 | 689016.72 | 602 | Electricity has been suspended to consumer due to tree trimming work in the feeder from 08:00Am to 05:00Pm | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-01 | 2025 | 6 | 1 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | POWERHOUSE SHUTDOWN REPORT Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is pending for the repair and maintenance work on the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-02 | 2025 | 6 | 2 | Daral Khwar HPS | 36.6 | 36.6 | 34.82 | 835760 | 835760 | 35.02 | 13.98 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6910314.41 | 352560.31 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 34.82 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-02 | 2025 | 6 | 2 | Jabori HPS | 10.2 | 5.1 | 4 | 100306 | 98000 | 6.7 | 3.29 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 559501.6 | 838110.56 | 2306 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-06-02 | 2025 | 6 | 2 | Machai HPS | 2.6 | 1.37 | 0.69 | 16412 | 16412 | 33.2 | 26 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 76660.45 | 214809.95 | 0 | 1.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 0142Hrs dated 02.06.2025 with Reverse power due to high system voltage . Unit synchronized with the system at 0202Hrs as system voltage stabilized. 2.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 2135Hrs dated 02.06.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault.Unit synchronized with the system at 2242Hrs as 11KV Machai-HPS line energized at 2200Hrs as system voltage stabilized. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-02 | 2025 | 6 | 2 | Malakand-3 HPS | 81 | 71 | 64.67 | 1552095 | 1541400 | 51 | 42.98 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4412565.78 | 1152523.02 | 10695 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. Hydrology is decreased due to variation in river flow, confirmed from Irrigation department. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-02 | 2025 | 6 | 2 | Pehur HPS | 18 | 7.04 | 6.6 | 158300 | 154000 | 16.35 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 580118 | 1047226 | 4300 | Plant remained operational through out 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-02 | 2025 | 6 | 2 | Reshun HPS | 4.2 | 3.97 | 2.24 | 52000 | 51399 | 3.28 | 3.18 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 692858.52 | 665925.48 | 601 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-02 | 2025 | 6 | 2 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | POWERHOUSE SHUTDOWN REPORT Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for the repair and maintenance work on the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-03 | 2025 | 6 | 3 | Daral Khwar HPS | 36.6 | 34.3 | 31.53 | 756730 | 756730 | 35.02 | 12.66 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6256870.66 | 1006004.06 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 31.53 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-03 | 2025 | 6 | 3 | Jabori HPS | 10.2 | 5.1 | 4.64 | 111598 | 109210 | 6.7 | 3.64 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 623501.73 | 774110.43 | 2388 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-06-03 | 2025 | 6 | 3 | Machai HPS | 2.6 | 1.38 | 1.03 | 25400 | 24468 | 31.6 | 27 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 114290.03 | 177180.37 | 932 | The load could not be increased in accordance with the available inflow due to high system voltage, which led to elevated stator temperatures. The unit remained synchronized, delivering power to the National Grid as per system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-03 | 2025 | 6 | 3 | Malakand-3 HPS | 81 | 70 | 67.16 | 1611775 | 1601450 | 51 | 44.16 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4584470.92 | 980617.88 | 10325 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. Hydrology is decreased due to variation in river flow, confirmed from Irrigation department. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-03 | 2025 | 6 | 3 | Pehur HPS | 18 | 7.57 | 6.45 | 154900 | 150000 | 20.31 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 565050 | 1062294 | 4900 | Plant remained operational through out 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-03 | 2025 | 6 | 3 | Reshun HPS | 4.2 | 3 | 2.05 | 43000 | 42425 | 2.74 | 2.63 | 87.67 | 13.48 | 91.33 | 45 | 92064 | 1241022.72 | 571889 | 669133.72 | 575 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-03 | 2025 | 6 | 3 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | POWERHOUSE SHUTDOWN REPORT Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is pending for the repair and maintenance work on the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-04 | 2025 | 6 | 4 | Daral Khwar HPS | 36.6 | 32.5 | 27.22 | 653380 | 653380 | 35.02 | 10.93 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 5402341.85 | 1860532.87 | 0 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 27.22 MW according to the available hydrology. 2. Plant shutdown at 16:02 Hrs for installation of auxiliary transformer. 3. Unit No.02, 03 and 01 were synchronized with national grid at 1819 Hrs, 1820 Hrs and 1820 Hrs respectively. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-04 | 2025 | 6 | 4 | Jabori HPS | 10.2 | 5.1 | 4.54 | 108979 | 106780 | 6.7 | 3.56 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 609628.38 | 787983.78 | 2199 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median | Link_Generation_Data_Summary.xlsx
2025-06-04 | 2025 | 6 | 4 | Machai HPS | 2.6 | 2.15 | 1.16 | 28500 | 27668 | 33.2 | 27 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 129237.23 | 162233.17 | 832 | 1.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 0521Hrs & 1838Hrs dated 04.06.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault.Unit synchronized with the system at 0528Hrs & 1908Hrs respectively as 11KV Machai-HPS line energized at 0524Hrs & 1852Hrs . 2.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 0253Hrs & 1400Hrs dated 03.06.2025 with Reverse power due to high system voltage. Unit synchronized with the system at 0315Hrs & 1510Hrs as system voltage stabilized. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-04 | 2025 | 6 | 4 | Malakand-3 HPS | 81 | 71 | 67.13 | 1611182 | 1600580 | 51 | 44.22 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4581980.37 | 983108.43 | 10602 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. Hydrology is decreased due to variation in river flow, confirmed from Irrigation department. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-04 | 2025 | 6 | 4 | Pehur HPS | 18 | 7.6 | 6.28 | 150700 | 146000 | 16.35 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 549982 | 1077362 | 4700 | plant remained operational since 24 hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-04 | 2025 | 6 | 4 | Reshun HPS | 4.2 | 3.4 | 2.17 | 48000 | 47387 | 2.99 | 2.93 | 97.67 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 638776.76 | 716383.82 | 613 | Tripping due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-04 | 2025 | 6 | 4 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.47 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | POWERHOUSE SHUTDOWN REPORT Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work on the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-05 | 2025 | 6 | 5 | Daral Khwar HPS | 36.6 | 36.6 | 30.48 | 731570 | 731570 | 35.02 | 12.23 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6048840.23 | 1214034.49 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 30.48 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-05 | 2025 | 6 | 5 | Jabori HPS | 10.2 | 5.1 | 4.57 | 109740 | 107500 | 7.1 | 3.58 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 613739 | 783873.16 | 2240 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-05 | 2025 | 6 | 5 | Machai HPS | 2.6 | 1.51 | 1.14 | 27116 | 26184 | 33.2 | 28 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 122305.46 | 169164.94 | 932 | Unit precautionary shut down at 1747Hrs Dated 05-06-2025 due to the drop in head race level as water decreased by irrigation department for the searching of dead body.The Unit after all preliminary checks and then synchronized with the system at 2149Hrs Dated 05-06-2025 as rated head was restored due to increase in canal discharge as water supply for Machai was restored. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-05 | 2025 | 6 | 5 | Malakand-3 HPS | 81 | 71 | 68.41 | 1641936 | 1631980 | 51 | 44.74 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4671869.15 | 893219.65 | 9956 | All three Units were on bar | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-05 | 2025 | 6 | 5 | Pehur HPS | 18 | 7.07 | 6.12 | 147000 | 142000 | 16.35 | 14.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 534914 | 1092430 | 5000 | plant remained operational since 24 hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-05 | 2025 | 6 | 5 | Reshun HPS | 4.2 | 3.08 | 2.37 | 56000 | 55412 | 3.52 | 3.43 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 746953.76 | 611830.24 | 588 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-05 | 2025 | 6 | 5 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | POWERHOUSE SHUTDOWN REPORT Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-06 | 2025 | 6 | 6 | Daral Khwar HPS | 36.6 | 36.6 | 35.18 | 844260 | 844260 | 35.02 | 14.12 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6980594.96 | 282279.76 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 35.18 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-06 | 2025 | 6 | 6 | Jabori HPS | 10.2 | 5 | 4.14 | 99470 | 97200 | 7.1 | 3.25 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 554934.24 | 842677.92 | 2270 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-06 | 2025 | 6 | 6 | Machai HPS | 2.6 | 1.64 | 1.39 | 34372 | 33384 | 33.2 | 29 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 155936.66 | 135533.74 | 988 | Unit remained on bar delivering power to National Grid as per available inflow and system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-06 | 2025 | 6 | 6 | Malakand-3 HPS | 81 | 72 | 68.17 | 1636174 | 1624620 | 51 | 44.66 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4650799.67 | 914289.13 | 11554 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. Hydrology is decreased due to variation in river flow, confirmed from Irrigation department. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-06 | 2025 | 6 | 6 | Pehur HPS | 18 | 5.38 | 5.16 | 124000 | 119000 | 20.31 | 13 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 448273 | 1179071 | 5000 | Generation remained less because of low head and opening of irrigation valve. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-06 | 2025 | 6 | 6 | Reshun HPS | 4.2 | 3.71 | 1.85 | 41000 | 40404 | 2.63 | 2.51 | 83.67 | 13.48 | 87.53 | 45 | 88233.6 | 1189388.93 | 544645.92 | 644743.01 | 596 | Line faults due to heavy wind. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-06 | 2025 | 6 | 6 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | POWERHOUSE SHUTDOWN REPORT Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-07 | 2025 | 6 | 7 | Daral Khwar HPS | 36.6 | 36.6 | 34.51 | 828130 | 828130 | 35.02 | 13.85 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6847227.28 | 415647.44 | 0 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 34.51 MW according to the available hydrology. 2. 132 KV Supply line failed at 1924 Hrs and was restored at 2016 Hrs. 3. Unit No.02, 03 and 01 were synchronized with national grid at 2025 Hrs, 2027 Hrs and 2043 Hrs respectively. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-07 | 2025 | 6 | 7 | Jabori HPS | 10.2 | 4.5 | 4.07 | 97825 | 95570 | 7.1 | 3.19 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 545628.24 | 851983.92 | 2255 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-07 | 2025 | 6 | 7 | Machai HPS | 2.6 | 2.2 | 0.61 | 11896 | 11496 | 33.2 | 20 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 53697.82 | 237772.58 | 400 | 1.Unit tripped at 0207Hrs dated 07.06.2025 on Reverse Power due to high system voltage and synchronized with the system at 0335Hrs as system voltage stabilized. 2.Unit precautionary shut down at 0503Hrs dated 07-06-2025 due to less hydrology as water decreased by Irrigation Department for the searching of humam dead body.Unit synchronized with the system at 1415Hrs as water supply for Machai was restored. 3.Unit tripped at 1915Hrs dated 07-06-2025 with to the tripping of 11KV Machai-HPS feeder on earth fault due to heavy windstorm. Unit standby since 1915Hrs dated 07-06-2025 while the 11KV Machai-HPS line re-energized at 1025Hrs as thefault was cleared by operation staff (PESCO) and Unit synchronized with the system at 1100Hrs dated 07-06-2025 | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-07 | 2025 | 6 | 7 | Malakand-3 HPS | 81 | 72 | 67.94 | 1630647 | 1620140 | 51 | 44.33 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4637974.78 | 927114.02 | 10507 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running.Hydrology is decreased due to variation in river flow | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-07 | 2025 | 6 | 7 | Pehur HPS | 18 | 4.9 | 3.59 | 87400 | 85000 | 16.35 | 9 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 320195 | 1307149 | 2400 | Tripping of 132 KV line for 40 mints. Plant remained shut down for 05 hrs due to nil irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-07 | 2025 | 6 | 7 | Reshun HPS | 4.2 | 1.64 | 0.92 | 21000 | 20419 | 2.12 | 1.28 | 42.83 | 13.48 | 70.5 | 45 | 71064 | 957942.72 | 275248.12 | 682694.6 | 581 | Line faults due to heavy wind. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-07 | 2025 | 6 | 7 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | POWERHOUSE SHUTDOWN REPORT Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-08 | 2025 | 6 | 8 | Daral Khwar HPS | 36.6 | 36.6 | 36.39 | 873260 | 873260 | 35.02 | 14.6 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7220375.66 | 42499.06 | 0 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.39 MW according to the available hydrology | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-08 | 2025 | 6 | 8 | Jabori HPS | 10.2 | 4 | 3.56 | 85575 | 83300 | 7.1 | 2.79 | 93 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 475576.36 | 922035.8 | 2275 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-08 | 2025 | 6 | 8 | Machai HPS | 2.6 | 1.78 | 0.64 | 15524 | 15048 | 33.2 | 30 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 70289.21 | 221181.19 | 476 | Not reported | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-08 | 2025 | 6 | 8 | Malakand-3 HPS | 81 | 72 | 66.1 | 1586395 | 1575870 | 51 | 43.49 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4511243.05 | 1053845.75 | 10525 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-08 | 2025 | 6 | 8 | Pehur HPS | 18 | 4.33 | 2.08 | 50000 | 47000 | 16.35 | 5.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 177049 | 1450295 | 3000 | Plant started at 0910 hrs, and again shut down at 2050 hrs for search of drowned person in the canal. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-08 | 2025 | 6 | 8 | Reshun HPS | 4.2 | 2.12 | 1.51 | 33000 | 32390 | 2.11 | 2.02 | 67.33 | 13.48 | 70.33 | 45 | 70896 | 955678.08 | 436617.2 | 519060.88 | 610 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-08 | 2025 | 6 | 8 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | POWERHOUSE SHUTDOWN REPORT Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-09 | 2025 | 6 | 9 | Daral Khwar HPS | 36.6 | 36.6 | 36.39 | 876610 | 873410 | 35.02 | 14.61 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7221615.9 | 41258.82 | 3200 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 36.39 MW according to the available hydrology | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-09 | 2025 | 6 | 9 | Jabori HPS | 10.2 | 5 | 3.52 | 84550 | 82250 | 7.1 | 2.76 | 92 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 469581.7 | 928030.46 | 2300 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-09 | 2025 | 6 | 9 | Machai HPS | 2.6 | 1.56 | 0.96 | 23332 | 22396 | 33.2 | 26 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 104611.72 | 186858.68 | 936 | Unit remained on bar delivering power to National Grid as per available inflow and system conditions | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-09 | 2025 | 6 | 9 | Malakand-3 HPS | 81 | 68 | 52.69 | 1264673 | 1255360 | 51 | 36.3 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3593719.07 | 1971369.73 | 9313 | As per information received from the Irrigation Department, water was diverted at Admandara Headworks into the Swat River to facilitate the search operation for dead body . Consequently, due to a reduction in inflow at the Forebay, Units #01, #02, and #03 were desynchronized from the system at 2031 Hrs, 1942 Hrs, and 1909 Hrs, respectively. The matter was duly communicated to the RCC. Subsequently, the units were resynchronized with the system as follows: Unit #01 at 0503 Hrs Unit #02 at 0522 Hrs Unit #03 at 0544 Hrs | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-09 | 2025 | 6 | 9 | Pehur HPS | 18 | 5.77 | 2.29 | 55100 | 53000 | 16.35 | 6 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 199651 | 1427693 | 2100 | The plant remained shut down for 09 hours upon instruction of the irrigation SDO in search of dead bodies in the canal. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-09 | 2025 | 6 | 9 | Reshun HPS | 4.2 | 3.12 | 2.13 | 47000 | 46396 | 2.99 | 2.88 | 95.9 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 625418.08 | 729742.5 | 604 | Tripping due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-09 | 2025 | 6 | 9 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-10 | 2025 | 6 | 10 | Daral Khwar HPS | 36.6 | 36.6 | 36.39 | 876190 | 873390 | 35.02 | 14.61 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7221450.54 | 41424.18 | 2800 | Unit 1, 2 and 3 were on bar delivering an average load equal to 36.39 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-10 | 2025 | 6 | 10 | Jabori HPS | 10.2 | 4 | 3.34 | 80180 | 77890 | 7.1 | 3.34 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 444689.59 | 952922.57 | 2290 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-10 | 2025 | 6 | 10 | Machai HPS | 2.6 | 1.55 | 0.19 | 5192 | 4884 | 33.2 | 10 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 22813.16 | 268657.24 | 308 | 1.Unit precautionary shut down at 0200Hrs and 1655Hrs dated 10-06-2025 due to the drop in head race level as water decreased by irrigation department for the searching of human dead body.The Unit after all preliminary checks and then synchronized with the system at 1408Hrs and 0031Hrs(11-06-2025) respectively as rated head was restored due to increase in canal discharge as water supply for Machai was restored. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-10 | 2025 | 6 | 10 | Malakand-3 HPS | 81 | 75 | 28.13 | 675119 | 669820 | 51 | 23.57 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1917493.71 | 3647595.09 | 5299 | As per information received from the Irrigation Department, water was diverted at Admandara Headworks into the Swat River to facilitate the search operation for dead body . Consequently, due to a reduction in inflow at the Forebay, Units #01, #02, and #03 were desynchronized from the system at 1132 Hrs, 1235 Hrs, and 1237 Hrs, respectively. The matter was duly communicated to the RCC. Subsequently, the units were resynchronized with the system as follows: Unit #01 at 2018 Hrs Unit #02 at 2025 Hrs Unit #03 at 2040 Hrs | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-10 | 2025 | 6 | 10 | Pehur HPS | 18 | 3.65 | 3.32 | 79700 | 76000 | 16.35 | 10 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 286292 | 1341052 | 3700 | Unit# 01 & 02 remained off the bar for 16 min due to tripping of 132 KV line CB3/E1Q1 (PHPC-Gadoon) circuit breaker on over current protection. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-10 | 2025 | 6 | 10 | Reshun HPS | 4.2 | 3.42 | 2.25 | 53000 | 52380 | 3.33 | 3.24 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 706082.4 | 652701.6 | 620 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-10 | 2025 | 6 | 10 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | POWERHOUSE SHUTDOWN REPORT Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-11 | 2025 | 6 | 11 | Daral Khwar HPS | 36.6 | 36.6 | 27.14 | 665320 | 663320 | 35.02 | 11.09 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 5484528.76 | 1778345.96 | 2000 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 27.14 MW according to the available hydrology. 2. Plant shutdown at 17:00 Hrs due to jumper and insulation disk failure between Matta and Mingora. 3. 132KV supply was restored at 2130Hrs. Units#1, 2 and 3 were synchronized at 2137 Hrs, 2141 Hrs and 2144 Hrs respectively. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-11 | 2025 | 6 | 11 | Jabori HPS | 10.2 | 3.4 | 3.17 | 76150 | 73830 | 6.49 | 2.48 | 82.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 421510.24 | 976101.92 | 2320 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-11 | 2025 | 6 | 11 | Machai HPS | 2.6 | 1.2 | 1.06 | 25200 | 24108 | 27.07 | 26 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 112608.47 | 178861.93 | 1092 | The load could not be increased in accordance with the available inflow due to high system voltage, which led to elevated stator temperatures. The unit remained synchronized, delivering power to the National Grid as per system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-11 | 2025 | 6 | 11 | Malakand-3 HPS | 81 | 71 | 67.18 | 1612425 | 1599590 | 51 | 43.03 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4579146.29 | 985942.51 | 12835 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-11 | 2025 | 6 | 11 | Pehur HPS | 18 | 3.41 | 2.8 | 72900 | 70000 | 16.35 | 10 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 263690 | 1363654 | 2900 | Plant operational 24 hrs | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-11 | 2025 | 6 | 11 | Reshun HPS | 4.2 | 3.41 | 1.3 | 33000 | 29399 | 2.41 | 2.02 | 67.33 | 13.48 | 80.33 | 45 | 80976 | 1091556.48 | 396298.52 | 695257.96 | 3601 | Line faults due to heavy wind. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-11 | 2025 | 6 | 11 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | POWERHOUSE SHUTDOWN REPORT Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-12 | 2025 | 6 | 12 | Daral Khwar HPS | 36.6 | 36.6 | 35.21 | 865130 | 861930 | 35.02 | 14.41 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7126695.82 | 136178.9 | 3200 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 35.21 MW according to the available hydrology | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-12 | 2025 | 6 | 12 | Jabori HPS | 10.2 | 3.4 | 3.14 | 75310 | 73010 | 6.49 | 2.46 | 82 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 416828.69 | 980783.47 | 2300 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-12 | 2025 | 6 | 12 | Machai HPS | 2.6 | 2.21 | 0.86 | 19404 | 18700 | 27.07 | 25 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 87347.7 | 204122.7 | 704 | The load could not be increased in accordance with the available inflow due to high system voltage, which led to elevated stator temperatures. The unit remained synchronized, delivering power to the National Grid as per system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-12 | 2025 | 6 | 12 | Malakand-3 HPS | 81 | 71 | 68.25 | 1638045 | 1625090 | 51 | 43.91 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4652145.14 | 912943.66 | 12955 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-12 | 2025 | 6 | 12 | Pehur HPS | 18 | 3.49 | 3.02 | 73700 | 70000 | 16.35 | 9 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 263690 | 1363654 | 3700 | The plant remained operational for 24 hours as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-12 | 2025 | 6 | 12 | Reshun HPS | 4.2 | 2.86 | 2.08 | 44000 | 43390 | 2.79 | 2.69 | 89.77 | 13.48 | 93 | 45 | 93744 | 1263669.12 | 584897.2 | 678771.92 | 610 | Line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-12 | 2025 | 6 | 12 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | POWERHOUSE SHUTDOWN REPORT Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-13 | 2025 | 6 | 13 | Daral Khwar HPS | 36.6 | 36.6 | 35.92 | 864840 | 862040 | 35.02 | 14.42 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7127605.33 | 135269.39 | 2800 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 35.92 MW according to the available hydrology | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-13 | 2025 | 6 | 13 | Jabori HPS | 10.2 | 4 | 3.1 | 74510 | 72210 | 6.49 | 2.43 | 81 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 412261.33 | 985350.83 | 2300 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-13 | 2025 | 6 | 13 | Machai HPS | 2.6 | 1.63 | 0.83 | 19756 | 19012 | 27.07 | 26 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 88805.05 | 202665.35 | 744 | The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 0026Hrs dated 13.06.2025 with Reverse power due to high system voltage . Unit synchronized with the system at 0305Hrs as system voltage stabilized.The load could not be increased in accordance with the available inflow due to high system voltage, which led to elevated stator temperatures. The unit remained synchronized, delivering power to the National Grid as per system conditions. 2.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 2232Hrs dated 13.06.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault.Unit synchronized with the system at 2249Hrs as 11KV Machai-HPS line energized at 2240Hrs. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-13 | 2025 | 6 | 13 | Malakand-3 HPS | 81 | 71 | 68.03 | 1632655 | 1620100 | 51 | 44.02 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4637860.27 | 927228.53 | 12555 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-13 | 2025 | 6 | 13 | Pehur HPS | 18 | 4.67 | 3.09 | 74200 | 72000 | 16.35 | 9 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 271224 | 1356120 | 2200 | Generation is less because of opening of irrigation valve & Plant remained shut down from 2045 hrs to 2120 hrs in search of dead body recovery in the canal. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-13 | 2025 | 6 | 13 | Reshun HPS | 4.2 | 3.14 | 1.9 | 42000 | 41400 | 2.78 | 2.57 | 85.67 | 13.48 | 92.5 | 45 | 93240 | 1256875.2 | 558072 | 698803.2 | 600 | Line faults | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-13 | 2025 | 6 | 13 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-14 | 2025 | 6 | 14 | Daral Khwar HPS | 36.6 | 36.6 | 35.29 | 849770 | 846970 | 35.02 | 14.16 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7003002.05 | 259872.67 | 2800 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 35.29 MW according to the available hydrology | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-14 | 2025 | 6 | 14 | Jabori HPS | 10.2 | 4.7 | 2.36 | 56740 | 54650 | 6.49 | 1.85 | 61.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 312007.78 | 1085604.38 | 2090 | Plant was operational as per available hydrology. Moreover plant was shutdown from 0945 Hrs to 1735 Hrs for cleaning of trash rack and desiltation of sand trap at weir site. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-14 | 2025 | 6 | 14 | Machai HPS | 2.6 | 1.04 | 0.71 | 17944 | 17028 | 27.07 | 27 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 79537.79 | 211932.61 | 916 | The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 1831Hrs dated 14.06.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault. Although the 11 kV line was re energized at 1832Hrs, the unit remained shut down/standby and could not synchronize with the system due to high system voltage. The unit finally synchronized with the system at 2108Hrs once the voltage stabilized. The load could not be increased in accordance with the available inflow due to high system voltage, which led to elevated stator temperatures. The unit remained synchronized, delivering power to the National Grid as per system conditions | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-14 | 2025 | 6 | 14 | Malakand-3 HPS | 81 | 71 | 67.88 | 1629021 | 1616990 | 51 | 44.43 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4628957.27 | 936131.53 | 12031 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-14 | 2025 | 6 | 14 | Pehur HPS | 18 | 5.43 | 3.32 | 79800 | 76000 | 27.01 | 9.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 286292 | 1341052 | 3800 | Plant remained operational throughout 24 hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-14 | 2025 | 6 | 14 | Reshun HPS | 4.2 | 3.23 | 1.94 | 47000 | 46388 | 2.9 | 2.88 | 95.9 | 13.48 | 96.73 | 45 | 97507.2 | 1314397.06 | 625310.24 | 689086.82 | 612 | Tripping | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-14 | 2025 | 6 | 14 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-15 | 2025 | 6 | 15 | Daral Khwar HPS | 36.6 | 35.3 | 30.67 | 738820 | 736020 | 35.3 | 12.31 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6085634.17 | 1177240.55 | 2800 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 30.67 MW according to the available hydrology. 2. All units tripped due to over frequency at 0347Hrs. 3. Unit No.01, 03 and 02 were synchronized with national grid at 0431 Hrs, 0502 Hrs and 0532 Hrs respectively. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-15 | 2025 | 6 | 15 | Jabori HPS | 10.2 | 3 | 2.4 | 53730 | 51640 | 6.49 | 1.75 | 58.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 294823.09 | 1102789.07 | 2090 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-15 | 2025 | 6 | 15 | Machai HPS | 2.6 | 1.03 | 0.86 | 20816 | 19756 | 27.07 | 26 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 92280.28 | 199190.12 | 1060 | The load could not be increased in accordance with the available inflow due to high system voltage, which led to elevated stator temperatures. The unit remained synchronized, delivering power to the National Grid as per system conditions | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-15 | 2025 | 6 | 15 | Malakand-3 HPS | 81 | 71 | 66.36 | 1592660 | 1581060 | 51 | 43.49 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4526100.46 | 1038988.34 | 11600 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-15 | 2025 | 6 | 15 | Pehur HPS | 18 | 3.91 | 3.09 | 74200 | 72000 | 16.35 | 9 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 271224 | 1356120 | 2200 | Plant remained operational through out 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-15 | 2025 | 6 | 15 | Reshun HPS | 4.2 | 4.01 | 2.36 | 50000 | 49380 | 3.07 | 3.06 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 665642.4 | 693141.6 | 620 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-15 | 2025 | 6 | 15 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-16 | 2025 | 6 | 16 | Daral Khwar HPS | 36.6 | 34 | 23.41 | 564170 | 561770 | 35.02 | 9.39 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 4644882.89 | 2617991.83 | 2400 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 23.41 MW according to the available hydrology. 2. NOC for shutdown on 132KV Swat-Matta transmission at 0830 Hrs and was restored at 1445 Hrs. 3. Unit No.02, 01 and 03 were synchronized with national grid at 1458 Hrs, 1504 Hrs and 1509 Hrs respectively. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-16 | 2025 | 6 | 16 | Jabori HPS | 10.2 | 4 | 2.43 | 58554 | 56090 | 6.49 | 1.91 | 63.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 320229.03 | 1077383.13 | 2464 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-16 | 2025 | 6 | 16 | Machai HPS | 2.6 | 1.46 | 0.81 | 18144 | 17336 | 27 | 26 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 80976.46 | 210493.94 | 808 | The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 1216Hrs dated 16.06.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault. Although the 11 kV line was re energized at 1220Hrs, the unit remained shut down and could not synchronize with the system as PTW # 12/2025 issued at 1230Hrs to Electrical and Mech(Sec) on GOVERNOR SYSTEM to clean and dehydrate the Hydraulic oil.PTW cancelled by Maintenance section at 1900Hrs with remarks The hydraulic oil from the governor sump tank and vessel tank was drained through the purification plant filter and dehydrated up to 55°C. The sump oil tank was topped up with the cleaned oil, and two new drums of oil were added through the purification plant filter. The vessel tank was thoroughly inspected and cleaned. Runner Block is thoroughly cleaned and re-adjusted along with their respective solenoid valves . The Unit, after all preliminary checks, started and finding everything normal then synchronized with the system at 1945Hrs . | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-16 | 2025 | 6 | 16 | Malakand-3 HPS | 81 | 71 | 67.01 | 1608241 | 1595620 | 51 | 43.6 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4567781.37 | 997307.43 | 12621 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-16 | 2025 | 6 | 16 | Pehur HPS | 18 | 3.93 | 3.8 | 91200 | 87000 | 16.35 | 11 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 327729 | 1299615 | 4200 | The plant has remained operational for 24 hours against available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-16 | 2025 | 6 | 16 | Reshun HPS | 4.2 | 2.85 | 1.62 | 33000 | 32414 | 2.11 | 2.02 | 67.33 | 13.48 | 70.33 | 45 | 70896 | 955678.08 | 436940.72 | 518737.36 | 586 | Tripping due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-16 | 2025 | 6 | 16 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-17 | 2025 | 6 | 17 | Daral Khwar HPS | 36.6 | 35.3 | 31.7 | 763618 | 760810 | 35.02 | 12.72 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6290605.32 | 972269.4 | 2808 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 31.70 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-17 | 2025 | 6 | 17 | Jabori HPS | 10.2 | 5.1 | 4.2 | 77450 | 75000 | 6.49 | 2.69 | 89.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 428190 | 969422.16 | 2450 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-17 | 2025 | 6 | 17 | Machai HPS | 2.6 | 1.59 | 0.95 | 22832 | 22000 | 27.07 | 26 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 102762 | 188708.4 | 832 | 1.Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 0803Hrs dated 17-06-2025 as PTW issued to Operation staff (PESCO) on KATLANG Grid.11KV Machai-HPS line re-energized at 1225Hrs as PTW canceled by Operation staff (PESCO). Unit synchronized with the system at 1338Hrs and load gradually increased according to available inflow and system condition. 2.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 1756Hrs dated 17.06.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault.Unit synchronized with the system at 1824Hrs as 11KV Machai-HPS line energized at 1814Hrs. 3. The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 2208Hrs dated 17.06.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault. Although the 11 kV line was re energized at 2210Hrs, the unit remained shut down/standby and could not synchronize with the system due to high system voltage. The unit finally synchronized with the system at 2308Hrs once the voltage stabilized. The load could not be increased in accordance with the available inflow due to high system voltage, which led to elevated stator temperatures. The unit remained synchronized, delivering power to the National Grid as per system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-17 | 2025 | 6 | 17 | Malakand-3 HPS | 81 | 71 | 67.79 | 1626859 | 1614190 | 51 | 44.21 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4620941.71 | 944147.09 | 12669 | All units on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-17 | 2025 | 6 | 17 | Pehur HPS | 18 | 3.94 | 3.82 | 91800 | 89000 | 27.01 | 11 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 335263 | 1292081 | 2800 | Plant remained operational throughout 24 hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-17 | 2025 | 6 | 17 | Reshun HPS | 4.2 | 3.41 | 2.27 | 54000 | 53399 | 3.31 | 3.3 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 719818.52 | 638965.48 | 601 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-17 | 2025 | 6 | 17 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-18 | 2025 | 6 | 18 | Daral Khwar HPS | 36.6 | 36.6 | 33.1 | 797200 | 794400 | 35.02 | 13.29 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6568337.52 | 694537.2 | 2800 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 33.10 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-18 | 2025 | 6 | 18 | Jabori HPS | 10.2 | 4 | 2.1 | 62552 | 60000 | 6.49 | 2.21 | 73.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 342552 | 1055060.16 | 2552 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-18 | 2025 | 6 | 18 | Machai HPS | 2.6 | 1.24 | 0.96 | 23332 | 22132 | 27.07 | 26.5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 103378.57 | 188091.83 | 1200 | The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 0720Hrs,2144Hrs & 2332Hrs dated 18.06.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault.Unit synchronized with the system at 0742Hrs,2307Hrs & 2342Hrs respectively as 11KV Machai-HPS line energized at 0723Hrs,2151Hrs & 2339Hrs . The load could not be increased in accordance with the available inflow due to high system voltage, which led to elevated stator temperatures. The unit remained synchronized, delivering power to the National Grid as per system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-18 | 2025 | 6 | 18 | Malakand-3 HPS | 81 | 71 | 67.31 | 1615450 | 1602460 | 51 | 43.56 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4587362.24 | 977726.56 | 12990 | 132KV supply shut down as per fax message & telephonic conversation from Mr. Rizwan of ISMO dated: 19-06-2025. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-18 | 2025 | 6 | 18 | Pehur HPS | 18 | 4.02 | 3.92 | 94200 | 90000 | 16.35 | 11 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 339030 | 1288314 | 4200 | The plant has remained operational for 24 hours against available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-18 | 2025 | 6 | 18 | Reshun HPS | 4.2 | 3.29 | 2.05 | 48000 | 47400 | 2.96 | 2.93 | 97.67 | 13.48 | 98.67 | 45 | 99456 | 1340666.88 | 638952 | 701714.88 | 600 | Lime faults | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-18 | 2025 | 6 | 18 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-19 | 2025 | 6 | 19 | Daral Khwar HPS | 36.6 | 36.6 | 34.73 | 836290 | 833490 | 35.02 | 13.94 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6891545.37 | 371329.35 | 2800 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 34.73 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-19 | 2025 | 6 | 19 | Jabori HPS | 10.2 | 3.4 | 2.4 | 59807 | 57360 | 6.49 | 1.95 | 65 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 327479.71 | 1070132.45 | 2447 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-19 | 2025 | 6 | 19 | Machai HPS | 2.6 | 1.6 | 0.93 | 22680 | 21604 | 27.07 | 26 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 100912.28 | 190558.12 | 1076 | The unit, while on bar and delivering power to the National Grid as per available water inflow and prevailing system conditions, tripped at 0702Hrs and 1300Hrs on 19.06.2025 due to reverse power resulting from high system voltage. Subsequently, the unit remained shut down/standby and could not be synchronized with the system due to persistently high system voltage. The unit was finally synchronized with the system at 1010Hrs and 1432Hrs respectively, once the voltage stabilized. The load could not be increased in accordance with the available inflow due to high system voltage, which led to elevated stator temperatures. The unit remained synchronized, delivering power to the National Grid as per system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-19 | 2025 | 6 | 19 | Malakand-3 HPS | 81 | 74 | 55.35 | 1328284 | 1317260 | 51 | 37.64 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3770920.2 | 1794168.6 | 11024 | As reported (by Irrigation department) water diverted at Admandara Head works to Swat river to facilitate the searching of dead body. Therefore Unit # 02 & 03 desynchronized from the system due to decrease inflow at Forebay. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-19 | 2025 | 6 | 19 | Pehur HPS | 18 | 4.13 | 4 | 95900 | 92000 | 16.35 | 11 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 346564 | 1280780 | 3900 | Plant operational 24 hrs | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-19 | 2025 | 6 | 19 | Reshun HPS | 4.2 | 3.27 | 2.28 | 51000 | 50379 | 3.14 | 3.12 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 679108.92 | 679675.08 | 621 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-19 | 2025 | 6 | 19 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-20 | 2025 | 6 | 20 | Daral Khwar HPS | 36.6 | 36.6 | 34.99 | 842630 | 839830 | 35.02 | 14.04 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6943966.39 | 318908.33 | 2800 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 34.99 MW according to the available hydrology. 2. Unit No.3 tripped at 2244 Hrs due to auxiliary failure caused by wind at 11KV Line. Unit synchronized at 2249 Hrs. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-20 | 2025 | 6 | 20 | Jabori HPS | 10.2 | 4.1 | 2.6 | 63661 | 61460 | 6.49 | 2.08 | 69.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 350887.43 | 1046724.73 | 2201 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-20 | 2025 | 6 | 20 | Machai HPS | 2.6 | 1.64 | 0.51 | 14000 | 13200 | 27.07 | 14 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 61657.2 | 229813.2 | 800 | 1.The unit, while on bar and delivering power to the National Grid as per available water inflow and prevailing system conditions, tripped at 0719Hrs on 20.06.2025 due to reverse power resulting from high system voltage. Subsequently, the unit remained shut down/standby and could not be synchronized with the system due to persistently high system voltage. The unit was finally synchronized with the system at 0906Hrs, once the voltage stabilized. 2.Unit precautionary shut down at 1245Hrs Dated 20-06-2025 due to the drop in head race level as water decreased by irrigation department for the searching of human dead body.The Unit after all preliminary checks and then synchronized with the system at 2024Hrs Dated 20-06-2025 as rated head was restored due to increase in canal discharge as water supply for Machai was restored. 3.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 2254 & 2314Hrs dated 20.06.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault.Unit synchronized with the system at 2302Hr & 2330Hrs respectively as 11KV Machai-HPS line energized at 2302Hrs & 2337Hrs. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-20 | 2025 | 6 | 20 | Malakand-3 HPS | 81 | 77 | 44.91 | 1077938 | 1069210 | 51 | 30.48 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3060827.47 | 2504261.33 | 8728 | As reported by Irrigation department water diverted at Amandara Head works to Swat river to facilitate the searching of dead body. Unit # 01,02 & 03 Desynchronized from the system due to decrease inflow at Forebay. Subsequently, the units were resynchronized with the system as follows: Unit #01 at 1703 Hrs Unit #02 at 1609 Hrs Unit #03 at 1613 Hrs As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-20 | 2025 | 6 | 20 | Pehur HPS | 18 | 4.23 | 4.09 | 98200 | 96000 | 16.35 | 11 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 361632 | 1265712 | 2200 | The plant has remained operational for 24 hours as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-20 | 2025 | 6 | 20 | Reshun HPS | 4.2 | 3.72 | 2.41 | 54000 | 53398 | 3.31 | 3.3 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 719805.04 | 638978.96 | 602 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-20 | 2025 | 6 | 20 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-21 | 2025 | 6 | 21 | Daral Khwar HPS | 36.6 | 36.6 | 34.03 | 819960 | 816760 | 35.02 | 13.66 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6753216.71 | 509658.01 | 3200 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 34.03 MW according to the available hydrology. 2. 132 KV Supply line failed at 1815 Hrs and was restored at 1841 Hrs. 3. Unit No.02, 03 and 01 were synchronised with national grid at 1851 Hrs, 1852 Hrs and 1856 Hrs respectively. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-21 | 2025 | 6 | 21 | Jabori HPS | 10.2 | 4.8 | 2.7 | 65032 | 62910 | 6.7 | 2.12 | 70.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 359165.77 | 1038446.39 | 2122 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-21 | 2025 | 6 | 21 | Machai HPS | 2.6 | 1.5 | 0.86 | 21332 | 20464 | 27.07 | 27 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 95587.34 | 195883.06 | 868 | 1.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 0024Hrs & 1411Hrs dated 21.06.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault.Unit synchronized with the system at 0130Hrs & 1434Hrs respectively as 11KV Machai-HPS line energized at 0034Hrs & 1430Hrs. 2.The unit, while on bar and delivering power to the National Grid,got tripped at 1949Hrs dated 20-06-2025. The tripping occurred due to a fault on the 11 kV MACHAI-HPS feeder, which experienced an earth fault and instantaneous fault, attributed to adverse weather conditions. An inquiry call was made to Katlang Grid regarding the tripping and possible restoration of power. As per their response, the line could not be restored since the fault still persists. The operation staff of PESCO was informed of the fault. The LS-Operation, PESCO (Mardan) was contacted and requested to take the necessary action to energize the feeder at the earliest. Follow-up communication was made with the Line Superintendent (PESCO) to inquire about the status of the 11 kV Machai-HPS line fault. According to his response, the fault still exists, and the field team is actively working to rectify it. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-21 | 2025 | 6 | 21 | Malakand-3 HPS | 81 | 74 | 62.35 | 1496372 | 1485000 | 51 | 45 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4251109.5 | 1313979.3 | 11372 | 132kv line tripped due to extreme weather Conditions, including a heavy storm causing tripping of Units at 1855Hrs. Subsequently, the Two units were resynchronized with the system as follows: Unit #02 at 2035 Hrs and Unit #03 at 2049 Hrs. As per available hydrology from Irrigation Department Two Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-21 | 2025 | 6 | 21 | Pehur HPS | 18 | 6.53 | 4.56 | 109500 | 105000 | 16.35 | 12 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 395535 | 1231809 | 4500 | The plant has remained operational for the last 24 hours against available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-21 | 2025 | 6 | 21 | Reshun HPS | 4.2 | 3.06 | 2.24 | 55000 | 54388 | 3.38 | 3.37 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 733150.24 | 625633.76 | 612 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-21 | 2025 | 6 | 21 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-22 | 2025 | 6 | 22 | Daral Khwar HPS | 36.6 | 36.6 | 34.34 | 826940 | 824140 | 35.02 | 13.78 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6814236.76 | 448637.96 | 2800 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 34.34 MW according to the available hydrology | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-22 | 2025 | 6 | 22 | Jabori HPS | 10.2 | 5 | 0.85 | 20585 | 19540 | 6.7 | 0.67 | 22.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 111557.77 | 1286054.39 | 1045 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-22 | 2025 | 6 | 22 | Machai HPS | 2.6 | 1.81 | 0.7 | 16024 | 15400 | 27.07 | 20 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 71933.4 | 219537 | 624 | 1.Unit remains on standby since 1949Hrs dated 21-06-2025 as the fault has not yet been cleared by the operation staff (PESCO), due to ongoing adverse weather conditions.11 kV Machai-HPC feeder was subsequently re-energized at 0818Hrs Dated 22-06-2025 following the clearance of the fault by PESCO operation staff who removed tree branches from the line and Unit synchronized with the system at 0838Hrs dated 22-06-2025. 2.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 1103Hrs & 1829Hrs dated 22.06.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault.Unit synchronized with the system at 1127Hrs & 1907Hrs respectively as 11KV Machai-HPS line energized at 1113Hrs & 1842Hrs. 3.The unit, while on bar and delivering power to the National Grid as per available water inflow and prevailing system conditions, tripped at 1148Hrs on 22.06.2025 due to reverse power resulting from high system voltage. Subsequently, the unit remained shut down/standby and could not be synchronized with the system due to persistently high system voltage. The unit was finally synchronized with the system at 1227Hrs, once the voltage stabilized. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-22 | 2025 | 6 | 22 | Malakand-3 HPS | 81 | 71 | 60.03 | 1440607 | 1429430 | 51 | 44.39 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4092029.26 | 1473059.54 | 11177 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. Hydrology is decreased due to variation in river flow, confirmed from Irrigation department. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-22 | 2025 | 6 | 22 | Pehur HPS | 18 | 6.49 | 6.05 | 145200 | 140000 | 16.35 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 527380 | 1099964 | 5200 | Plant remained operational through out 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-22 | 2025 | 6 | 22 | Reshun HPS | 4.2 | 3.78 | 2.49 | 56000 | 55368 | 3.44 | 3.43 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 746360.64 | 612423.36 | 632 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-22 | 2025 | 6 | 22 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-23 | 2025 | 6 | 23 | Daral Khwar HPS | 36.6 | 32.3 | 30.97 | 746580 | 743380 | 35.02 | 12.43 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6146488.85 | 1116385.87 | 3200 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 30.97 MW according to the available hydrology | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-23 | 2025 | 6 | 23 | Jabori HPS | 10.2 | 5 | 4.28 | 36280 | 35030 | 6.7 | 3.36 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 199993.28 | 1197618.88 | 1250 | 1- Plant was operational and delivering power to national grid as per available hydrology. 2- Plant was precautionary shutdown due to maintenance of Cooling Water Pumps from 1200 Hrs to 0400 Hrs and from 1300 Hrs to 2320 Hrs. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-23 | 2025 | 6 | 23 | Machai HPS | 2.6 | 1.8 | 0.77 | 17768 | 16804 | 27.07 | 26.5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 78491.48 | 212978.92 | 964 | 1.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 0006Hrs & 2241Hrs dated 23.06.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault.Unit synchronized with the system at 0112Hrs & 2258Hrs respectively as 11KV Machai-HPS line energized at 0024Hrs & 2246Hrs. 2.The unit, while on bar and delivering power to the National Grid as per available water inflow and prevailing system conditions, tripped at 0144Hrs & 1258Hrs on 23.06.2025 due to reverse power resulting from high system voltage. Subsequently, the unit remained shut down/standby and could not be synchronized with the system due to persistently high system voltage. The unit was finally synchronized with the system at 0545Hrs & 1419Hrs respectively, once the voltage stabilized. The load could not be increased in accordance with the available inflow due to high system voltage, which led to elevated stator temperatures. The unit remained synchronized, delivering power to the National Grid as per system conditions | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-23 | 2025 | 6 | 23 | Malakand-3 HPS | 81 | 69 | 64.38 | 1545090 | 1532710 | 51 | 43.06 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4387688.92 | 1177399.88 | 12380 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-23 | 2025 | 6 | 23 | Pehur HPS | 18 | 6.71 | 5.37 | 129100 | 125000 | 27.07 | 13 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 470875 | 1156469 | 4100 | Plant remained operational throughout 24 hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-23 | 2025 | 6 | 23 | Reshun HPS | 4.2 | 3.54 | 2.52 | 58000 | 57389 | 3.56 | 3.55 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 773603.72 | 585180.28 | 611 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-23 | 2025 | 6 | 23 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-24 | 2025 | 6 | 24 | Daral Khwar HPS | 36.6 | 31.3 | 30.07 | 724560 | 721760 | 35.02 | 12.07 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 5967728.21 | 1295146.51 | 2800 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 30.07 MW according to the available hydrology | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-24 | 2025 | 6 | 24 | Jabori HPS | 10.2 | 3 | 2.57 | 59143 | 57000 | 6.7 | 2 | 66.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 325424.4 | 1072187.76 | 2143 | Plant was shutdown from 1153 Hrs to 1251 Hrs due to necessary maintenance of cooling water pumps. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-24 | 2025 | 6 | 24 | Machai HPS | 2.6 | 1.52 | 0.74 | 16556 | 15400 | 27.07 | 27 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 71933.4 | 219537 | 1156 | 1.The unit, while on bar and delivering power to the National Grid as per available water inflow and prevailing system conditions, tripped at 0100Hrs & 0524Hrs on 24.06.2025 due to reverse power resulting from high system voltage.The unit were synchronized with the system at 0110Hrs & 0541Hrs respectively, once the voltage stabilized. The load could not be increased in accordance with the available inflow due to high system voltage, which led to elevated stator temperatures. The unit remained synchronized, delivering power to the National Grid as per system conditions. 2.33. Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 0630Hrs dated 24-06-2025 as PTW issued to Operation staff (PESCO) on KATLANG Grid.11KV Machai-HPS line re-energized at 0930Hrs as PTW canceled by Operation staff (PESCO). Unit synchronized with the system at 1054Hrs and load gradually increased according to available inflow and system condition. 3.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 2101Hrs & 2305Hrs dated 24.06.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault.Unit synchronized with the system at 2110Hrs & 2348Hrs respectively as 11KV Machai-HPS line energized at 2105Hrs & 2318Hrs. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-24 | 2025 | 6 | 24 | Malakand-3 HPS | 81 | 68 | 65.1 | 1562309 | 1549280 | 51 | 42.98 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4435123.86 | 1129964.94 | 13029 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-24 | 2025 | 6 | 24 | Pehur HPS | 18 | 5.84 | 5.02 | 120700 | 117000 | 27.07 | 12 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 440739 | 1186605 | 3700 | Plant off the bar for 01:49 hrs due to drowned person in the canal. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-24 | 2025 | 6 | 24 | Reshun HPS | 4.2 | 3.4 | 2.64 | 62000 | 61370 | 3.78 | 3.8 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 827267.6 | 531516.4 | 630 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-24 | 2025 | 6 | 24 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-25 | 2025 | 6 | 25 | Daral Khwar HPS | 36.6 | 36.6 | 31.79 | 766080 | 762880 | 35.02 | 12.76 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6307720.7 | 955154.02 | 3200 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 31.79 MW according to the available hydrology | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-25 | 2025 | 6 | 25 | Jabori HPS | 10.2 | 4.8 | 3.04 | 45680 | 44200 | 6.7 | 2.38 | 79.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 252346.64 | 1145265.52 | 1480 | Plant was shutdown from 1035 Hrs to 1648 Hrs and from 2017 Hrs to 2204 Hrs for maintenance work on SCADA Server. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-25 | 2025 | 6 | 25 | Machai HPS | 2.6 | 1.54 | 0.7 | 17540 | 16676 | 27.07 | 26 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 77893.6 | 213576.8 | 864 | 1.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 0914Hrs,1236Hrs, 1403Hrs & 1423Hrs dated 25.06.2025 due to a fault on the 11 kV MACHAI-HPS feeder, which experienced an earth fault and instantaneous fault, attributed to adverse weather conditions. Unit synchronized with the system at 1025Hrs,1315Hrs,1410Hrs & 1510Hrs respectively as 11KV Machai-HPS line energized at 1019Hrs, 1309Hrs,1406Hrs & 1504Hrs . The load could not be increased in accordance with the available inflow due to high system voltage, which led to elevated stator temperatures. The unit remained synchronized, delivering power to the National Grid as per system conditions. 2.The unit, while on bar and delivering power to the National Grid as per available water inflow and prevailing system conditions, tripped at 2131Hrs on 25.06.2025 due to reverse power resulting from high system voltage. Subsequently, the unit remained shut down/standby and could not be synchronized with the system due to persistently high system voltage. The unit was finally synchronized with the system at 0007Hrs, once the voltage stabilized. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-25 | 2025 | 6 | 25 | Malakand-3 HPS | 81 | 68 | 61.35 | 1472362 | 1459500 | 51 | 40.7 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4178110.65 | 1386978.15 | 12862 | Due to heavy rain in the surrounding of swat river catchment area the water flow is reduced by Irrigation department and Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-25 | 2025 | 6 | 25 | Pehur HPS | 18 | 7.49 | 6.59 | 158200 | 153000 | 27.07 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 576351 | 1050993 | 5200 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-25 | 2025 | 6 | 25 | Reshun HPS | 4.2 | 3.38 | 2.34 | 49000 | 48399 | 3.01 | 3 | 99.97 | 13.48 | 100 | 45 | 100800 | 1358784 | 652418.52 | 706365.48 | 601 | Outgoing feeder Breaker tripped. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-25 | 2025 | 6 | 25 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-26 | 2025 | 6 | 26 | Daral Khwar HPS | 36.6 | 34.8 | 30.51 | 735080 | 732280 | 35.02 | 12.25 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6054710.72 | 1208164 | 2800 | 1. Unit No. 01, 02 and 03 were on bar delivering an average load equal to 30.51MW, according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-26 | 2025 | 6 | 26 | Jabori HPS | 10.2 | 4.8 | 2.32 | 48796 | 47090 | 6.7 | 1.82 | 60.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 268846.23 | 1128765.93 | 1706 | Plant was shutdown from 2030 Hrs to 2335 Hrs for checking of different equipments including cooling water pumps, unit #02 synchronizer and SCADA by contractor representative. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-26 | 2025 | 6 | 26 | Machai HPS | 2.6 | 1.29 | 0.84 | 20012 | 19096 | 27.07 | 25 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 89197.42 | 202272.98 | 916 | Unit tripped three times on Earth fault. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-26 | 2025 | 6 | 26 | Malakand-3 HPS | 81 | 61 | 57.85 | 1388331 | 1376440 | 51 | 39.28 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3940334.79 | 1624754.01 | 11891 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-26 | 2025 | 6 | 26 | Pehur HPS | 18 | 7.96 | 7.63 | 183100 | 177000 | 16.35 | 17 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 666759 | 960585 | 6100 | Plant remained operational through out 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-26 | 2025 | 6 | 26 | Reshun HPS | 4.2 | 3.38 | 2.5 | 55000 | 54397 | 3.37 | 3.38 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 733271.56 | 625512.44 | 603 | Line faults | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-26 | 2025 | 6 | 26 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-27 | 2025 | 6 | 27 | Daral Khwar HPS | 36.6 | 36.6 | 31.39 | 756250 | 753450 | 35.02 | 12.6 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6229750.64 | 1033124.08 | 2800 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 31.39 MW according to the available hydrology | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-27 | 2025 | 6 | 27 | Jabori HPS | 10.2 | 5.1 | 3.25 | 45630 | 43870 | 6.7 | 2.55 | 85 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 250462.6 | 1147149.56 | 1760 | Plant was precautionary shutdown at 1552 Hrs dated 27-06-2025 due to extremely muddy water at weir site. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-27 | 2025 | 6 | 27 | Machai HPS | 2.6 | 0.99 | 0.47 | 15724 | 14828 | 27.07 | 24 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 69261.59 | 222208.81 | 896 | Unit 2 times tripped due to the tripping of 132KV line Mardan tripped. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-27 | 2025 | 6 | 27 | Malakand-3 HPS | 81 | 62 | 42.57 | 1021607 | 1012560 | 51 | 37.02 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2898655.51 | 2666433.29 | 9047 | continuous heavy rainfall in the Upper Swat region, severe flooding has occurred, resulting in highly turbid water carrying large volumes of garbage, debris, and silt. This has led to the choking of trash racks at the forebay, obstructing normal water flow. As a preventive measure to avoid equipment damage and ensure operational safety, Unit # 01 desynchronized at 17.15hrs ,Unit # 02 desynchronized at 16:28hrs& Unit # 03 desynchronized at 16:14hrs dated 27-06-2025 | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-27 | 2025 | 6 | 27 | Pehur HPS | 18 | 8.63 | 6.84 | 164100 | 158000 | 16.35 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 595186 | 1032158 | 6100 | Plant remained shutdown for 03 Hrs 10 mins as per instructions of irrigation SDO due to flood warning. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-27 | 2025 | 6 | 27 | Reshun HPS | 4.2 | 3.34 | 2.6 | 57000 | 56400 | 3.5 | 3.49 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 760272 | 598512 | 600 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-27 | 2025 | 6 | 27 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-28 | 2025 | 6 | 28 | Daral Khwar HPS | 36.6 | 31.8 | 28.19 | 679240 | 676440 | 35.02 | 11.31 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 5593008.85 | 1669865.87 | 2800 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 28.19 MW according to the available hydrology | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-28 | 2025 | 6 | 28 | Jabori HPS | 10.2 | 5.1 | 3.3 | 39610 | 38140 | 6.7 | 2.58 | 86 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 217748.89 | 1179863.27 | 1470 | Unit #01 was synchronized at 1245 Hrs with the national grid after the muddy rainwater from the weir site had subsided. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-28 | 2025 | 6 | 28 | Machai HPS | 2.6 | 1.24 | 0.23 | 4380 | 4224 | 27.07 | 13 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 19730.3 | 271740.1 | 156 | 1. The unit, while on bar and delivering power to the National Grid as per available water inflow and prevailing system conditions, tripped at 0223Hrs on 28.06.2025 due to reverse power resulting from high system voltage. Subsequently, the unit remained shut down/standby and could not be synchronized with the system due to persistently high system voltage. The unit was finally synchronized with the system at 0927Hrs, once the voltage stabilized. 2.The unit was precautionarily shut down at 1328Hrs on 28-06-2025 due to a drop in headrace level, following water diversion by the Irrigation Department from Amandara Headworks. According to a report from the Sub Engineer, Irrigation Department (Katlang Section), the trash rack at RD-75+000 of the Machai Branch Syphon was damaged during a heavy windstorm and rainfall on 28-06-2025. Consequently, water supply to the Machai Branch has been suspended until the damaged trash rack at RD-75+000 is repaired to allow for urgent restoration. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-28 | 2025 | 6 | 28 | Malakand-3 HPS | 81 | 19 | 2.42 | 58036 | 57300 | 51 | 2 | 66.67 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 164032.71 | 5401056.09 | 736 | Water was diverted at Amandara Headworks by the Irrigation Department to facilitate the repair of the trash rack at RD 75+000 on the Machai Branch Syphon, following damage caused by recent rainfall. Therefore, the Malakand III Complex was shut down. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-28 | 2025 | 6 | 28 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 16.35 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down for 24 hours due to nil irrigation demand and a flood warning in the command area. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-28 | 2025 | 6 | 28 | Reshun HPS | 4.2 | 3.38 | 1.15 | 38000 | 37404 | 2.35 | 2.33 | 77.53 | 13.48 | 78.33 | 45 | 78960 | 1064380.8 | 504205.92 | 560174.88 | 596 | Flow of water decreased due to accumulation of sand and gravel at Intake area. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-28 | 2025 | 6 | 28 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-29 | 2025 | 6 | 29 | Daral Khwar HPS | 36.6 | 27 | 25.48 | 614800 | 611600 | 35.02 | 10.23 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 5056892.28 | 2205982.44 | 3200 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 25.48 MW according to the available hydrology | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-29 | 2025 | 6 | 29 | Jabori HPS | 10.2 | 4.8 | 2.44 | 46450 | 44370 | 6.7 | 1.92 | 64 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 253317.2 | 1144294.96 | 2080 | Plant was precautionary shutdown at 1913 Hrs dated 29-06-2025 due to extremely muddy water at weir site. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-29 | 2025 | 6 | 29 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 27.07 | 0 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 1328Hrs on 28-06-2025 due to insufficient, Following water diversion by the Irrigation Department from Amandara Headworks. According to a report from the Sub Engineer, Irrigation Department (Katlang Section), the trash rack at RD-75+000 of the Machai Branch Syphon was damaged during a heavy windstorm and rainfall on 28-06-2025. Consequently, water supply to the Machai Branch has been suspended until the damaged trash rack at RD-75+000 is repaired to allow for urgent restoration. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-06-29 | 2025 | 6 | 29 | Malakand-3 HPS | 81 | 70 | 7.55 | 181261 | 179580 | 51 | 4.86 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 514083.67 | 5051005.13 | 1681 | Units synchronized with the system after restoration of water supply by irrigation department. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-29 | 2025 | 6 | 29 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 27.07 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | Plant remained shut down since 2050 Hours dated 27-06-2025 upon instruction of irrigation SDO due to nil irrigation and flood warning in the command area. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-29 | 2025 | 6 | 29 | Reshun HPS | 4.2 | 1.94 | 1.56 | 40000 | 39410 | 2.45 | 2.45 | 81.6 | 13.48 | 81.73 | 45 | 82387.2 | 1110579.46 | 531246.8 | 579332.66 | 590 | Due to accumulation of sand and gravel in weir, the flow of can't be diverting. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-29 | 2025 | 6 | 29 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-30 | 2025 | 6 | 30 | Daral Khwar HPS | 36.6 | 25 | 23.77 | 573320 | 570520 | 35.02 | 9.54 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 4717230.52 | 2545644.2 | 2800 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 23.77 MW according to the available hydrology | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-30 | 2025 | 6 | 30 | Jabori HPS | 10.2 | 5.1 | 4.26 | 66035 | 64260 | 6.7 | 3.34 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 366873.19 | 1030738.97 | 1775 | Unit # 01 was synchronized at 0825 Hrs with the national grid after the muddy rainwater from the weir site had subsided. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-30 | 2025 | 6 | 30 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 27.07 | 10 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 1328 Hrs on 28-06-2025 due to insufficient hydrology. The trash rack at RD-75+000 of the Machai Branch Syphon has not been repaired by the Irrigation Department. Instead, they have decided to keep the said syphon open without a trash rack. Water was re-diverted to the Machai Canal by the Irrigation Department on 30-06-2025, with recorded inflow reaching up to 10 cumecs. A call was made to Mr. Fazli Wahid (Irrigation Department) to inquire about the low inflow. As per his response, there is currently no water demand from the XEN (Swabi Irrigation Division) due to recent heavy rainfall. Therefore, the water supply to Machai will remain between 9 to 11 cumecs until the next indent, which is insufficient for the smooth operation of the plant | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-06-30 | 2025 | 6 | 30 | Malakand-3 HPS | 81 | 68 | 61.6 | 1478390 | 1466060 | 51 | 39.99 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4196889.96 | 1368198.84 | 12330 | All units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-30 | 2025 | 6 | 30 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 27.07 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | Plant remained shut down since 2050 Hours dated 27-06-2025 upon instruction of irrigation SDO due to nil irrigation and flood warning in the command area. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-30 | 2025 | 6 | 30 | Reshun HPS | 4.2 | 1.97 | 1.62 | 34000 | 33424 | 2.18 | 2.08 | 69.37 | 13.48 | 72.67 | 45 | 73248 | 987383.04 | 450555.52 | 536827.52 | 576 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-06-30 | 2025 | 6 | 30 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-01 | 2025 | 7 | 1 | Daral Khwar HPS | 36.6 | 23 | 22.36 | 539400 | 536600 | 28.25 | 8.97 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 4436769.78 | 2826104.94 | 2800 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 22.36 MW according to the available hydrology | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-01 | 2025 | 7 | 1 | Jabori HPS | 10.2 | 4.7 | 3.26 | 78340 | 75880 | 7.62 | 2.56 | 85.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 433214.1 | 964398.06 | 2460 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-01 | 2025 | 7 | 1 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 28.34 | 29.6 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 1328 Hrs on 28-06-2025 due to insufficient hydrology. Water was re-diverted to the Machai Canal by the Irrigation Department on 30-06-2025, with recorded inflow reaching up to 10 cumecs. A call was made to Mr. Fazli Wahid (Irrigation Department) to inquire about the low inflow. As per his response, there is currently no water demand from the XEN (Swabi Irrigation Division) due to recent heavy rainfall. Therefore, the water supply to Machai will remain between 9 to 11 cumecs until the next indent, which is insufficient for the smooth operation of the plant. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load; Avg Historical Hydrology interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-07-01 | 2025 | 7 | 1 | Malakand-3 HPS | 81 | 68 | 61.54 | 1477003 | 1464400 | 51 | 40.27 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4192137.88 | 1372950.92 | 12603 | All units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-01 | 2025 | 7 | 1 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 21.22 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | Plant shut down since 27-06-2025 due to nil irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-01 | 2025 | 7 | 1 | Reshun HPS | 4.2 | 2.77 | 1.94 | 46000 | 45417 | 2.89 | 2.82 | 93.87 | 13.48 | 96.33 | 45 | 97104 | 1308961.92 | 612221.16 | 696740.76 | 583 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-01 | 2025 | 7 | 1 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-02 | 2025 | 7 | 2 | Daral Khwar HPS | 36.6 | 21.5 | 20.9 | 504380 | 501580 | 28.25 | 8.39 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 4147213.91 | 3115660.81 | 2800 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 20.90 MW according to the available hydrology | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-02 | 2025 | 7 | 2 | Jabori HPS | 10.2 | 3.5 | 2.78 | 66768 | 64320 | 7.62 | 2.18 | 72.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 367215.74 | 1030396.42 | 2448 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-02 | 2025 | 7 | 2 | Machai HPS | 2.6 | 0.88 | 0.39 | 9224 | 8712 | 29.6 | 16 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 40693.75 | 250776.65 | 512 | 1.The Unit after all preliminary checks and started at 1140Hrs Dated 02-07-2025 as rated head was restored due to increase in canal discharge as per new indent of Swabi Irrigation Sub Division. Unit kept on FSNL for an half hour to carryout heat run test and finding everything normal then synchronized with the system at 1213Hrs and load gradually increased according to available inflow and system condition. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-02 | 2025 | 7 | 2 | Malakand-3 HPS | 81 | 66 | 59.89 | 1437355 | 1424590 | 51 | 40.04 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4078173.79 | 1486915.01 | 12765 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. Inflow is low due to water reduced by irrigation department. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-02 | 2025 | 7 | 2 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 21.22 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant remained shut down because of nil irrigation demand for 24 hours. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-02 | 2025 | 7 | 2 | Reshun HPS | 4.2 | 3.29 | 2.44 | 49000 | 48519 | 3.02 | 3 | 99.97 | 13.48 | 100 | 45 | 100800 | 1358784 | 654036.12 | 704747.88 | 481 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-02 | 2025 | 7 | 2 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-03 | 2025 | 7 | 3 | Daral Khwar HPS | 36.6 | 20 | 19.93 | 481010 | 478210 | 28.25 | 8 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3953983.74 | 3308890.98 | 2800 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 19.93 MW according to the available hydrology | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-03 | 2025 | 7 | 3 | Jabori HPS | 10.2 | 2.7 | 2.4 | 57715 | 55270 | 7.62 | 1.88 | 62.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 315547.48 | 1082064.68 | 2445 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-03 | 2025 | 7 | 3 | Machai HPS | 2.6 | 1 | 0.53 | 13708 | 12716 | 29.6 | 17 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 59396.44 | 232073.96 | 992 | 1.The unit, while on bar and delivering power to the National Grid as per available water inflow and prevailing system conditions, tripped at 0049Hrs and 0436Hrs on 03.07.2025 due to reverse power resulting from high system voltage. Subsequently, the unit remained shut down/standby and could not be synchronized with the system due to persistently high system voltage. The unit was finally synchronized with the system at 0419Hrs and 0522Hrs respectively, once the voltage stabilized. The load could not be increased in accordance with the available inflow due to high system voltage, which led to elevated stator temperatures. The unit remained synchronized, delivering power to the National Grid as per system conditions. 2.Due to the recent heavy rainfall, reduced hydrological discharge was maintained in accordance with the demand of the XEN (Swabi Irrigation Division). | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-03 | 2025 | 7 | 3 | Malakand-3 HPS | 81 | 64 | 56.97 | 1367380 | 1354570 | 51 | 38.75 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3877727.54 | 1687361.26 | 12810 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running.Inflow is low due to water reduced by irrigation department. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-03 | 2025 | 7 | 3 | Pehur HPS | 18 | 6.87 | 1.24 | 29700 | 29000 | 21.22 | 2 | 66.67 | 3.767 | 100 | 41 | 432000 | 1627344 | 109243 | 1518101 | 700 | The plant has remained operational since 1930 hours on 03-07-2025 with restricted flow. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-03 | 2025 | 7 | 3 | Reshun HPS | 4.2 | 1.72 | 1.02 | 24502 | 49964 | 3.12 | 3.09 | 24.31 | 13.48 | 100 | 45 | 100800 | 1358784 | 673514.72 | 685269.28 | 0 | No data submitted for this date | zafar.src@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-07-03 | 2025 | 7 | 3 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-04 | 2025 | 7 | 4 | Daral Khwar HPS | 36.6 | 20 | 19.42 | 468910 | 466110 | 28.25 | 7.8 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3853937.31 | 3408937.41 | 2800 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 19.42 MW according to the available hydrology. 2. 132 KV Supply line tripped at 2355 Hrs. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-04 | 2025 | 7 | 4 | Jabori HPS | 10.2 | 2.4 | 2.38 | 57144 | 54720 | 7.62 | 1.86 | 62 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 312407.42 | 1085204.74 | 2424 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-04 | 2025 | 7 | 4 | Machai HPS | 2.6 | 0.89 | 0.76 | 17540 | 16456 | 29.6 | 18 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 76865.98 | 214604.42 | 1084 | 1.Due to the recent heavy rainfall, reduced hydrological discharge was maintained in accordance with the demand of the XEN (Swabi Irrigation Division). | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-04 | 2025 | 7 | 4 | Malakand-3 HPS | 81 | 63 | 56.81 | 1363431 | 1351090 | 51 | 38.63 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3867765.34 | 1697323.46 | 12341 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. Inflow is low due to water reduced by irrigation department. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-04 | 2025 | 7 | 4 | Pehur HPS | 18 | 7.33 | 6.35 | 152500 | 147000 | 21.22 | 11 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 553749 | 1073595 | 5500 | Unit# 01 & 02 were taken off the bar at 2138 & 2152 Hrs upon the instructions of SDO irrigation due to nil irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-04 | 2025 | 7 | 4 | Reshun HPS | 4.2 | 52000 | 2.49 | 3 | 51410 | 3.22 | 3.18 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 693006.8 | 665777.2 | 51406.66 | Nil | zafar.src@gmail.com | Original | CHECK: Net > Units (source me verify karein) | Link_Generation_Data_Summary.xlsx
2025-07-04 | 2025 | 7 | 4 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-05 | 2025 | 7 | 5 | Daral Khwar HPS | 36.6 | 21.5 | 19.95 | 481500 | 478700 | 28.25 | 8.01 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3958035.21 | 3304839.51 | 2800 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 19.95 MW according to the available hydrology. 2. 132 KV Supply line was restored at 00:35 Hrs. 3. Unit No.03, 01 and 02 were synchronised with national grid at 00:45 Hrs, 00:50 Hrs and 00:52 Hrs respectively. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-05 | 2025 | 7 | 5 | Jabori HPS | 10.2 | 3 | 2 | 46570 | 44130 | 7.62 | 1.6 | 53.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 251947 | 1145665.16 | 2440 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-05 | 2025 | 7 | 5 | Machai HPS | 2.6 | 1.07 | 0.68 | 16988 | 15708 | 29.6 | 17 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 73372.07 | 218098.33 | 1280 | Due to the recent heavy rainfall, reduced hydrological discharge was maintained in accordance with the demand of the XEN (Swabi Irrigation Division). | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-05 | 2025 | 7 | 5 | Malakand-3 HPS | 81 | 62 | 56.27 | 1350479 | 1338700 | 51 | 37.59 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3832296.49 | 1732792.31 | 11779 | All three units are on bar as per available hydrology from irrigation department. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-05 | 2025 | 7 | 5 | Pehur HPS | 18 | 9380 | 2 | 93000 | 90000 | 21.22 | 6.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 339030 | 1288314 | 3000 | Plant remained shut down from 2152 hrs dated 04-07-2025 to 1342 hrs dated 05-07-2025, due to nil irrigation demand as per instruction of SDO irrigation. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-05 | 2025 | 7 | 5 | Reshun HPS | 4.2 | 4.11 | 2.45 | 55000 | 54418 | 3.38 | 3.37 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 733554.64 | 625229.36 | 582 | Nil | zafar.src@gmail.com | Original | Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-07-05 | 2025 | 7 | 5 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-06 | 2025 | 7 | 6 | Daral Khwar HPS | 36.6 | 22 | 18.42 | 445110 | 442140 | 28.25 | 7.39 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3655746.16 | 3607128.56 | 2970 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 18.42 MW according to the available hydrology. 2. Due to sudden variation on 132KV supply line the units put on standby for safety. 2. Unit No.02,03 and 01 synchronized at 137Hrs, 1338Hrs and 1343Hrs respectively. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-06 | 2025 | 7 | 6 | Jabori HPS | 10.2 | 4 | 2.8 | 63914 | 61680 | 7.62 | 2.19 | 73 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 352143.46 | 1045468.7 | 2234 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-06 | 2025 | 7 | 6 | Machai HPS | 2.6 | 0.97 | 0.71 | 17284 | 16320 | 29.6 | 17 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 76230.72 | 215239.68 | 964 | Due to the recent heavy rainfall, reduced hydrological discharge was maintained in accordance with the demand of the XEN (Swabi Irrigation Division). | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-06 | 2025 | 7 | 6 | Malakand-3 HPS | 81 | 60 | 54.3 | 1303087 | 1291390 | 51 | 36.62 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3696862.15 | 1868226.65 | 11697 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-06 | 2025 | 7 | 6 | Pehur HPS | 18 | 9.75 | 4.4 | 106400 | 102000 | 21.22 | 7.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 384234 | 1243110 | 4400 | Plant shut down at 1135 hrs due to nil irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-06 | 2025 | 7 | 6 | Reshun HPS | 4.2 | 3.3 | 2.58 | 56000 | 55425 | 3.44 | 4.43 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 747129 | 611655 | 575 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-06 | 2025 | 7 | 6 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-07 | 2025 | 7 | 7 | Daral Khwar HPS | 36.6 | 19 | 18.01 | 434320 | 432140 | 28.25 | 7.23 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3573063.16 | 3689811.56 | 2180 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 18.01 MW according to the available hydrology. 2. At 1059Hrs Plant shutdown as per PESCO NOC for hotspot removal at 132KV line. 3. At 1115 Hrs Unit#2 and Unit#3 synchronized with national grid. 4. 132 KV Supply line failed at 12:15 Hrs and was restored at 12:35 Hrs. 5. Unit No.03 and 02 were synchronised with national grid at 12:50 Hrs, 12:51 Hrs respectively. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-07 | 2025 | 7 | 7 | Jabori HPS | 10.2 | 5.1 | 2.83 | 39621 | 38080 | 7.62 | 2.21 | 73.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 217406.34 | 1180205.82 | 1541 | Plant was precautionary shutdown at 1400 Hrs due to extremely muddy water at weirsite. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-07 | 2025 | 7 | 7 | Machai HPS | 2.6 | 0.62 | 0.11 | 4136 | 3788 | 29.6 | 13 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 17693.75 | 273776.65 | 348 | 1Unit being on bar delivering power to National Grid as per available water inflow and system conditions, precautionary shut down at 0958Hrs Dated 07-07-2025 due to the drop in head race level as water decreased by irrigation department .Call made to Mr. Fazli Wahid (Irrigation Deptt.) for the inquiry of less inflow, As per his response, there was no water demand from the XEN (Swabi Irrigation Division) due to heavy rainfall. Therefore, the water supply for Machai Canal will remain between 300–450 cusecs (13 cumecs) until the next indent, which is insufficient for the smooth operation of the plant. Unit is standby since 0958Hrs Dated 07-07-2025, Due to the recent heavy rainfall, reduced hydrological discharge was maintained in accordance with the demand of the XEN (Swabi Irrigation Division). | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-07 | 2025 | 7 | 7 | Malakand-3 HPS | 81 | 61 | 55.39 | 1329479 | 1317370 | 51 | 37.3 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3771235.1 | 1793853.7 | 12109 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-07 | 2025 | 7 | 7 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 21.22 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down for 24 hours, dated 07-07-2025, due to nil irrigation demand as per the instruction of SDO irrigation. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-07 | 2025 | 7 | 7 | Reshun HPS | 4.2 | 3.43 | 2.06 | 50000 | 49425 | 3.08 | 3.06 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 666249 | 692535 | 575 | Due to accumulation of sand and gravel on the weir flow of water stopped for two hours. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-07 | 2025 | 7 | 7 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-08 | 2025 | 7 | 8 | Daral Khwar HPS | 36.6 | 18.5 | 17.74 | 428190 | 425840 | 28.25 | 7.12 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3520972.87 | 3741901.85 | 2350 | 1. Unit No. 02 and 03 were on bar delivering an average load equal to 17.74 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-08 | 2025 | 7 | 8 | Jabori HPS | 10.2 | 8 | 3.76 | 41932 | 40620 | 7.62 | 2.95 | 98.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 231907.7 | 1165704.46 | 1312 | Plant was synchronized at 1145 Hrs with the national grid after the muddy rainwater from the weir site had subsided. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-08 | 2025 | 7 | 8 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 29.6 | 11 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Unit being on bar delivering power to National Grid as per available water inflow and system conditions, precautionary shut down at 0958Hrs Dated 07-07-2025 due to the drop in head race level as water decreased by irrigation department .Call made to Mr. Fazli Wahid (Irrigation Deptt.) for the inquiry of less inflow, As per his response, there was no water demand from the XEN (Swabi Irrigation Division) due to heavy rainfall. Therefore, the water supply for Machai Canal will remain between 300–400 cusecs (11 cumecs) until the next indent, which is insufficient for the smooth operation of the plant. Unit is standby since 0958Hrs Dated 07-07-2025, Due to the recent heavy rainfall, reduced hydrological discharge was maintained in accordance with the demand of the XEN (Swabi Irrigation Division). | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-07-08 | 2025 | 7 | 8 | Malakand-3 HPS | 81 | 61 | 56.94 | 1366501 | 1354260 | 51 | 38.75 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3876840.1 | 1688248.7 | 12241 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-08 | 2025 | 7 | 8 | Pehur HPS | 18 | 5.97 | 0.7 | 16700 | 14000 | 21 | 21.22 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 52738 | 1574606 | 2700 | Plant remained shutdown since 06-07-2025 due to nil irrigation demand. Unit# 01 was taken on bar at 2104 Hrs with 6.0 MW. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-08 | 2025 | 7 | 8 | Reshun HPS | 4.2 | 3.41 | 2.46 | 54000 | 53399 | 3.31 | 3.3 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 719818.52 | 638965.48 | 601 | Powerhouse tripped 8time due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-08 | 2025 | 7 | 8 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-09 | 2025 | 7 | 9 | Daral Khwar HPS | 36.6 | 20.5 | 17.36 | 416670 | 416670 | 28.25 | 6.97 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3445152.56 | 3817722.16 | 0 | Unit No.02 and 03 were on bar delivering an average load equal to 17.36 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-09 | 2025 | 7 | 9 | Jabori HPS | 10.2 | 5.2 | 3.3 | 41568 | 40400 | 7.62 | 2.61 | 87 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 230651.68 | 1166960.48 | 1168 | Plant was precautionary shutdown at 0525 Hrs due to muddy rainwater and synchronized at 1727 Hrs. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-09 | 2025 | 7 | 9 | Machai HPS | 2.6 | 0.9 | 0.17 | 4180 | 3872 | 29.6 | 15.5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 18086.11 | 273384.29 | 308 | The Unit after all preliminary checks and started at 1835Hrs Dated 09-07-2025 as rated head was restored due to increase in canal discharge as per new indent of Swabi Irrigation Sub Division. Unit kept on FSNL for an half hour to carryout heat run test and finding everything normal then synchronized with the system at 1906Hrs and load gradually increased according to available inflow and system condition. Due to the recent heavy rainfall, reduced hydrological discharge was maintained in accordance with the demand of the XEN (Swabi Irrigation Division). | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-09 | 2025 | 7 | 9 | Malakand-3 HPS | 81 | 65 | 58.01 | 1392213 | 1380920 | 51 | 38.89 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3953159.68 | 1611929.12 | 11293 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-09 | 2025 | 7 | 9 | Pehur HPS | 18 | 5.83 | 0.77 | 18500 | 17000 | 21.22 | 1.13 | 37.67 | 3.767 | 100 | 41 | 432000 | 1627344 | 64039 | 1563305 | 1500 | Plant remained shutdown since 0312 Hrs dated 09-07-2025 due to nil irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-09 | 2025 | 7 | 9 | Reshun HPS | 4.2 | 1.99 | 1.59 | 35000 | 34427 | 2.21 | 2.14 | 71.4 | 13.48 | 73.67 | 45 | 74256 | 1000970.88 | 464075.96 | 536894.92 | 573 | Outgoing feeder Breaker tripped due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-09 | 2025 | 7 | 9 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-10 | 2025 | 7 | 10 | Daral Khwar HPS | 36.6 | 19.5 | 17.35 | 416500 | 416500 | 28.25 | 6.97 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3443746.95 | 3819127.77 | 0 | Unit No.02 and 03 were on bar delivering an average load equal to 17.35 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-10 | 2025 | 7 | 10 | Jabori HPS | 10.2 | 8 | 5 | 120538 | 118610 | 7.62 | 3.93 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 677168.21 | 720443.95 | 1928 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-10 | 2025 | 7 | 10 | Machai HPS | 2.6 | 0.56 | 0.19 | 4332 | 4004 | 29.6 | 15.5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 18702.68 | 272767.72 | 328 | The Unit remained on bar, delivering power to the National Grid as per the available inflow and system conditions. However, due to the recent heavy rainfall, the Irrigation Department maintained reduced hydrological discharge in accordance with the demand of the XEN (Swabi Irrigation Division). | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-10 | 2025 | 7 | 10 | Malakand-3 HPS | 81 | 66 | 60.6 | 1454297 | 1443000 | 51 | 39.86 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4130876.1 | 1434212.7 | 11297 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-10 | 2025 | 7 | 10 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 21.22 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant remained shut down for 24 hours due to nil irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-10 | 2025 | 7 | 10 | Reshun HPS | 4.2 | 2.02 | 1.67 | 36000 | 35410 | 2.21 | 2.2 | 73.43 | 13.48 | 73.8 | 45 | 74390.4 | 1002782.59 | 477326.8 | 525455.79 | 590 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-10 | 2025 | 7 | 10 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-11 | 2025 | 7 | 11 | Daral Khwar HPS | 36.6 | 17.5 | 15.76 | 378300 | 378300 | 28.25 | 6.33 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3127897.89 | 4134976.83 | 0 | 1. Unit No.02 and 03 were on bar delivering an average load equal to 15.76 MW according to the available hydrology. 2. 132KV supply line failed at 11:06 Hrs and was restored at 11:18 Hrs. 3. Unit No.03 and 02 were synchronised with national grid at 11:27 Hrs, 11:33 Hrs respectively. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-11 | 2025 | 7 | 11 | Jabori HPS | 10.2 | 5.8 | 4.52 | 81420 | 80490 | 8.69 | 3.54 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 459533.51 | 938078.65 | 930 | Plant was precautionary shutdown at 1906 Hrs due to extremely muddy water at weirsite. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-11 | 2025 | 7 | 11 | Machai HPS | 2.6 | 0.66 | 0.44 | 10588 | 9900 | 29.6 | 15.5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 46242.9 | 245227.5 | 688 | 1.Unit tripped at 1305Hrs dated 11.07.2025 due to training of 11KV Machai-HPS feeder earth fault. Unit synchronized with the system at 1348Hrs as 11KV Machai-HPS line re-energized at 1310Hrs. 2.Unit precautionary shut down at 1841Hrs dated 11-07-2025 due to less hydrology as water decreased by Irrigation Department for the searching of humam dead body.Unit synchronized with the system at 2314Hrs as rated head was restored. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-11 | 2025 | 7 | 11 | Malakand-3 HPS | 81 | 68 | 53.22 | 1277354 | 1267170 | 51 | 36.18 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3627527.56 | 1937561.24 | 10184 | All units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-11 | 2025 | 7 | 11 | Pehur HPS | 18 | 11.18 | 1.54 | 72000 | 36000 | 21.22 | 3 | 16.67 | 3.767 | 100 | 41 | 432000 | 1627344 | 135612 | 1491732 | 36000 | Unit# 01 and unit#02 taken on bar at 2012 Hrs and 2025 Hrs respectively dated 11-07-25 with load of 11.0 MW as per irrigation demand of 15 cms. | phpcmw18@gmail.com | Original | Units = Net + Aux; Plant factor recalculated | Link_Generation_Data_Summary.xlsx
2025-07-11 | 2025 | 7 | 11 | Reshun HPS | 4.2 | 2.07 | 1.56 | 34000 | 33402 | 2.18 | 2.08 | 69.37 | 13.48 | 72.83 | 45 | 73416 | 989647.68 | 450258.96 | 539388.72 | 598 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-11 | 2025 | 7 | 11 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-12 | 2025 | 7 | 12 | Daral Khwar HPS | 36.6 | 16 | 14.32 | 343780 | 343780 | 28.25 | 5.75 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2842476.17 | 4420398.55 | 0 | Unit No.02 and 03 were on bar delivering an average load equal to 14.32 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-12 | 2025 | 7 | 12 | Jabori HPS | 10.2 | 7 | 5.5 | 66148 | 65830 | 8.69 | 4.32 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 375836.64 | 1021775.52 | 318 | Plant was synchronized at 1152 Hrs after the muddy rainwater had subsided. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-12 | 2025 | 7 | 12 | Machai HPS | 2.6 | 0.69 | 0.51 | 12448 | 11704 | 29.6 | 15.5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 54669.38 | 236801.02 | 744 | 1.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 0128Hrs & 2204Hrs dated 12.07.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault.Unit synchronized with the system at 0246Hrs & 2326Hrs respectively as 11KV Machai-HPS line energized at 0226Hrs & 2217Hrs . 2.Due to the recent heavy rainfall, reduced hydrological discharge was maintained by irrigation Deptt in accordance with the demand of the XEN (Swabi Irrigation Division). | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-12 | 2025 | 7 | 12 | Malakand-3 HPS | 81 | 66 | 60.75 | 1457933 | 1447230 | 51 | 40.49 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4142985.32 | 1422103.48 | 10703 | As per available hydrology from irrigation department all three units at Malakand-III HPC are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-12 | 2025 | 7 | 12 | Pehur HPS | 18 | 11.5 | 11.26 | 270300 | 263000 | 21.22 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 990721 | 636623 | 7300 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-12 | 2025 | 7 | 12 | Reshun HPS | 4.2 | 1.77 | 1.53 | 34000 | 33401 | 2.18 | 2.08 | 100 | 13.48 | 72.73 | 45 | 73315.2 | 988288.9 | 450245.48 | 538043.42 | 599 | Outgoing line feeder tripping due to line faults. | zafar.src@gmail.com | Original | Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-07-12 | 2025 | 7 | 12 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-13 | 2025 | 7 | 13 | Daral Khwar HPS | 36.6 | 36.6 | 16.98 | 407420 | 407420 | 28.25 | 6.81 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3368670.79 | 3894203.93 | 0 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 16.98 MW according to the available hydrology. 2. Unit No.01 was synchronised with the national grid at 21:00 Hrs due to increased hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-13 | 2025 | 7 | 13 | Jabori HPS | 10.2 | 6.5 | 4.2 | 102852 | 102320 | 8.69 | 3.36 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 584165.34 | 813446.82 | 532 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-13 | 2025 | 7 | 13 | Machai HPS | 2.6 | 0.78 | 0.43 | 10836 | 10208 | 29.6 | 16 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 47681.57 | 243788.83 | 628 | 1.Incident Report – Tripping of Unit due earth fault and instantaneous fault, attributed to adverse weather conditions. The unit, which was on bar delivering power to the National Grid as per available water inflow and system conditions, tripped at 1815Hrs on 13-07-2025. The tripping occurred due to a fault on the 11 kV MACHAI-HPS feeder, which experienced an earth fault and instantaneous fault, attributed to heavy windstorm and rainfall. An inquiry call was made to Katlang Grid regarding the tripping and possible restoration of power. As per their response, the line could not be restored as the fault was still persistent. The operation staff of PESCO was immediately informed of the issue. The LS-Operation, PESCO (KATLANG) was contacted and requested to take prompt action to energize the feeder. However, no field team was dispatched by PESCO to clear the Machai-HPS line fault. Consequently, PEDO staff initiated line patrolling to locate and rectify the fault along the 11 kV Machai-HPS feeder. According to field updates, the fault persisted, and rectification was hindered by ongoing adverse weather conditions. The 11 kV Machai-HPS feeder was eventually re-energized at 1458Hrs on 14-07-2025, following fault clearance by PEDO staff, who removed tree branches from various locations along the line. The unit was synchronized with the system at 1532Hrs on 14-07-2025, and load was gradually increased according to the available inflow and prevailing system conditions. 2.Due to recent heavy rainfall, reduced hydrological discharge was maintained by the Irrigation Department, in accordance with the demand of XEN (Swabi Irrigation Division). | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-13 | 2025 | 7 | 13 | Malakand-3 HPS | 81 | 65 | 58.83 | 1411992 | 1400580 | 51 | 39.57 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4009440.37 | 1555648.43 | 11412 | As per available hydrology from irrigation department all units at Malakand-III HPC are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-13 | 2025 | 7 | 13 | Pehur HPS | 18 | 11.46 | 5 | 242300 | 235000 | 21.22 | 16.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 885245 | 742099 | 7300 | Plant shut down at 2208 hrs due to nil irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-13 | 2025 | 7 | 13 | Reshun HPS | 4.2 | 2.07 | 1.37 | 34000 | 33400 | 2.18 | 2.08 | 69.37 | 13.48 | 72.73 | 45 | 73315.2 | 988288.9 | 450232 | 538056.9 | 600 | Outgoing line feeder tripped 9 time due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-13 | 2025 | 7 | 13 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-14 | 2025 | 7 | 14 | Daral Khwar HPS | 36.6 | 36.6 | 25.9 | 621680 | 621680 | 28.25 | 10.4 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 5140236.74 | 2122637.98 | 0 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 25.90 MW according to the available hydrology. 2. Unit No.01 stopped at 1306 Hrs due to less hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-14 | 2025 | 7 | 14 | Jabori HPS | 10.2 | 8.5 | 3.8 | 85190 | 84640 | 8.69 | 3.03 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 483226.69 | 914385.47 | 550 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-14 | 2025 | 7 | 14 | Machai HPS | 2.6 | 1.02 | 0.35 | 7912 | 7436 | 29.6 | 16 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 34733.56 | 256736.84 | 476 | 1.The unit has remained on standby since 1815hrs Dated 13-07-2025 due to a fault on the 11 kV MACHAI-HPS feeder, The 11 kV Machai-HPS feeder was eventually re-energized at 1458Hrs on 14-07-2025, following fault clearance by PEDO staff, who removed tree branches from various locations along the line. The unit was synchronized with the system at 1532Hrs on 14-07-2025, and load was gradually increased according to the available inflow and prevailing system conditions. 2.Due to recent heavy rainfall, reduced hydrological discharge was maintained by the Irrigation Department, in accordance with the demand of XEN (Swabi Irrigation Division). | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-14 | 2025 | 7 | 14 | Malakand-3 HPS | 81 | 66 | 58.93 | 1414417 | 1402860 | 51 | 40.4 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4015967.32 | 1549121.48 | 11557 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-14 | 2025 | 7 | 14 | Pehur HPS | 18 | 11.89 | 5.67 | 136000 | 134000 | 21.22 | 10 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 504778 | 1122566 | 2000 | Generation remained less because of restriction of flow in the canal due to nil irrigation demand. Unit# 01 & 02 were syynchronized at 1157 Hrs & 1207 Hrs respectively on date 14-07-2025 against 15 cms discharge. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-14 | 2025 | 7 | 14 | Reshun HPS | 4.2 | 2.7 | 1.55 | 32000 | 31410 | 1.99 | 1.96 | 65.3 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 423406.8 | 477919.92 | 590 | Tripping due to line faults | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-14 | 2025 | 7 | 14 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-15 | 2025 | 7 | 15 | Daral Khwar HPS | 36.6 | 20.5 | 18.53 | 444660 | 444660 | 28.25 | 7.44 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3676582.28 | 3586292.44 | 0 | Unit No.02 and 03 were on bar delivering an average load equal to 18.53 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-15 | 2025 | 7 | 15 | Jabori HPS | 10.2 | 10.2 | 5.66 | 130374 | 129760 | 8.69 | 4.44 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 740825.79 | 656786.37 | 614 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-15 | 2025 | 7 | 15 | Machai HPS | 2.6 | 1.06 | 0.9 | 22128 | 21076 | 29.6 | 18 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 98446 | 193024.4 | 1052 | 1.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 1350Hrs & 2130Hrs dated 15.07.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault.Unit synchronized with the system at 1358Hrs & 2143Hrs respectively as 11KV Machai-HPS line energized at 1353Hrs & 2135Hrs . 2.Due to recent heavy rainfall, reduced hydrological discharge was maintained by the Irrigation Department, in accordance with the demand of XEN (Swabi Irrigation Division). | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-15 | 2025 | 7 | 15 | Malakand-3 HPS | 81 | 62 | 58.19 | 1396636 | 1385010 | 51 | 39.78 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3964868.13 | 1600220.67 | 11626 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-15 | 2025 | 7 | 15 | Pehur HPS | 18 | 11.88 | 11.35 | 272500 | 265000 | 21.22 | 19 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 998255 | 629089 | 7500 | The plant remained operational as per available head. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-15 | 2025 | 7 | 15 | Reshun HPS | 4.2 | 2.96 | 1.97 | 44000 | 43408 | 2.69 | 2.69 | 89.77 | 13.48 | 89.67 | 45 | 90384 | 1218376.32 | 585139.84 | 633236.48 | 592 | Tripping due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-15 | 2025 | 7 | 15 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | Shutdown Details: Date: May 17, 2025 Time: 9:30 AM Current Status: The powerhouse is currently shut down, resulting in zero generation. Reasons for Shutdown: 1. Flooded Flow: High water flow due to flooding has likely caused operational issues. 2. Annual Maintenance and Repair: Approval for Technical Sanction (TS) is in process for approval of the repair and maintenance work in the runner assemblies. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-16 | 2025 | 7 | 16 | Daral Khwar HPS | 36.6 | 36.6 | 32.15 | 771550 | 771550 | 28.25 | 12.9 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6379406.86 | 883467.86 | 0 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 32.15 MW according to the available hydrology. 2. Unit No.01 synchronized with the national grid at 0441 Hrs due to increased hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-16 | 2025 | 7 | 16 | Jabori HPS | 10.2 | 10.2 | 6.76 | 155656 | 154900 | 8.69 | 5.31 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 884355.08 | 513257.08 | 756 | Trash Rack is heavily choked and its cleaning is not possible due to heavy flow of rain water. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-16 | 2025 | 7 | 16 | Machai HPS | 2.6 | 1.27 | 0.93 | 22780 | 22044 | 29.6 | 18 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 102967.52 | 188502.88 | 736 | 1.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 0004Hrs,0030Hrs & 1946Hrs dated 16.07.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault.Unit synchronized with the system at 0021Hrs,0038Hrs & 2100Hrs respectively as 11KV Machai-HPS line energized at 0017Hrs,0031Hrs & 1947Hrs. 2.The unit, while on bar delivering power to the National Grid as per available water inflow and system conditions, was shut down as a precaution at 2254Hrs on 16-07-2025 due to a drop in the headrace level, caused by reduced water supply from the Irrigation Department. A call was made to Mr. Fazli Wahid (Irrigation Department) to inquire about the decreased inflow. As per his response, there was no water demand from the XEN (Swabi Irrigation Division) due to heavy rainfall. Consequently, the water supply to the Machai Canal has been suspended until the next indent, rendering the inflow insufficient for the smooth operation of the plant. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-16 | 2025 | 7 | 16 | Malakand-3 HPS | 81 | 68 | 60.87 | 1460860 | 1449240 | 51 | 40.93 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4148739.35 | 1416349.45 | 11620 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-16 | 2025 | 7 | 16 | Pehur HPS | 18 | 11.84 | 4.64 | 111300 | 107000 | 21.22 | 8 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 403069 | 1224275 | 4300 | Plant remained shutdown from 0943 Hrs due to nil irrigation demand as per instructions of irrigation SDO. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-16 | 2025 | 7 | 16 | Reshun HPS | 4.2 | 3.08 | 1.83 | 44000 | 43401 | 2.8 | 2.69 | 43.65 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 585045.48 | 683152.92 | 599 | No data submitted for this date | zafar.src@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-07-16 | 2025 | 7 | 16 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The power house is shut down due to flooded conditions and annual maintenance. Note: The repair and maintenance work on the runner assemblies is awaiting Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-17 | 2025 | 7 | 17 | Daral Khwar HPS | 36.6 | 36.6 | 31.66 | 762960 | 759760 | 28.25 | 12.71 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6281923.61 | 980951.11 | 3200 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 31.66 MW according to the available hydrology. 2. Unit No.01 put on stand by at 2102 Hrs due to low hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-17 | 2025 | 7 | 17 | Jabori HPS | 10.2 | 4.5 | 3.08 | 7708 | 7400 | 8.69 | 2.42 | 80.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 42248.08 | 1355364.08 | 308 | Plant was shutdown at 0226 hrs dated 17/07/2025 due to heavily chocked main trash rack. The cleaning of main trash rack is not possible due to higher water flow. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-17 | 2025 | 7 | 17 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 29.6 | 2 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 2254Hrs on 16-07-2025 due to insufficient hydrology. Due to the recent heavy rainfall, reduced hydrological discharge was maintained by irrigation Deptt in accordance with the demand of the XEN (Swabi Irrigation Division). Consequently, the water supply to the Machai Canal has been suspended until the next indent. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-07-17 | 2025 | 7 | 17 | Malakand-3 HPS | 81 | 68 | 60.9 | 1461630 | 1450050 | 51 | 40.89 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4151058.14 | 1414030.66 | 11580 | As per available hydrology from irrigation department all Three Units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-17 | 2025 | 7 | 17 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 21.22 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | Plant shut down since 16-07-2025 due to nil irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-17 | 2025 | 7 | 17 | Reshun HPS | 4.2 | 3.29 | 2.17 | 44000 | 43394 | 2.91 | 2.69 | 89.77 | 13.48 | 97 | 45 | 97776 | 1318020.48 | 584951.12 | 733069.36 | 606 | Lines faults | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-17 | 2025 | 7 | 17 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The power house is shut down due to flooded conditions and annual maintenance. Note: The repair and maintenance work on the runner assemblies is awaiting Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-18 | 2025 | 7 | 18 | Daral Khwar HPS | 36.6 | 26.3 | 23.27 | 560770 | 558370 | 28.25 | 9.34 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 4616770.67 | 2646104.05 | 2400 | Unit No.02 and 03 were on bar delivering an average load equal to 23.27 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-18 | 2025 | 7 | 18 | Jabori HPS | 10.2 | 5.1 | 4 | 45000 | 44490 | 8.69 | 3.2 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 254002.31 | 1143609.85 | 510 | Unit # 02 was synchronized at 1332 Hrs after partial cleaning of main trash rack. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-18 | 2025 | 7 | 18 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 29.6 | 2 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 2254Hrs on 16-07-2025 due to insufficient hydrology. Due to the recent heavy rainfall, reduced hydrological discharge was maintained by irrigation Deptt in accordance with the demand of the XEN (Swabi Irrigation Division). Consequently, the water supply to the Machai Canal has been suspended until the next indent. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-07-18 | 2025 | 7 | 18 | Malakand-3 HPS | 81 | 67 | 58.21 | 1397065 | 1385620 | 51 | 38.48 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3966614.37 | 1598474.43 | 11445 | 132KV lines tripped at 1755Hrs, Supply restored at 1803Hrs, Unit # 01 sync at 1833Hrs, unit # 02 sync at 1834Hrs and unit # 03 sync at 1937Hrs. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-18 | 2025 | 7 | 18 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 21.22 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | Plant shut down since 16-07-2025 due to nil irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-18 | 2025 | 7 | 18 | Reshun HPS | 4.2 | 3.01 | 1.79 | 43000 | 42400 | 2.59 | 2.63 | 42.66 | 13.48 | 86.42 | 45 | 87108 | 1174215.84 | 571552 | 602663.84 | 600 | No data submitted for this date | zafar.src@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-07-18 | 2025 | 7 | 18 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The power house is shut down due to flooded conditions and annual maintenance. Note: The repair and maintenance work on the runner assemblies is awaiting Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-19 | 2025 | 7 | 19 | Daral Khwar HPS | 36.6 | 21.5 | 19.61 | 472640 | 470640 | 28.25 | 7.87 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3891392.71 | 3371482.01 | 2000 | Unit No.02 and 03 were on bar delivering an average load equal to 19.61 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-19 | 2025 | 7 | 19 | Jabori HPS | 10.2 | 10 | 4.98 | 119720 | 118700 | 8.69 | 3.91 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 677682.04 | 719930.12 | 1020 | Unit 01 and 02 was operational as per available hydrology. Unit #01 was synchronized at 1313 Hrs after cleaning of Trash rack. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-19 | 2025 | 7 | 19 | Machai HPS | 2.6 | 0.7 | 0.35 | 8768 | 8228 | 29.6 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 38432.99 | 253037.41 | 540 | The Unit after all preliminary checks and started at 1020Hrs Dated 19-07-2025 as rated head was restored due to increase in canal discharge as per new indent of Swabi Irrigation Sub Division. Unit kept on FSNL for an half hour to carryout heat run test and finding everything normal then synchronized with the system at 1045Hrs and load gradually increased according to available inflow and system condition. Due to recent heavy rainfall, reduced hydrological discharge was maintained by the Irrigation Department, in accordance with the demand of XEN (Swabi Irrigation Division). | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-19 | 2025 | 7 | 19 | Malakand-3 HPS | 81 | 67 | 62.89 | 1509461 | 1497920 | 51 | 40.76 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4288095.58 | 1276993.22 | 11541 | As per available hydrology from irrigation department all three are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-19 | 2025 | 7 | 19 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 21.22 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | Plant remained shutdown since 0943 Hrs dated 16-07-2025, due to nil irrigation demand as per instructions of irrigation SDO. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-19 | 2025 | 7 | 19 | Reshun HPS | 4.2 | 3.34 | 2.16 | 42000 | 41407 | 2.28 | 2.57 | 85.67 | 13.48 | 75.83 | 45 | 76440 | 1030411.2 | 558166.36 | 472244.84 | 593 | Line faults | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-19 | 2025 | 7 | 19 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The power house is shut down due to flooded conditions and annual maintenance. Note: The repair and maintenance work on the runner assemblies is awaiting Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-20 | 2025 | 7 | 20 | Daral Khwar HPS | 36.6 | 18.5 | 17.6 | 424370 | 422370 | 28.25 | 7.06 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3492281.87 | 3770592.85 | 2000 | 1. Unit No.02 and 03 were on bar delivering an average load equal to 17.60 MW according to the available hydrology. 2. 132 KV supply line failed at 17:46 Hrs and was restored at 17:58 Hrs. 3. Unit No.03 and 02 were synchronised with national grid at 18:08 Hrs, 18:13 Hrs respectively. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-20 | 2025 | 7 | 20 | Jabori HPS | 10.2 | 8 | 7.12 | 170980 | 169440 | 8.69 | 5.59 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 967366.85 | 430245.31 | 1540 | Unit#01 and 02 was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-20 | 2025 | 7 | 20 | Machai HPS | 2.6 | 0.6 | 0.43 | 14212 | 13420 | 29.6 | 15.5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 62684.82 | 228785.58 | 792 | 1.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 0743Hrs dated 20.07.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault. Although the 11 kV line was re energized at 0753Hrs, the unit remained shut down/standby and could not synchronize with the system due to high system voltage. The unit finally synchronized with the system at 1132Hrs once the voltage stabilized. 2.Due to recent heavy rainfall, reduced hydrological discharge was maintained by the Irrigation Department, in accordance with the demand of XEN (Swabi Irrigation Division). | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-20 | 2025 | 7 | 20 | Malakand-3 HPS | 81 | 67 | 61.45 | 1474816 | 1463030 | 51 | 40.09 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4188215.98 | 1376872.82 | 11786 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-20 | 2025 | 7 | 20 | Pehur HPS | 18 | 10.62 | 4.9 | 116600 | 113000 | 21.22 | 8 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 425671 | 1201673 | 3600 | Plant remained shutdown since 0943 Hrs dated 16-07-2025, due to nil irrigation demand. Unit# 01 & 02 were taken on bar at 1225 & 1230 Hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-20 | 2025 | 7 | 20 | Reshun HPS | 4.2 | 3.22 | 2.37 | 58000 | 57384 | 3.56 | 3.55 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 773536.32 | 585247.68 | 616 | Tripping due line fault. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-20 | 2025 | 7 | 20 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The power house is shut down due to flooded conditions and annual maintenance. Note: The repair and maintenance work on the runner assemblies is awaiting Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-21 | 2025 | 7 | 21 | Daral Khwar HPS | 36.6 | 25.3 | 18.02 | 434990 | 432590 | 28.25 | 7.23 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3576783.9 | 3686090.82 | 2400 | Unit No.02 and 03 were on bar delivering an average load equal to 18.02 MW according to the available hydrology | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-21 | 2025 | 7 | 21 | Jabori HPS | 10.2 | 10.2 | 6.31 | 151570 | 150220 | 10.32 | 4.95 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 857636.02 | 539976.14 | 1350 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-21 | 2025 | 7 | 21 | Machai HPS | 2.6 | 1.02 | 0.75 | 16836 | 16016 | 29.6 | 16 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 74810.74 | 216659.66 | 820 | 19.2 Incident Report – Tripping of Unit due earth fault and instantaneous fault, attributed to adverse weather conditions. The unit, which was on bar delivering power to the National Grid as per available water inflow and system conditions, tripped at 2206Hrs on 21-07-2025. The tripping occurred due to a fault on the 11 kV MACHAI-HPS feeder, which experienced an earth fault and instantaneous fault, attributed to heavy windstorm and rainfall. An inquiry call was made to Katlang Grid regarding the tripping and possible restoration of power. As per their response, the line could not be restored as the fault was still persistent. The operation staff of PESCO was immediately informed of the issue. The LS-Operation, PESCO (KATLANG) was contacted and requested to take prompt action to energize the feeder. However, no field team was dispatched by PESCO to clear the Machai-HPS line fault. the fault persisted, and rectification was hindered by ongoing adverse weather conditions. The unit has remained on standby since 2206hrs Dated 21-07-2025 due to a fault on the 11 kV MACHAI-HPS feeder. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-21 | 2025 | 7 | 21 | Malakand-3 HPS | 81 | 67 | 60.48 | 1451636 | 1439590 | 51 | 10.72 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4121114.29 | 1443974.51 | 12046 | 132KV lines supply tripped at 2301HRS, restored at 2317HRS. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-21 | 2025 | 7 | 21 | Pehur HPS | 18 | 11.07 | 9.31 | 223600 | 216000 | 21.22 | 16 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 813672 | 813672 | 7600 | At 2200 hrs plant shut down due to nil irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-21 | 2025 | 7 | 21 | Reshun HPS | 4.2 | 3.36 | 2.26 | 52000 | 51390 | 3.32 | 3.18 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 692737.2 | 666046.8 | 610 | Line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-21 | 2025 | 7 | 21 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse has been shut down due to flooded conditions and requires annual mechanical repair & maintenance for further operation of the plant.. Note: The repair and maintenance work on the runner assemblies is awaiting Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-22 | 2025 | 7 | 22 | Daral Khwar HPS | 36.6 | 25.5 | 21.89 | 527680 | 525280 | 28.25 | 8.78 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 4343172.62 | 2919702.1 | 2400 | Unit No.2 and 3 were on bar delivering an average load equal to 21.89 according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-22 | 2025 | 7 | 22 | Jabori HPS | 10.2 | 10 | 6.64 | 159460 | 157840 | 10.32 | 5.21 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 901140.13 | 496472.03 | 1620 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-22 | 2025 | 7 | 22 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 29.6 | 16.67 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 2206hrs Dated 21-07-2025 due to a fault on the 11 kV MACHAI-HPS feeder. Consequently, PEDO staff initiated line patrolling to locate and rectify the fault along the 11 kV Machai-HPS feeder.The 11 kV Machai-HPS feeder was eventually re-energized at 0700Hrs on 22-07-2025, following fault clearance by PEDO staff, who removed tree branches from various locations along the line. Although the 11 kV line was re energized but the unit has remained on standby due to insufficient hydrology, A call was made to Mr. Fazli Wahid (Irrigation Department) to inquire about the decreased inflow. As per his response, there was no water demand from the XEN (Swabi Irrigation Division) due to recent heavy rainfall. Consequently, the water supply to the Machai Canal has been suspended until the next indent, rendering the inflow insufficient for the smooth operation of the plant. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-07-22 | 2025 | 7 | 22 | Malakand-3 HPS | 81 | 53 | 39.64 | 951284 | 941070 | 51 | 27.31 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2694001.09 | 2871087.71 | 10214 | Due to heavy rainfall in the upper Swat region, the Irrigation Department has reduced the water discharge to prevent any potential flood-related incidents so Unit # 01 & 03 desynchronized at 0346HRS and 0708HRS as of less hydrology & kept standby & then Unit # 03 synchronized at 1042HRS & Unit # 01 synchronized at 1506HRS Now As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-22 | 2025 | 7 | 22 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 21.22 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | Plant remained shutdown since 2200 Hrs dated 21-07-2025, due to nil irrigation demand as per instructions of irrigation SDO. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-22 | 2025 | 7 | 22 | Reshun HPS | 4.2 | 3.26 | 2.37 | 51000 | 50430 | 3.14 | 3.12 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 679796.4 | 678987.6 | 570 | Line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-22 | 2025 | 7 | 22 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse has been shut down due to flooded conditions and requires annual mechanical repair & maintenance for further operation of the plant. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-23 | 2025 | 7 | 23 | Daral Khwar HPS | 36.6 | 30.6 | 22.28 | 537070 | 534670 | 28.25 | 8.94 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 4420811.96 | 2842062.76 | 2400 | Unit No.02 and 03 were on bar delivering an average load equal to 22.28 MW according to the available hydrology | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-23 | 2025 | 7 | 23 | Jabori HPS | 10.2 | 10.2 | 8.33 | 200060 | 198010 | 10.32 | 6.54 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 1130478.69 | 267133.47 | 2050 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-23 | 2025 | 7 | 23 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 29.6 | 17.33 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0700Hrs on 22-07-2025 due to insufficient hydrology. Due to the recent heavy rainfall, reduced hydrological discharge was maintained by irrigation Deptt in accordance with the demand of the XEN (Swabi Irrigation Division). Consequently, the water supply to the Machai Canal has been suspended until the next indent. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-07-23 | 2025 | 7 | 23 | Malakand-3 HPS | 81 | 54 | 49.26 | 1182139 | 1171430 | 51 | 33.06 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3353452.66 | 2211636.14 | 10709 | The flow has been reduced by irrigation department due to heavy rain fall in the catchment of upper swat river to avoid any potential plant related incident. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-23 | 2025 | 7 | 23 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 21.22 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | Plant remained shutdown since 2200 Hrs dated 21-07-2025, due to nil irrigation demand as per instructions of irrigation SDO. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-23 | 2025 | 7 | 23 | Reshun HPS | 4.2 | 3.17 | 2.05 | 47000 | 46398 | 2.9 | 2.88 | 95.9 | 13.48 | 96.73 | 45 | 97507.2 | 1314397.06 | 625445.04 | 688952.02 | 602 | Tripping due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-23 | 2025 | 7 | 23 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse has been shut down due to flooded conditions and requires annual mechanical repair & maintenance for further operation of the plant.. Note: The repair and maintenance work on the runner assemblies is awaiting Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-24 | 2025 | 7 | 24 | Daral Khwar HPS | 36.6 | 30.6 | 25.44 | 612550 | 610550 | 28.25 | 10.21 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 5048210.57 | 2214664.15 | 2000 | Unit No.02 and 03 were on bar delivering an average load equal to 25.44 MW according to the available hydrology | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-24 | 2025 | 7 | 24 | Jabori HPS | 10.2 | 10.1 | 7.3 | 175130 | 173180 | 10.32 | 5.72 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 988719.26 | 408892.9 | 1950 | Not reported | 1973akkhan@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-24 | 2025 | 7 | 24 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 29.6 | 18 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0700Hrs on 22-07-2025 due to insufficient hydrology. Due to the recent heavy rainfall, reduced hydrological discharge was maintained by irrigation Deptt in accordance with the demand of the XEN (Swabi Irrigation Division). Consequently, the water supply to the Machai Canal has been suspended until the next indent. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-07-24 | 2025 | 7 | 24 | Malakand-3 HPS | 81 | 63 | 53.34 | 1280233 | 1269150 | 51 | 36.67 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3633195.7 | 1931893.1 | 11083 | The Irrigation Department has reduced the water flow due to heavy rainfall in the catchment area of the Upper Swat River, as the water contains mud and debris which causes choking of trash racks at fore bay and sediment and also to avoid flooding in the downstream area & canals to protect public properties, The inflow will be increased as and when the situation is improved. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-24 | 2025 | 7 | 24 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 21.22 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | Plant remained shutdown since 2200 Hrs dated 21-07-2025, due to nil irrigation demand as per instructions of irrigation SDO. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-24 | 2025 | 7 | 24 | Reshun HPS | 4.2 | 3.04 | 1.89 | 41000 | 40410 | 2.63 | 2.51 | 83.67 | 13.48 | 87.53 | 45 | 88233.6 | 1189388.93 | 544726.8 | 644662.13 | 590 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-24 | 2025 | 7 | 24 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse has been shut down for annual mechanical repair and maintenance, as well as due to flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-25 | 2025 | 7 | 25 | Daral Khwar HPS | 36.6 | 30.6 | 26.14 | 629660 | 627260 | 28.25 | 10.49 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 5186373.86 | 2076500.86 | 2400 | Unit No.2 and 3 were on bar delivering an average load equal to 26.14 according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-25 | 2025 | 7 | 25 | Jabori HPS | 10.2 | 8.9 | 8.17 | 147087 | 145210 | 10.32 | 6.4 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 829032.93 | 568579.23 | 1877 | Plant was shutdown at 1750 Hrs due to flood situation and extremely muddy water at weir site. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-25 | 2025 | 7 | 25 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 29.6 | 18.67 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Preventive Maintenance Observations and Remedial Actions During Water Supply Shutdown Summary: During the monthly preventive maintenance and repair activities on the turbine—carried out in coordination with the shutdown of canal water supply due to recent heavy rainfall—the following critical observations were made: Technical Observations: • The Babbitt metal lining of the shell-type turbine guide bearing exhibited significant corrosion and surface degradation over time. • Continued operation of the turbine in this condition posed a serious risk of damage to the turbine shaft, due to inadequate bearing support and potential misalignment. Remedial Measures Undertaken: In a joint decision by the Deputy Plant Manager (Mechanical)- Malakand-III HPS, the Resident Engineer-Machai HPS, and the Director (O&M)-PEDO, Peshawar, the following corrective actions were approved: • Re-babbitting of the turbine guide bearing to be carried out at a specialized facility in Gujranwala. • Repair of the shaft sleeve at the Malakand-III HPS mechanical workshop. • Comprehensive inspection and repair of all waterway components of the turbine, including seals and associated mechanical assemblies. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load; Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-07-25 | 2025 | 7 | 25 | Malakand-3 HPS | 81 | 64 | 58.03 | 1392671 | 1380870 | 51 | 40.16 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3953016.55 | 1612072.25 | 11801 | All three units are currently on bar as per available hydrology. However, the incoming water is muddy and contains debris and garbage, which is causing frequent choking of the trash racks at the forebay and leading to sediment accumulation. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-25 | 2025 | 7 | 25 | Pehur HPS | 18 | 5.93 | 2.57 | 61900 | 55000 | 21.22 | 4 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 207185 | 1420159 | 6900 | Unit#01 taken on bar dt 25-07-2025 at 1030 hrs as per 05 cms of irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-25 | 2025 | 7 | 25 | Reshun HPS | 4.2 | 3.18 | 2.04 | 46000 | 45360 | 2.89 | 2.82 | 93.87 | 13.48 | 96.33 | 45 | 97104 | 1308961.92 | 611452.8 | 697509.12 | 640 | Tripping due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-25 | 2025 | 7 | 25 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse has been shut down for annual mechanical repair and maintenance, as well as due to flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-26 | 2025 | 7 | 26 | Daral Khwar HPS | 36.6 | 24.8 | 21.93 | 528280 | 526280 | 28.25 | 8.8 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 4351440.92 | 2911433.8 | 2000 | Unit No.2 and 3 were on bar delivering an average load equal to 21.93 according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-26 | 2025 | 7 | 26 | Jabori HPS | 10.2 | 9.3 | 5.9 | 83214 | 81870 | 10.32 | 4.6 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 467412.2 | 930199.96 | 1344 | Plamt was synchronized at 1024 Hrs after muddy rainwater from the weir site had subsided. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-26 | 2025 | 7 | 26 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 29.6 | 19.33 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Preventive Maintenance Observations and Remedial Actions During Water Supply Shutdown Summary: During the monthly preventive maintenance and repair activities on the turbine—carried out in coordination with the shutdown of canal water supply due to recent heavy rainfall—the following critical observations were made: Technical Observations: • The Babbitt metal lining of the shell-type turbine guide bearing exhibited significant corrosion and surface degradation over time. • Continued operation of the turbine in this condition posed a serious risk of damage to the turbine shaft, due to inadequate bearing support and potential misalignment. Remedial Measures Undertaken: In a joint decision by the Deputy Plant Manager (Mechanical)- Malakand-III HPS, the Resident Engineer-Machai HPS, and the Director (O&M)-PEDO, Peshawar, the following corrective actions were approved: • Re-babbitting of the turbine guide bearing to be carried out at a specialized facility in Gujranwala. • Repair of the shaft sleeve at the Malakand-III HPS mechanical workshop. • Comprehensive inspection and repair of all waterway components of the turbine, including seals and associated mechanical assemblies. NOTE: The aforementioned repair and maintenance activities are currently underway, with all tasks being executed as per standard engineering procedures and quality assurance protocols. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load; Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-07-26 | 2025 | 7 | 26 | Malakand-3 HPS | 81 | 64 | 59.11 | 1418708 | 1406460 | 51 | 39.67 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4026273.04 | 1538815.76 | 12248 | All three generating units are currently on bar as per the available hydrology. However, the incoming water is muddy and contains debris and garbage, causing frequent choking of the trash racks at the forebay and leading to deposition of unwanted material, which is affecting the smooth flow conditions. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-26 | 2025 | 7 | 26 | Pehur HPS | 18 | 11.6 | 7.15 | 171700 | 166000 | 21.22 | 12 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 625322 | 1002022 | 5700 | The plant has remained operational for 24 hours with a restriction of flow due to low irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-26 | 2025 | 7 | 26 | Reshun HPS | 4.2 | 3.27 | 2 | 47000 | 46400 | 2.9 | 2.88 | 95.9 | 13.48 | 96.73 | 45 | 97507.2 | 1314397.06 | 625472 | 688925.06 | 600 | Tripping due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-26 | 2025 | 7 | 26 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-27 | 2025 | 7 | 27 | Daral Khwar HPS | 36.6 | 23 | 19.91 | 479800 | 477800 | 28.25 | 7.99 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3950593.74 | 3312280.98 | 2000 | Unit No.02 and 03 were on bar delivering an average load equal to 19.91 MW according to the available hydrology | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-27 | 2025 | 7 | 27 | Jabori HPS | 10.2 | 8.74 | 7.75 | 186126 | 183760 | 10.32 | 6.08 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 1049122.59 | 348489.57 | 2366 | Plant was operational as per available hydrology | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-27 | 2025 | 7 | 27 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 29.6 | 20 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Preventive Maintenance Observations and Remedial Actions During Water Supply Shutdown Summary: During the monthly preventive maintenance and repair activities on the turbine—carried out in coordination with the shutdown of canal water supply due to recent heavy rainfall—the following critical observations were made: Technical Observations: • The Babbitt metal lining of the shell-type turbine guide bearing exhibited significant corrosion and surface degradation over time. • Continued operation of the turbine in this condition posed a serious risk of damage to the turbine shaft, due to inadequate bearing support and potential misalignment. Remedial Measures Undertaken: In a joint decision by the Deputy Plant Manager (Mechanical)- Malakand-III HPS, the Resident Engineer-Machai HPS, and the Director (O&M)-PEDO, Peshawar, the following corrective actions were approved: • Re-babbitting of the turbine guide bearing to be carried out at a specialized facility in Gujranwala. • Repair of the shaft sleeve at the Malakand-III HPS mechanical workshop. • Comprehensive inspection and repair of all waterway components of the turbine, including seals and associated mechanical assemblies. The aforementioned repair and maintenance activities are currently underway, with all tasks being executed as per standard engineering procedures and quality assurance protocols. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-07-27 | 2025 | 7 | 27 | Malakand-3 HPS | 81 | 63 | 58.68 | 1408431 | 1396360 | 51 | 40.26 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3997359.77 | 1567729.03 | 12071 | All three units are currently on bar as per available hydrology. However, the incoming water is muddy and contains debris and garbage, which is causing frequent choking of the trash racks at the forebay and leading to sediment accumulation. Unit # 01 tripped at 0103hrs due to high turbine guide bearing pad temperature & synchronized at 0205hrs. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-27 | 2025 | 7 | 27 | Pehur HPS | 18 | 11.59 | 5.31 | 127500 | 123000 | 21.22 | 9 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 463341 | 1164003 | 4500 | plant remained shutdown from 0855 hrs to 1700 hrs due to drowned person in the canal. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-27 | 2025 | 7 | 27 | Reshun HPS | 4.2 | 2.9 | 2.12 | 42000 | 41390 | 2.78 | 2.57 | 85.67 | 13.48 | 92.5 | 45 | 93240 | 1256875.2 | 557937.2 | 698938 | 610 | Tripping due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-27 | 2025 | 7 | 27 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-28 | 2025 | 7 | 28 | Daral Khwar HPS | 36.6 | 19 | 17.61 | 224670 | 422670 | 28.25 | 7.07 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3494762.36 | 3768112.36 | 198000 | Unit No.02 and 03 were on bar delivering an average load equal to 17.61 MW according to the available hydrology | daralkhwarhpc@gmail.com | Original | CHECK: Net > Units (source me verify karein) | Link_Generation_Data_Summary.xlsx
2025-07-28 | 2025 | 7 | 28 | Jabori HPS | 10.2 | 8.6 | 7.12 | 173269 | 170900 | 10.32 | 5.66 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 975702.28 | 421909.88 | 2369 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-28 | 2025 | 7 | 28 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 29.6 | 19.5 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The aforementioned repair and maintenance activities are currently underway, with all tasks being executed as per standard engineering procedures and quality assurance protocols. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-07-28 | 2025 | 7 | 28 | Malakand-3 HPS | 81 | 64 | 56.84 | 1364230 | 1351840 | 51 | 39.43 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3869912.37 | 1695176.43 | 12390 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-28 | 2025 | 7 | 28 | Pehur HPS | 18 | 10.35 | 6.48 | 155500 | 153000 | 21.22 | 10.6 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 576351 | 1050993 | 2500 | After completing the maintenance work, unit# 01 was taken on bar along with unit# 02 with total load 9.20 MW. Irrigation valve is also open due to high irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-28 | 2025 | 7 | 28 | Reshun HPS | 4.2 | 2.7 | 1.6 | 38500 | 37900 | 2.47 | 2.36 | 38.19 | 13.48 | 82.25 | 45 | 82908 | 1117599.84 | 510892 | 606707.84 | 600 | No data submitted for this date | zafar.src@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-07-28 | 2025 | 7 | 28 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-29 | 2025 | 7 | 29 | Daral Khwar HPS | 36.6 | 18.5 | 16.49 | 398080 | 395680 | 28.25 | 6.62 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3271600.94 | 3991273.78 | 2400 | Unit No.02 and 03 were on bar delivering an average load equal to 16.49 MW according to the available hydrology | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-29 | 2025 | 7 | 29 | Jabori HPS | 10.2 | 8.3 | 6.7 | 165466 | 163110 | 10.32 | 5.4 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 931227.61 | 466384.55 | 2356 | Plant was operational as per available hydrology | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-29 | 2025 | 7 | 29 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 29.6 | 19 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The aforementioned repair and maintenance activities are currently underway, with all tasks being executed as per standard engineering procedures and quality assurance protocols. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-07-29 | 2025 | 7 | 29 | Malakand-3 HPS | 81 | 65 | 58.23 | 1397430 | 1384580 | 51 | 39.3 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3963637.17 | 1601451.63 | 12850 | As per available hydrology from Irrigation Department Three Units at Malakand- III Power House are running. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-29 | 2025 | 7 | 29 | Pehur HPS | 18 | 11.52 | 10.5 | 252200 | 245000 | 21.22 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 922915 | 704429 | 7200 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-29 | 2025 | 7 | 29 | Reshun HPS | 4.2 | 2.2 | 1.52 | 35000 | 34410 | 2.16 | 2.14 | 71.4 | 13.48 | 72 | 45 | 72576 | 978324.48 | 463846.8 | 514477.68 | 590 | Line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-29 | 2025 | 7 | 29 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 3 | 100 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-30 | 2025 | 7 | 30 | Daral Khwar HPS | 36.6 | 30.6 | 21.64 | 521720 | 519320 | 28.25 | 8.68 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 4293893.56 | 2968981.16 | 2400 | Unit No.2 and 3 were on bar delivering an average load equal to 21.64 according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-30 | 2025 | 7 | 30 | Jabori HPS | 10.2 | 9 | 6.9 | 170078 | 167900 | 10.32 | 5.5 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 958574.68 | 439037.48 | 2178 | Plant was on bar as per available hydrology | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-30 | 2025 | 7 | 30 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 29.6 | 18 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The aforementioned repair and maintenance activities are currently underway, with all tasks being executed as per standard engineering procedures and quality assurance protocols. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-07-30 | 2025 | 7 | 30 | Malakand-3 HPS | 81 | 65 | 57.43 | 1378352 | 1366350 | 51 | 39.36 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3911450.14 | 1653638.66 | 12002 | 1. At 2012Hrs dated 30/07/2025 unit No. 01 was shut down on an emergency basis due to a rise in the turbine guide bearing temperature. 2. Two units are currently on bar as per available hydrology. However, the incoming water is muddy and contains debris and garbage, which is causing frequent choking of the trash racks at the forebay and leading to sediment accumulation. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-30 | 2025 | 7 | 30 | Pehur HPS | 18 | 4.17 | 1.16 | 27900 | 25000 | 21.22 | 2 | 66.67 | 3.767 | 100 | 41 | 432000 | 1627344 | 94175 | 1533169 | 2900 | Plant remained shut down from 0025 hrs to 1735 hrs due to nil irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-30 | 2025 | 7 | 30 | Reshun HPS | 4.2 | 2.52 | 1.5 | 36000 | 22952 | 2.22 | 2.2 | 35.71 | 13.48 | 74.11 | 45 | 74704 | 1007009.92 | 309392.96 | 697616.96 | 13048 | No data submitted for this date | zafar.src@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-07-30 | 2025 | 7 | 30 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-31 | 2025 | 7 | 31 | Daral Khwar HPS | 36.6 | 22 | 19.4 | 467530 | 465530 | 28.25 | 7.79 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3849141.7 | 3413733.02 | 2000 | Unit No.02 and 03 were on bar delivering an average load equal to 19.40 MW according to the available hydrology | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-31 | 2025 | 7 | 31 | Jabori HPS | 10.2 | 7.26 | 6.33 | 154165 | 151930 | 10.32 | 5 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 867398.76 | 530213.4 | 2235 | Unit 01 and 02 was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-31 | 2025 | 7 | 31 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 19.6 | 19 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The aforementioned repair and maintenance activities are currently underway, with all tasks being executed as per standard engineering procedures and quality assurance protocols. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-07-31 | 2025 | 7 | 31 | Malakand-3 HPS | 81 | 49 | 47.62 | 1142985 | 1132770 | 51 | 40.15 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3242780.68 | 2322308.12 | 10215 | 1. At 2012Hrs,dated 30/07/2025 unit No. 01 was shut down on an emergency basis due to a rise in the turbine guide bearing temperature. 2. Two units are currently on bar as per available hydrology. However, the incoming water is muddy and contains debris and garbage, which is causing frequent choking of the trash racks at the forebay and leading to sediment accumulation. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-31 | 2025 | 7 | 31 | Pehur HPS | 18 | 5.3 | 4.44 | 106600 | 104000 | 21.22 | 6.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 391768 | 1235576 | 2600 | Generation is less because only 1 unit on bar with restricted flow as per irrigation official. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-07-31 | 2025 | 7 | 31 | Reshun HPS | 4.2 | 2.59 | 1.54 | 37000 | 11495 | 2.29 | 2.26 | 36.71 | 13.48 | 76.22 | 45 | 76832 | 1035695.36 | 154952.6 | 880742.76 | 25505 | No data submitted for this date | zafar.src@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-07-31 | 2025 | 7 | 31 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-01 | 2025 | 8 | 1 | Daral Khwar HPS | 36.6 | 18 | 16.53 | 399580 | 396780 | 15.6 | 6.64 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3280696.07 | 3982178.65 | 2800 | Unit No.02 and 03 were on bar delivering an average load equal to 16.53 MW according to the available hydrology | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-01 | 2025 | 8 | 1 | Jabori HPS | 10.2 | 7.9 | 5.64 | 137530 | 135270 | 9.93 | 4.49 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 772283.48 | 625328.68 | 2260 | Plant was operational as per available. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-01 | 2025 | 8 | 1 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 25.3 | 19 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The aforementioned repair and maintenance activities are currently underway, with all tasks being executed as per standard engineering procedures and quality assurance protocols. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-08-01 | 2025 | 8 | 1 | Malakand-3 HPS | 81 | 49 | 47.52 | 1140589 | 1129980 | 51 | 40.21 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3234793.75 | 2330295.05 | 10609 | 1. At 2012Hrs,dated 30/07/2025 unit No. 01 was shut down on an emergency basis due to a rise in the turbine guide bearing temperature. 2. Two units are currently on bar as per available hydrology. However, the incoming water is muddy and contains debris and garbage, which is causing frequent choking of the trash racks at the forebay and leading to sediment accumulation. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-01 | 2025 | 8 | 1 | Pehur HPS | 18 | 11.35 | 8.44 | 202500 | 198000 | 18.39 | 13 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 745866 | 881478 | 4500 | Unit# 01 was taken on bar at 1015 Hrs with 5.40 MW along with unit# 02. Irrigation valve is also open due to high irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-01 | 2025 | 8 | 1 | Reshun HPS | 4.2 | 2.1 | 1.61 | 38000 | 37 | 2.35 | 2.33 | 77.53 | 13.48 | 78.33 | 45 | 78960 | 1064380.8 | 504.57 | 1063876.23 | 37962.57 | Nil. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-01 | 2025 | 8 | 1 | Shishi HPS | 1.8 | 0 | 24 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-02 | 2025 | 8 | 2 | Daral Khwar HPS | 36.6 | 15.5 | 15.27 | 368010 | 366410 | 15.6 | 6.13 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3029587.8 | 4233286.92 | 1600 | Unit No.2 and 3 were on bar delivering an average load equal to 15.27 according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-02 | 2025 | 8 | 2 | Jabori HPS | 10.2 | 9.5 | 6.6 | 160411 | 158150 | 9.93 | 5.2 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 902909.98 | 494702.18 | 2261 | Not reported | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-02 | 2025 | 8 | 2 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 25.3 | 21 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The reinstallation and assembly of repaired components is currently in progress, being carried out under the supervision of qualified technical staff. All works are proceeding in accordance with approved engineering procedures, alignment protocols, and quality control standards to ensure the unit’s safe return to service. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-08-02 | 2025 | 8 | 2 | Malakand-3 HPS | 81 | 64 | 57.26 | 1374245 | 1362890 | 51 | 39.29 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3901545.2 | 1663543.6 | 11355 | Units 02 and 03 remained on bar as per available hydrology, while Unit 01 was synchronized with the system at 01:54 hrs dated 02-08-2025 after completion of the following repair works: 1. Replaced the rotating piece with a repaired spare one. 2. Repaired the headcover chamber through welding. 3. Replaced damaged pads with spares one | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-02 | 2025 | 8 | 2 | Pehur HPS | 18 | 12.4 | 11.77 | 282400 | 274000 | 18.39 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1032158 | 595186 | 8400 | Plant remained operational through out 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-02 | 2025 | 8 | 2 | Reshun HPS | 4.2 | 1.97 | 1.54 | 36000 | 35428 | 2.24 | 2.2 | 73.43 | 13.48 | 74.67 | 45 | 75264 | 1014558.72 | 477569.44 | 536989.28 | 572 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-02 | 2025 | 8 | 2 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-03 | 2025 | 8 | 3 | Daral Khwar HPS | 36.6 | 14.5 | 14.05 | 339270 | 337270 | 15.6 | 5.64 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2788649.54 | 4474225.18 | 2000 | Unit No.02 and 03 were on bar delivering an average load equal to 14.05 MW according to the available hydrology | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-03 | 2025 | 8 | 3 | Jabori HPS | 10.2 | 7.58 | 5.52 | 135360 | 133000 | 9.93 | 4.42 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 759323.6 | 638288.56 | 2360 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-08-03 | 2025 | 8 | 3 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 25.3 | 22 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The reinstallation and assembly of repaired components is currently in progress, being carried out . All works are proceeding in accordance with approved engineering procedures, alignment protocols, and quality control standards to ensure the unit’s safe return to service. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-08-03 | 2025 | 8 | 3 | Malakand-3 HPS | 81 | 64 | 54.12 | 1298809 | 1288400 | 51 | 39.65 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3688302.68 | 1876786.12 | 10409 | Units #01, 02, and 03 tripped at 03:24 hrs on 03-08-2025 due to a failure in the 132 kV line supply. After restoration of 132kv supply at 03:34 hrs, Units #01, 02, and 03 were synchronized with the system at 04:02 hrs, 04:04 hrs, and 04:22 hrs, respectively. Subsequently, Unit #03 was desynchronized at 07:47 hrs due to vibrations observed at the lower portion of the draft tube cone. The unit was re-synchronized at 12:26 hrs the same day after maintenance activities, including tightening of draft tube bolts, replacement of one slip bolt with a spare, welding of broken bolts, and inspection and tightening of the middle and upper cone bolts. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-03 | 2025 | 8 | 3 | Pehur HPS | 18 | 12.08 | 11.72 | 11 | 274000 | 18.39 | 18.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1032158 | 595186 | 273988.69 | The plant has remained operational for 24 hours as per available hydrology. | phpcmw18@gmail.com | Original | CHECK: Net > Units (source me verify karein) | Link_Generation_Data_Summary.xlsx
2025-08-03 | 2025 | 8 | 3 | Reshun HPS | 4.2 | 1.96 | 1.47 | 33000 | 32431 | 2.11 | 2.02 | 67.33 | 13.48 | 70.33 | 45 | 70896 | 955678.08 | 437169.88 | 518508.2 | 569 | Powerhouse tripped 8times due to the line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-03 | 2025 | 8 | 3 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-04 | 2025 | 8 | 4 | Daral Khwar HPS | 36.6 | 14 | 13.45 | 325240 | 322840 | 15.6 | 5.4 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2669337.97 | 4593536.75 | 2400 | 1. Unit No.02 & 03 were on bar delivering an average load equal to 13.45 MW according to the available hydrology. 2. Unit No.02 stopped at 13:10 Hrs due to low hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-04 | 2025 | 8 | 4 | Jabori HPS | 10.2 | 7 | 5.07 | 121630 | 119280 | 9.93 | 3.97 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 680993.38 | 716618.78 | 2350 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-04 | 2025 | 8 | 4 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 25.3 | 22 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The reinstallation and assembly of repaired components is currently in progress, being carried out . All works are proceeding in accordance with approved engineering procedures, alignment protocols, and quality control standards to ensure the unit’s safe return to service. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-08-04 | 2025 | 8 | 4 | Malakand-3 HPS | 81 | 61 | 53.29 | 1278882 | 1267670 | 51 | 38.15 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3628958.91 | 1936129.89 | 11212 | All three units were on bar as per available hydrology from the Irrigation Department. However, due to vibration observed in Unit #03, the unit was desynchronized at 09:23 hrs for maintenance. Activities carried out included tightening of draft tube cone bolts, welding of angle iron supports on five sides of the lower cone, and strengthening of the upper and middle cones through support welds. After completion, the unit was re-synchronized at 17:10 hrs. Vibration was significantly reduced post-maintenance. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-04 | 2025 | 8 | 4 | Pehur HPS | 18 | 12.5 | 10.46 | 251200 | 244000 | 18.39 | 17 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 919148 | 708196 | 7200 | Generation is less because plant remained shutdown from 1740 Hrs to 2013 Hrs dt. 04-08-25 due to emergency PTW to rectify fault occured on 11kv STFA feeder crossing beneath the T/line on the request of SE (operation) pesco swabi circle in correspondence with RCC. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-04 | 2025 | 8 | 4 | Reshun HPS | 4.2 | 2.92 | 1.74 | 41667 | 41097 | 2.62 | 2.55 | 41.34 | 13.48 | 80.22 | 45 | 80864 | 1090046.72 | 553987.56 | 536059.16 | 570 | No data submitted for this date | zafar.src@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-08-04 | 2025 | 8 | 4 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-05 | 2025 | 8 | 5 | Daral Khwar HPS | 36.6 | 13.5 | 12.99 | 314090 | 311690 | 15.6 | 5.21 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2577146.43 | 4685728.29 | 2400 | Unit No. 03 was on bar delivering an average load equal to 12.99 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-05 | 2025 | 8 | 5 | Jabori HPS | 10.2 | 6.7 | 4.97 | 119245 | 116830 | 9.93 | 3.89 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 667005.84 | 730606.32 | 2415 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-05 | 2025 | 8 | 5 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 25.3 | 22 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The reinstallation and assembly of repaired components is currently in progress, being carried . All works are proceeding in accordance with approved engineering procedures, alignment protocols, and quality control standards to ensure the unit’s safe return to service. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-08-05 | 2025 | 8 | 5 | Malakand-3 HPS | 81 | 61 | 53.88 | 1293140 | 1281510 | 51 | 37.28 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3668578.68 | 1896510.12 | 11630 | Units #01, #02, and #03 tripped at 14:16 hrs due to tripping of the 132 kV supply. After restoration of supply at 14:24 hrs, Units #01, #02, and #03 were synchronized with the system at 14:43 hrs, 14:51 hrs, and 15:08 hrs, respectively. All units are currently on bar as per available hydrology from the Irrigation Department. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-05 | 2025 | 8 | 5 | Pehur HPS | 18 | 11.95 | 11.76 | 282400 | 275000 | 18.39 | 18.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1035925 | 591419 | 7400 | The plant has remained operational as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-05 | 2025 | 8 | 5 | Reshun HPS | 4.2 | 3.53 | 2.1 | 50333 | 49763 | 3.12 | 3.08 | 49.93 | 13.48 | 90.11 | 45 | 90832 | 1224415.36 | 670805.24 | 553610.12 | 570 | No data submitted for this date | zafar.src@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-08-05 | 2025 | 8 | 5 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-06 | 2025 | 8 | 6 | Daral Khwar HPS | 36.6 | 15.3 | 13.81 | 333860 | 331460 | 15.6 | 5.54 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2740610.72 | 4522264 | 2400 | Unit No. 03 were on bar delivering an average load equal to 13.81 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-06 | 2025 | 8 | 6 | Jabori HPS | 10.2 | 9 | 5.72 | 137230 | 134830 | 9.93 | 4.48 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 769771.44 | 627840.72 | 2400 | Not reported | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-06 | 2025 | 8 | 6 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 25.3 | 22 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The reinstallation and assembly of repaired components is currently in progress, being carried . All works are proceeding in accordance with approved engineering procedures, alignment protocols, and quality control standards to ensure the unit’s safe return to service. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-08-06 | 2025 | 8 | 6 | Malakand-3 HPS | 81 | 63 | 53.81 | 1291363 | 1279520 | 51 | 36.18 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3662881.9 | 1902206.9 | 11843 | Unit #01 was desynchronized from the system at 22:43 hrs on 06-08-2025 due to water leakage observed at the coupling of the turbine guide bearing, which is part of the closed-loop cooling water system. After completion of maintenance work, the unit was re-synchronized with the system at 03:44 hrs on 07-08-2025. All units are currently on bar as per available hydrology from the Irrigation Department. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-06 | 2025 | 8 | 6 | Pehur HPS | 18 | 11.83 | 11.09 | 266100 | 258000 | 18.39 | 17 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 971886 | 655458 | 8100 | Plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-06 | 2025 | 8 | 6 | Reshun HPS | 4.2 | 3.14 | 2.43 | 59000 | 58429 | 3.62 | 3.61 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 787622.92 | 571161.08 | 571 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-06 | 2025 | 8 | 6 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-07 | 2025 | 8 | 7 | Daral Khwar HPS | 36.6 | 15.3 | 13.11 | 317150 | 314750 | 15.6 | 5.26 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2602447.42 | 4660427.3 | 2400 | Unit No.03 were on bar delivering an average load equal to 13.11 MW according to the available hydrology | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-07 | 2025 | 8 | 7 | Jabori HPS | 10.2 | 7.5 | 1.46 | 35121 | 34110 | 9.93 | 1.15 | 38.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 194740.81 | 1202871.35 | 1011 | Plant was shutdown at 2345 Hrs dated 06-08-2025 due to extremely muddy water at weirsite. Plant remained shutdown till 1846 Hrs (07-08-2025) for repair work of intake and gravel trap gate at weir site by EPC Contractor. Unit 01 and 02 wa synchronized with national grid at 1846 Hrs and 1857 Hrs respectively. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-07 | 2025 | 8 | 7 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 25.3 | 22 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The reinstallation and assembly of repaired components is currently in progress, being carried . All works are proceeding in accordance with approved engineering procedures, alignment protocols, and quality control standards to ensure the unit’s safe return to service. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-08-07 | 2025 | 8 | 7 | Malakand-3 HPS | 81 | 63 | 47.23 | 1133489 | 1122800 | 51 | 33.24 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3214239.56 | 2350849.24 | 10689 | Unit # 01, 02 & 03 desynchronized from the system at 19:35Hrs, 20:08Hrs & 19:51Hrs respectively due to water diversion by the Irrigation Department to facilitate searching of a dead body Unit # 01, 02 & 03 synchronized with the system at 22:34Hrs, 23:19Hrs & 23:29Hrs respectively. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-07 | 2025 | 8 | 7 | Pehur HPS | 18 | 10.68 | 4.7 | 112900 | 112000 | 18.39 | 7 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 421904 | 1205440 | 900 | The plant has remained shut down since 11:05 hours due to nil irrigation demand because of heavy rainfall downstream. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-07 | 2025 | 8 | 7 | Reshun HPS | 4.2 | 3.96 | 2.35 | 56500 | 55930 | 3.47 | 3.46 | 56.05 | 13.48 | 100 | 45 | 100800 | 1358784 | 753936.4 | 604847.6 | 570 | No data submitted for this date | zafar.src@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-08-07 | 2025 | 8 | 7 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-08 | 2025 | 8 | 8 | Daral Khwar HPS | 36.6 | 15.3 | 12.7 | 307080 | 304680 | 15.6 | 5.1 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2519185.64 | 4743689.08 | 2400 | Unit No.03 were on bar delivering an average load equal to 12.70 MW according to the available hydrology | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-08 | 2025 | 8 | 8 | Jabori HPS | 10.2 | 6 | 4.54 | 109100 | 107400 | 9.93 | 3.56 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 613168.08 | 784444.08 | 1700 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-08 | 2025 | 8 | 8 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 25.3 | 22 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The aforementioned repair and maintenance activities are currently underway, with all tasks being executed as per standard engineering procedures and quality assurance protocols. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-08-08 | 2025 | 8 | 8 | Malakand-3 HPS | 81 | 64 | 46.83 | 1123905 | 1112790 | 51 | 36.48 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3185583.93 | 2379504.87 | 11115 | Heavy water leakage observed from the connecting pipe joint between turbine guide bearing cooler of unit # 01 and closed loop cooling water system. Unit # 01 shutdown under emergency at 0143 Hrs. date 8-08-2025 in order to avoid any damage to turbine bearing of Unit # 01 due to decrease of water flow of closed loop system. After thoroughly inspection/checking no water leakage observed from closed loop system. Therefore Unit # 01 synchronized with system 18:13 Hrs. on date: 08-08-2025 however the decreasing water flow in closed loop system is still monitoring. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-08 | 2025 | 8 | 8 | Pehur HPS | 18 | 5.1 | 1.94 | 46700 | 45000 | 18.39 | 3 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 169515 | 1457829 | 1700 | Plant remained shutdown for 1410 hrs due to nill irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-08 | 2025 | 8 | 8 | Reshun HPS | 4.2 | 3.51 | 2.44 | 54000 | 53430 | 3.31 | 3.3 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 720236.4 | 638547.6 | 570 | Tripping due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-08 | 2025 | 8 | 8 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-09 | 2025 | 8 | 9 | Daral Khwar HPS | 36.6 | 15.3 | 12.51 | 302680 | 300280 | 15.6 | 5.02 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2482805.12 | 4780069.6 | 2400 | Unit No.03 was on bar delivering an average load equal to 12.51 according to available hydrology | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-09 | 2025 | 8 | 9 | Jabori HPS | 10.2 | 6.7 | 4.62 | 110960 | 109320 | 9.93 | 3.63 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 624129.74 | 773482.42 | 1640 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-09 | 2025 | 8 | 9 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 25.3 | 22 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The aforementioned repair and maintenance activities are currently underway, with all tasks being executed as per standard engineering procedures and quality assurance protocols. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-08-09 | 2025 | 8 | 9 | Malakand-3 HPS | 81 | 63 | 54.35 | 1304332 | 1292950 | 51 | 36.3 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3701327.96 | 1863760.84 | 11382 | Units are running as per available hydrology; however, the trend of water flow is decreasing, as per information from the Irrigation Department. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-09 | 2025 | 8 | 9 | Pehur HPS | 18 | 11.93 | 5.9 | 141500 | 136000 | 18.39 | 9.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 512312 | 1115032 | 5500 | Unit# 01 remained off the bar for 2030 Hrs while unit# 02 remained on bar with 5.0 MW because of restriction of flow in canal due to low irrigation demand. Unit# 01 was taken on bar at 2030 Hrs along with unit# 02 with full load. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-09 | 2025 | 8 | 9 | Reshun HPS | 4.2 | 3.19 | 2.31 | 50000 | 49390 | 3.08 | 3.06 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 665777.2 | 693006.8 | 610 | Line fault | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-09 | 2025 | 8 | 9 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-10 | 2025 | 8 | 10 | Daral Khwar HPS | 36.6 | 14.2 | 12.4 | 299970 | 297570 | 15.6 | 4.98 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2460398.03 | 4802476.69 | 2400 | Unit No.03 were on bar delivering an average load equal to 12.40 MW according to the available hydrology | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-10 | 2025 | 8 | 10 | Jabori HPS | 10.2 | 5.2 | 4.88 | 117340 | 115590 | 9.93 | 3.83 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 659926.43 | 737685.73 | 1750 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-10 | 2025 | 8 | 10 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 25.3 | 22 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The aforementioned repair and maintenance activities are currently underway, with all tasks being executed as per standard engineering procedures and quality assurance protocols. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-08-10 | 2025 | 8 | 10 | Malakand-3 HPS | 81 | 59 | 53.35 | 1280385 | 1269200 | 51 | 35.61 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3633338.84 | 1931749.96 | 11185 | All Three Units are running As per available hydrology ,however the trend of water flow is decreasing ,as per information from irrigation department. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-10 | 2025 | 8 | 10 | Pehur HPS | 18 | 11.91 | 11.81 | 283500 | 276000 | 18.39 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1039692 | 587652 | 7500 | Plant operational 24 hrs | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-10 | 2025 | 8 | 10 | Reshun HPS | 4.2 | 3.75 | 2.23 | 53500 | 52888 | 3.28 | 3.28 | 53.08 | 13.48 | 100 | 45 | 100800 | 1358784 | 712930.24 | 645853.76 | 612 | No data submitted for this date | zafar.src@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-08-10 | 2025 | 8 | 10 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-11 | 2025 | 8 | 11 | Daral Khwar HPS | 36.6 | 12 | 11.66 | 282170 | 279770 | 15.6 | 4.68 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2313222.29 | 4949652.43 | 2400 | Unit No.03 were on bar delivering an average load equal to 11.66 MW according to the available hydrology | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-11 | 2025 | 8 | 11 | Jabori HPS | 10.2 | 5.1 | 4.7 | 91720 | 90120 | 9.43 | 2.99 | 99.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 514513.1 | 883099.06 | 1600 | Plant was shutdown at 1502 Hrs for welding steel rods pieces at end of cooling water suction line to prevent entrance of debris/floating material inside cooling water line. Unit # 01 was synchronized with National grid at 1941 Hrs. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-08-11 | 2025 | 8 | 11 | Koto HPS | 40.8 | 13.5 | 12.9 | 310250 | 307800 | 65.85 | 34.07 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 2536272 | 5532336 | 2450 | Plant was operational on average load of 12.9 MW as per available hydrology | luqmanln@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-11 | 2025 | 8 | 11 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 25.3 | 21 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The maintenance team from Malakand-III HPS, mobilized to carry out repair and maintenance activities, is currently on-site. All tasks are being executed in accordance with standard engineering procedures and quality assurance protocols. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-08-11 | 2025 | 8 | 11 | Malakand-3 HPS | 81 | 57 | 51.95 | 1246712 | 1234570 | 51 | 34.49 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3534203.54 | 2030885.26 | 12142 | All three Units are running as per available hydrology; however, the trend of water flow is decreasing, as per information from the Irrigation Department. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-11 | 2025 | 8 | 11 | Pehur HPS | 18 | 11.96 | 11.82 | 283600 | 276000 | 18.39 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1039692 | 587652 | 7600 | Plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-11 | 2025 | 8 | 11 | Reshun HPS | 4.2 | 3.28 | 2.46 | 57000 | 56385 | 3.5 | 3.49 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 760069.8 | 598714.2 | 615 | Line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-11 | 2025 | 8 | 11 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-12 | 2025 | 8 | 12 | Daral Khwar HPS | 36.6 | 12.4 | 11.54 | 279410 | 277010 | 15.6 | 4.63 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2290401.78 | 4972472.94 | 2400 | Unit No. 03 was on bar delivering an average load equal to 11.54 according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-12 | 2025 | 8 | 12 | Jabori HPS | 10.2 | 5 | 4.68 | 112490 | 110770 | 8.94 | 3.67 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 632408.08 | 765204.08 | 1720 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-12 | 2025 | 8 | 12 | Koto HPS | 40.8 | 13.67 | 11.88 | 287500 | 285120 | 65.85 | 32.7 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 2349388.8 | 5719219.2 | 2380 | Plant was operational on average load of 11.8 MW as per available hydrolog | luqmanln@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-12 | 2025 | 8 | 12 | Machai HPS | 2.6 | 0.97 | 25.3 | 2216 | 2068 | 25.3 | 16 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 9659.63 | 281810.77 | 148 | Following the completion of all preliminary checks, the Unit was gradually brought to variable speed (“creep mode”) at 1900 Hrs on 12-08-2025 to conduct a mechanical run test. Upon satisfactory inspection during variable speed operation, the Unit was transitioned to Full Speed No Load (FSNL) and maintained in this state for approximately one hour to execute a heat run test and perform detailed mechanical observations. All operational parameters remained within prescribed limits. At 2000Hrs, the Unit was successfully synchronized with the grid, and load was incrementally increased to in accordance with prevailing system demand and operating conditions. The Unit’s performance during the test was observed to be normal and satisfactory | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-12 | 2025 | 8 | 12 | Malakand-3 HPS | 81 | 63 | 55.31 | 1327358 | 1314710 | 51 | 35.95 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3763620.32 | 1801468.48 | 12648 | All three Units are running as per available hydrology; however, the trend of water flow is decreasing, as per information from the Irrigation Department. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-12 | 2025 | 8 | 12 | Pehur HPS | 18 | 11.91 | 11.82 | 283700 | 273000 | 18.39 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1028391 | 598953 | 10700 | Plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-12 | 2025 | 8 | 12 | Reshun HPS | 4.2 | 3.24 | 2.51 | 55000 | 54402 | 3.38 | 3.37 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 733338.96 | 625445.04 | 598 | Powerhouse tripped 6time due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-12 | 2025 | 8 | 12 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-13 | 2025 | 8 | 13 | Daral Khwar HPS | 36.6 | 13 | 12.29 | 297390 | 294990 | 15.6 | 4.93 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2439065.82 | 4823808.9 | 2400 | Unit No.03 were on bar delivering an average load equal to 12.29 MW according to the available hydrology | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-13 | 2025 | 8 | 13 | Jabori HPS | 10.2 | 5.3 | 4.82 | 113300 | 111650 | 8.93 | 3.7 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 637432.18 | 760179.98 | 1650 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-08-13 | 2025 | 8 | 13 | Koto HPS | 40.8 | 13.63 | 11.32 | 271750 | 270360 | 65.85 | 32.23 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 2227766.4 | 5840841.6 | 1390 | Plant was operational on average load of 11.32 MW as per available hydrology | luqmanln@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-13 | 2025 | 8 | 13 | Machai HPS | 2.6 | 1.03 | 0.93 | 22680 | 21428 | 25.3 | 16 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 100090.19 | 191380.21 | 1252 | The unit remained on bar, delivering power to the National Grid as per the available water inflow and system conditions. However, the Irrigation Department maintained reduced hydrological discharge in accordance with the demand of the XEN (Swabi Irrigation Division). | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-13 | 2025 | 8 | 13 | Malakand-3 HPS | 81 | 63 | 58.55 | 1405245 | 1393880 | 51 | 38.4 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3990260.28 | 1574828.52 | 11365 | All three Units are running as per available hydrology; however, the trend of water flow is decreasing, as per information from the Irrigation Department. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-13 | 2025 | 8 | 13 | Pehur HPS | 18 | 11.9 | 11.84 | 284200 | 276000 | 18.39 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1039692 | 587652 | 8200 | Plant remained operational through out 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-13 | 2025 | 8 | 13 | Reshun HPS | 4.2 | 3.57 | 2.12 | 51000 | 50398 | 3.16 | 3.12 | 50.6 | 13.48 | 97.11 | 45 | 97888 | 1319530.24 | 679365.04 | 640165.2 | 602 | No data submitted for this date | zafar.src@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-08-13 | 2025 | 8 | 13 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-14 | 2025 | 8 | 14 | Daral Khwar HPS | 36.6 | 36.6 | 18.98 | 458250 | 455450 | 15.6 | 7.62 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3765797.24 | 3497077.48 | 2800 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 18.98 MW according to the available hydrology. 2. Complex shutdown due to severe flood and choking inlet trash racks as well as in the sand trap at 09:29 Hrs. 3. Complete flushing of gravel trap, sand trap, cleaning of all trash racks, ensuring clear catchment and cleaning of cooling water system carried out. 4. Unit No.02, 03 and 01 were synchronised with national grid at 17:04 Hrs, 17:10 Hrs and 17:15 Hrs respectively. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-14 | 2025 | 8 | 14 | Jabori HPS | 10.2 | 5.3 | 5.3 | 26723 | 26020 | 8.92 | 4.19 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 148553.38 | 1249058.78 | 703 | Plant was shutdown and intake gates were closed at 0512 Hrs dated 14-08-2025 due to flood in Siren river. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-14 | 2025 | 8 | 14 | Koto HPS | 40.8 | 13.7 | 13.22 | 313250 | 311760 | 65.8 | 33.89 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 2568902.4 | 5499705.6 | 1490 | Unit No. 02 was on bar delivering an average load equal to 13.22 according to available hydrology. | luqmanln@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-14 | 2025 | 8 | 14 | Machai HPS | 2.6 | 0.93 | 0.87 | 21216 | 20284 | 25.3 | 16 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 94746.56 | 196723.84 | 932 | The unit remained on bar, delivering power to the National Grid as per the available water inflow and system conditions. However, the Irrigation Department maintained reduced hydrological discharge in accordance with the demand of the XEN (Swabi Irrigation Division). | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-14 | 2025 | 8 | 14 | Malakand-3 HPS | 81 | 67 | 61.6 | 1478428 | 1467810 | 51 | 40.71 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 4201899.69 | 1363189.11 | 10618 | The Units are running as per available hydrology; however due to heavy rain in the catchment area of river swat the water are muddy and carrying heavy trashes. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-14 | 2025 | 8 | 14 | Pehur HPS | 18 | 11.96 | 11.81 | 283400 | 276000 | 18.39 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1039692 | 587652 | 7400 | Plant remained operational through out 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-14 | 2025 | 8 | 14 | Reshun HPS | 4.2 | 3.29 | 1.96 | 47000 | 46394 | 2.95 | 2.88 | 46.63 | 13.48 | 94.22 | 45 | 94976 | 1280276.48 | 625391.12 | 654885.36 | 606 | No data submitted for this date | zafar.src@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-08-14 | 2025 | 8 | 14 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-15 | 2025 | 8 | 15 | Daral Khwar HPS | 36.6 | 36.6 | 34.5 | 831220 | 828020 | 15.6 | 13.85 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6846317.77 | 416556.95 | 3200 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 34.50 MW according to the available hydrology. 2. Plant was shutdown due to debris accumulation at intake (water way) at 2305 Hrs, resulting in flow diversion over weir hump gradual reduction in load and head variation on units. 3. Complete flushing of intake and gravel channel was subsequently performed. 4. Unit No.03, 01 and 02 were synchronised with national grid at 00:54 Hrs, 01:05 Hrs and 01:10 Hrs respectively. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-15 | 2025 | 8 | 15 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 8.02 | 2.1 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | Plant was shutdown at 0512 Hrs dated 14-08-2025 due to flood. | faizanbabar5@gmail.com | Original | Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-08-15 | 2025 | 8 | 15 | Koto HPS | 40.8 | 13.7 | 5.77 | 132750 | 131197 | 65.8 | 35 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1081063.28 | 6987544.72 | 1553 | The plant was shut down on 15-8-2025 10.30 AM due to heavy flood in punjkora river that choke the intake trash rack. | luqmanln@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-15 | 2025 | 8 | 15 | Machai HPS | 2.6 | 0.96 | 0.62 | 15476 | 14648 | 25.3 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 68420.81 | 223049.59 | 828 | Unit remained on bar delivering power to National Grid as per available inflow and system conditions, however the reduced inflow was maintained by the Irrigation Department as per demand of XEN (Swabi Irrigation Division) | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-15 | 2025 | 8 | 15 | Malakand-3 HPS | 81 | 65 | 25.47 | 611263 | 605490 | 51 | 22.32 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1733336.22 | 3831752.58 | 5773 | Units were running at as per available hydrology but due to heavy rain in catchment area & as flood alert in upper swat the irrigation department gradually decreased the water discharge in main canal as excessive trashes arrived at sediment & forebay resulting in choking of trash racks at 05:00hrs dated 15-08-2025 creating differential level between up & down stream about 5 feet .As such to avoid any damages units being desynchronized stepwise: Unit #03 at 06:12 Hrs., Unit #02 at 11:13 Hrs., and Unit #01 at 15:24 Hrs., leading to a complete complex shutdown to avoid any damage. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-15 | 2025 | 8 | 15 | Pehur HPS | 18 | 12.29 | 9.09 | 218200 | 210000 | 18.39 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 791070 | 836274 | 8200 | plant remained shutdown since 1842 hrs of the instructions of sdo irrigation due to flood warning in the command area. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-15 | 2025 | 8 | 15 | Reshun HPS | 4.2 | 3.08 | 1.93 | 43000 | 42390 | 2.74 | 2.63 | 87.67 | 13.48 | 91.33 | 45 | 92064 | 1241022.72 | 571417.2 | 669605.52 | 610 | Not reported | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-15 | 2025 | 8 | 15 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-16 | 2025 | 8 | 16 | Daral Khwar HPS | 36.6 | 36.6 | 32.62 | 786550 | 782950 | 15.6 | 13.09 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6473665.48 | 789209.24 | 3600 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 32.62 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-16 | 2025 | 8 | 16 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 8.94 | 0 | 0 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | Plant was shutdown at 0512 Hrs dated 14-08-2025 due to flood. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-16 | 2025 | 8 | 16 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 65.8 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | Due to heavy flood in Panjkora River the sand and silts accumulated at Intake and Sand Trap that choke the trash racks. Therefore, in order to ensure proper cleaning and to avoid operational hazards, the total complex was shutdown at 1030 Hrs of 16/08/2025. | luqmanln@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-16 | 2025 | 8 | 16 | Machai HPS | 2.6 | 0.5 | 0.05 | 2420 | 2200 | 25.3 | 5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 10276.2 | 281194.2 | 220 | 1.The unit, while on bar and delivering power to the National Grid as per available water inflow and prevailing system conditions, tripped at 0258Hrs on 16.08.2025 due to reverse power resulting from high system voltage. Subsequently, the unit remained shut down/standby and could not be synchronized with the system due to persistently high system voltage. The unit was finally synchronized with the system at 0714Hrs, once the voltage stabilized. 2.The unit, while on bar delivering power to the National Grid as per available water inflow and system conditions, was shut down as a precaution at 0900Hrs on 16-08-2025 due to a drop in the headrace level, caused by reduced water supply from the Irrigation Department. A call was made to Mr. Fazli Wahid (Irrigation Department) to inquire about the decreased inflow. As per his response, there was no water demand from the XEN (Swabi Irrigation Division) due to recent heavy rainfall. Consequently, the water supply to the Machai Canal has been suspended until the next indent, rendering the inflow insufficient for the smooth operation of the plant. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-16 | 2025 | 8 | 16 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 0 | 5565088.8 | 0 | Due to the arrival of very heavy trashes and severe choking of trash racks at forebay and sediment excluder, the cleaning work could not be completed. Therefore, in order to ensure proper cleaning and to avoid operational hazards, the total complex shutdown is hereby extended till 0700 hrs of 17/08/2025. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-16 | 2025 | 8 | 16 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 18.39 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | Plant remained shutdown throughout 24 hrs due to nill irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-16 | 2025 | 8 | 16 | Reshun HPS | 4.2 | 2.21 | 2.37 | 58000 | 57359 | 3.56 | 3.55 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 773199.32 | 585584.68 | 641 | Powerhouse tripped times due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-16 | 2025 | 8 | 16 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-17 | 2025 | 8 | 17 | Daral Khwar HPS | 36.6 | 36.6 | 29.74 | 716930 | 713730 | 15.6 | 11.94 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 5901333.76 | 1361540.96 | 3200 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 29.74 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-17 | 2025 | 8 | 17 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 8.9 | 0 | 0 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | Plant was shutdown at 0512 Hrs dated 14-08-2025 due to flood. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-17 | 2025 | 8 | 17 | Koto HPS | 40.8 | 13.02 | 11.69 | 183385 | 182770 | 65.8 | 34.95 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1506024.8 | 6562583.2 | 615 | Plant back to operation on 10:10 AM after cleaning of sediment and intake trash racks and one unit running on average load of 11.69 MW. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-17 | 2025 | 8 | 17 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 25.3 | 3 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0900Hrs on 16-08-2025 due to insufficient hydrology. Due to the recent heavy rainfall, reduced hydrological discharge was maintained by irrigation Deptt in accordance with the demand of the XEN (Swabi Irrigation Division). Consequently, the water supply to the Machai Canal has been suspended until the next indent. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-08-17 | 2025 | 8 | 17 | Malakand-3 HPS | 81 | 26 | 11.96 | 287014 | 283720 | 51 | 11.01 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 812205.24 | 4752883.56 | 3294 | After cleaning of trash racks at the Sediment Excluder and Forebay, water supply was diverted back by the Irrigation Department. Unit #01 was synchronized with the system at 12:35 Hrs on 17-08-2025, while Units #02 and #03 remained on standby due to less hydrology. The Irrigation Department faced an electricity issue at A.T Works, which restricted them from diverting the maximum supply towards Malakand-III. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-17 | 2025 | 8 | 17 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 18.39 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | Plant remained shut down since 1842 hours dated 15-08-2025, upon instruction of irrigation SDO due to flood warningand nill irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-17 | 2025 | 8 | 17 | Reshun HPS | 4.2 | 3.45 | 2.45 | 54000 | 53400 | 3.31 | 3.3 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 719832 | 638952 | 600 | Powerhouse tripped 10times due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-17 | 2025 | 8 | 17 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-18 | 2025 | 8 | 18 | Daral Khwar HPS | 36.6 | 29.6 | 27.94 | 674120 | 670520 | 15.6 | 11.21 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 5544060.52 | 1718814.2 | 3600 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 27.94 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-18 | 2025 | 8 | 18 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 8.9 | 0 | 0 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | Plant was shutdown at 0512 Hrs dated 14-08-2025 due to flood. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-18 | 2025 | 8 | 18 | Koto HPS | 40.8 | 13.48 | 12.29 | 297500 | 294560 | 65.8 | 35 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 2427174.4 | 5641433.6 | 2940 | Unit#01 was operational on average load of 12.29MW as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-18 | 2025 | 8 | 18 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 25.3 | 0 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0900Hrs on 16-08-2025 due to insufficient hydrology. Due to the recent heavy rainfall, reduced hydrological discharge was maintained by irrigation Deptt in accordance with the demand of the XEN (Swabi Irrigation Division). Consequently, the water supply to the Machai Canal has been suspended until the next indent. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-08-18 | 2025 | 8 | 18 | Malakand-3 HPS | 81 | 52 | 38.28 | 918764 | 909820 | 51 | 25.89 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2604541.71 | 2960547.09 | 8944 | Two units are currently in operation while one unit remains on standby due to low hydrology, as per information from the Irrigation Department the diversion bund at Amandara Headworks meant to divert river water into the main canal was completely washed away during the recent flood. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-18 | 2025 | 8 | 18 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 18.35 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | Plant shut down due to flood warning | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-18 | 2025 | 8 | 18 | Reshun HPS | 4.2 | 3.08 | 2.26 | 50000 | 49402 | 3.08 | 3.06 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 665938.96 | 692845.04 | 598 | Line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-18 | 2025 | 8 | 18 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-19 | 2025 | 8 | 19 | Daral Khwar HPS | 36.6 | 28.5 | 26.03 | 628230 | 624630 | 15.6 | 10.45 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 5164628.23 | 2098246.49 | 3600 | Unit No.01, 02 and 03 were on bar delivering an average load equal to 26.03 MW according to the available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-19 | 2025 | 8 | 19 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 8.9 | 0 | 0 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | Plant was shutdown and intake gate was closed at 0512 Hrs dated 14-08-2025 due to flood. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-19 | 2025 | 8 | 19 | Koto HPS | 40.8 | 17.45 | 13.52 | 325749 | 323390 | 65.8 | 37 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 2664733.6 | 5403874.4 | 2359 | Two units was operational with average load of 13.52MW and maximum load of 17.45 as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-19 | 2025 | 8 | 19 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 25.3 | 0 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0900Hrs on 16-08-2025 due to insufficient hydrology. Due to the recent heavy rainfall, reduced hydrological discharge was maintained by irrigation Deptt in accordance with the demand of the XEN (Swabi Irrigation Division). Consequently, the water supply to the Machai Canal has been suspended until the next indent. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-08-19 | 2025 | 8 | 19 | Malakand-3 HPS | 81 | 41 | 32.97 | 791224 | 782420 | 51 | 22.26 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2239833.73 | 3325255.07 | 8804 | Two units are currently in operation while one unit remains on standby due to low hydrology, as per information from the Irrigation Department the diversion bund at Amandara Headworks meant to divert river water into the main canal was completely washed away during the flood. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-19 | 2025 | 8 | 19 | Pehur HPS | 18 | 1.56 | 1.47 | 35200 | 35000 | 18.37 | 2 | 8.15 | 3.767 | 100 | 41 | 432000 | 1627344 | 131845 | 1495499 | 200 | No data submitted for this date | phpcmw18@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-08-19 | 2025 | 8 | 19 | Reshun HPS | 4.2 | 3.26 | 2.4 | 54000 | 53389 | 3.31 | 3.3 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 719683.72 | 639100.28 | 611 | nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-19 | 2025 | 8 | 19 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-20 | 2025 | 8 | 20 | Daral Khwar HPS | 36.6 | 24 | 21.71 | 523910 | 521110 | 15.6 | 8.71 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 4308693.81 | 2954180.91 | 2800 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 21.71 MW according to the available hydrology. 2. Unit No.01 stopped at 1018 Hrs due to low hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-20 | 2025 | 8 | 20 | Jabori HPS | 10.2 | 10.1 | 4.47 | 109700 | 108250 | 8.24 | 3.58 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 618020.9 | 779591.26 | 1450 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-20 | 2025 | 8 | 20 | Koto HPS | 40.8 | 20.2 | 14.14 | 341250 | 338138 | 65.8 | 44.11 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 2786257.12 | 5282350.88 | 3112 | Two units were operational with an average load of 14.14MW and a maximum load of 20.20MW as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-20 | 2025 | 8 | 20 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 25.3 | 0 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0900Hrs on 16-08-2025 due to insufficient hydrology. Due to the recent heavy rainfall, reduced hydrological discharge was maintained by irrigation Deptt in accordance with the demand of the XEN (Swabi Irrigation Division). Consequently, the water supply to the Machai Canal has been suspended until the next indent. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-08-20 | 2025 | 8 | 20 | Malakand-3 HPS | 81 | 39 | 32.66 | 783950 | 775010 | 51 | 22.83 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2218621.13 | 3346467.67 | 8940 | Units # 01 & 02 tripped at 13:29 hrs due to failure of 132 kV line supply. After restoration of the 132 kV supply, Unit #02 was synchronized at 14:02 hrs and Unit #01 at 14:09 hrs. Unit #03 remained on standby due to low hydrology. Two units are currently in operation while one unit remains on standby due to low hydrology. As per information from the Irrigation Department the diversion bund at Amandara Headworks meant to divert river water into the main canal was completely washed away during the flood. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-20 | 2025 | 8 | 20 | Pehur HPS | 18 | 5.8 | 2.93 | 70400 | 70000 | 18.39 | 4 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 263690 | 1363654 | 400 | Unit #01 remained off the bar, while at 0920 hours, Unit #2 was synchronized with a 4.60 MW load against a restricted discharge of 06 cms from the irrigation SDO due to low irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-20 | 2025 | 8 | 20 | Reshun HPS | 4.2 | 3 | 2.42 | 58000 | 57395 | 3.56 | 3.55 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 773684.6 | 585099.4 | 605 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-20 | 2025 | 8 | 20 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-21 | 2025 | 8 | 21 | Daral Khwar HPS | 36.6 | 20.5 | 19.33 | 466260 | 463860 | 15.6 | 7.76 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3835333.64 | 3427541.08 | 2400 | Unit No.02 and 03 were on bar delivering an average load equal to 19.33 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-21 | 2025 | 8 | 21 | Jabori HPS | 10.2 | 10.2 | 9.9 | 238780 | 236340 | 8.24 | 7.8 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 1349312.33 | 48299.83 | 2440 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-21 | 2025 | 8 | 21 | Koto HPS | 40.8 | 13.8 | 10.56 | 239750 | 239315 | 65.8 | 36 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1971955.6 | 6096652.4 | 435 | The plant was shut down for 2-3 hours for cleaning of the intake trash racks due to a recent flood in the Panjkora River. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-21 | 2025 | 8 | 21 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 25.3 | 0 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0900Hrs on 16-08-2025 due to insufficient hydrology. Due to the recent heavy rainfall, reduced hydrological discharge was maintained by irrigation Deptt in accordance with the demand of the XEN (Swabi Irrigation Division). Consequently, the water supply to the Machai Canal has been suspended until the next indent. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-08-21 | 2025 | 8 | 21 | Malakand-3 HPS | 81 | 38 | 33.62 | 806785 | 797550 | 51 | 22.78 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2283146.38 | 3281942.42 | 9235 | As per available hydrology from Irrigation Department Unit # 01 & 02 are on bar while Unit # 03 remains standby due to less hydrology. As per information from the Irrigation Department, the diversion bund at Amandara Headworks, which diverts river water into the main canal, was completely washed away during the flood. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-21 | 2025 | 8 | 21 | Pehur HPS | 18 | 12.05 | 9.3 | 223200 | 214000 | 18.39 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 806138 | 821206 | 9200 | Unit# 01 remained off the bar for 1030 Hrs due to restriction of flow in canal while unit# 01 was taken on bar at 1030 Hrs along with unit# 02 with total load 12.0 MW. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-21 | 2025 | 8 | 21 | Reshun HPS | 4.2 | 3.21 | 2.33 | 53000 | 52387 | 3.32 | 3.24 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 706176.76 | 652607.24 | 613 | powerhouse tripped 4times due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-21 | 2025 | 8 | 21 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-22 | 2025 | 8 | 22 | Daral Khwar HPS | 36.6 | 18.7 | 17.79 | 429000 | 427000 | 15.6 | 7.14 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3530564.1 | 3732310.62 | 2000 | Unit No.02 and 03 were on bar delivering an average load equal to 17.79 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-22 | 2025 | 8 | 22 | Jabori HPS | 10.2 | 9.9 | 8.56 | 205654 | 203050 | 8.24 | 6.72 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 1159253.06 | 238359.1 | 2604 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-22 | 2025 | 8 | 22 | Koto HPS | 40.8 | 15.4 | 13.51 | 324999 | 319885 | 65.8 | 42.76 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 2635852.4 | 5432755.6 | 5114 | Plant was operational on average load of 13.51 MW and a maximum load of 15.40 MW as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-22 | 2025 | 8 | 22 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 25.3 | 0 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0900Hrs on 16-08-2025 due to insufficient hydrology. Due to the recent heavy rainfall, reduced hydrological discharge was maintained by irrigation Deptt in accordance with the demand of the XEN (Swabi Irrigation Division). Consequently, the water supply to the Machai Canal has been suspended until the next indent. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-08-22 | 2025 | 8 | 22 | Malakand-3 HPS | 81 | 36 | 32.11 | 770657 | 761200 | 51 | 21.92 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2179087.24 | 3386001.56 | 9457 | Two units are currently in operation while one unit remains on standby due to low hydrology, as per information from the Irrigation Department the diversion bund at Amandara Headworks meant to divert river water into the main canal was completely washed away during the flood. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-22 | 2025 | 8 | 22 | Pehur HPS | 18 | 12000 | 11.95 | 286700 | 279000 | 18.39 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1050993 | 576351 | 7700 | Plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-22 | 2025 | 8 | 22 | Reshun HPS | 4.2 | 3.67 | 2.44 | 57000 | 56391 | 3.5 | 3.49 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 760150.68 | 598633.32 | 609 | powerhouse tripped 6time due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-22 | 2025 | 8 | 22 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-23 | 2025 | 8 | 23 | Daral Khwar HPS | 36.6 | 30.6 | 20.11 | 484610 | 482610 | 15.6 | 8.07 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3990364.26 | 3272510.46 | 2000 | 1. Unit No.01, 02 and 03 were on bar delivering an average load equal to 20.11 MW according to the available hydrology. 2. 132 KV Supply line failed at 0943 Hrs and was restored at 0955 Hrs. 3. Unit No.02 and 03 were synchronized with national grid at 10:05 Hrs, 10:08 Hrs respectively. 4. Unit No.01 was synchronised with the national grid at 1735Hrs due to increased hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-23 | 2025 | 8 | 23 | Jabori HPS | 10.2 | 10.2 | 8.99 | 215921 | 213430 | 8.24 | 7 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 1218514.56 | 179097.6 | 2491 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-23 | 2025 | 8 | 23 | Koto HPS | 40.8 | 15.9 | 13.38 | 321250 | 319625 | 65.5 | 38.14 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 2633710 | 5434898 | 1625 | Plant was operational on avg load of 13.38MW and maximum load of 15.9MW as per available hydrology | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-23 | 2025 | 8 | 23 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 25.3 | 0 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0900Hrs on 16-08-2025 due to insufficient hydrology. Due to the recent heavy rainfall, reduced hydrological discharge was maintained by irrigation Deptt in accordance with the demand of the XEN (Swabi Irrigation Division). Consequently, the water supply to the Machai Canal has been suspended until the next indent. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-08-23 | 2025 | 8 | 23 | Malakand-3 HPS | 81 | 37 | 31.69 | 760620 | 751100 | 51 | 21.83 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2150173.97 | 3414914.83 | 9520 | Two units are currently in operation while one unit remains on standby due to low hydrology, as per information from the Irrigation Department the diversion bund at Amandara Headworks meant to divert river water into the main canal was completely washed away during the flood. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-23 | 2025 | 8 | 23 | Pehur HPS | 18 | 12.05 | 9.9 | 237500 | 229000 | 18.39 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 862643 | 764701 | 8500 | At 2000 hrs, Plant shut down due to nil irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-23 | 2025 | 8 | 23 | Reshun HPS | 4.2 | 3.17 | 2.19 | 48000 | 47406 | 2.96 | 2.93 | 97.67 | 13.48 | 98.67 | 45 | 99456 | 1340666.88 | 639032.88 | 701634 | 594 | powerhouse tripped 8time due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-23 | 2025 | 8 | 23 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.47 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-24 | 2025 | 8 | 24 | Daral Khwar HPS | 36.6 | 22.5 | 18.51 | 446740 | 444340 | 15.6 | 7.43 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3673936.42 | 3588938.3 | 2400 | 1. Unit No.02 and 03 were on bar delivering an average load equal to 18.51 MW according to the available hydrology. 2. Unit No.01 was shutdown at 0235Hrs due to low hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-24 | 2025 | 8 | 24 | Jabori HPS | 10.2 | 9.9 | 8.7 | 210155 | 207830 | 8.24 | 6.87 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 1186543.04 | 211069.12 | 2325 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-24 | 2025 | 8 | 24 | Koto HPS | 40.8 | 13.77 | 13.64 | 327500 | 325707 | 65.8 | 36.64 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 2683825.68 | 5384782.32 | 1793 | Unit No.1 is operational on rated load as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-24 | 2025 | 8 | 24 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 25.3 | 0 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0900Hrs on 16-08-2025 due to insufficient hydrology. Due to the recent heavy rainfall, reduced hydrological discharge was maintained by irrigation Deptt in accordance with the demand of the XEN (Swabi Irrigation Division). Consequently, the water supply to the Machai Canal has been suspended until the next indent. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-08-24 | 2025 | 8 | 24 | Malakand-3 HPS | 81 | 38 | 31.61 | 758654 | 749950 | 51 | 21.66 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2146881.87 | 3418206.94 | 8704 | Two units are currently in operation while one unit remains on standby due to low hydrology, as per information from the Irrigation Department the diversion bund at Amandara Headworks meant to divert river water into the main canal was completely washed away during the flood. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-24 | 2025 | 8 | 24 | Pehur HPS | 18 | 6.04 | 2.9 | 69800 | 69000 | 18.39 | 5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 259923 | 1367421 | 800 | Unit#02 taken on bar with 6.0 mw at 1216 hrs dt 24-08-2025 as per irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-24 | 2025 | 8 | 24 | Reshun HPS | 4.2 | 3.23 | 2.3 | 55000 | 54390 | 3.38 | 3.37 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 733177.2 | 625606.8 | 610 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-24 | 2025 | 8 | 24 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-25 | 2025 | 8 | 25 | Daral Khwar HPS | 36.6 | 19.5 | 17.84 | 430060 | 428060 | 15.6 | 7.16 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3539328.5 | 3723546.22 | 2000 | Unit No.02 and 03 were on bar delivering an average load equal to 17.84 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-25 | 2025 | 8 | 25 | Jabori HPS | 10.2 | 10.1 | 8.3 | 199840 | 197540 | 8.24 | 6.53 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 1127795.37 | 269816.79 | 2300 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-25 | 2025 | 8 | 25 | Koto HPS | 40.8 | 14.09 | 13.64 | 326500 | 320281 | 65.8 | 36.88 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 2639115.44 | 5429492.56 | 6219 | The Plant was operational on average load 13.64 and maximum load of 14.09 | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-25 | 2025 | 8 | 25 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 25.3 | 11 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0900Hrs on 16-08-2025 till date due to insufficient hydrology, experienced reduced hydrological discharge throughout the monsoon period due to heavy rainfall and flood control measures. This reduction was implemented by the Irrigation Department in accordance with the directives of the XEN (Swabi Irrigation Division), which further limited water availability for power generation. According to the new indent of XEN (Swabi Irrigation Division) the water supply for Machai was increased upto 400 cusec which is not sufficient for the smooth operation of the Plant From: SDO Dargai To: SDO SHGI, Sub Engineers Dargai, katlang & Htn, c/SDO Head Works, c/Xen Irrigation Malakand, c/Xen Irrigation Swabi, c/SDO G.T.I, c/All Concerned C/W No. 677-7 Date: August 21, 2025 Subject: Released the Water Supply in Machai Branch. References: 1. SDO Shgi Canal Wire No. 16 dated August 21, 2025 2. Sub Engr Htn Canal Wire No. 153 dated August 21, 2025 3. Sub Engineer Katlang Section Canal Wire No. 80 dated August 21, 2025. This is to inform you that the supply has been released in the Machai Branch & run as 2.20=655 cusec, to Run Rd-95+000 Machai Branch as 3.00=289 cusec. Sub Engrs Dargai and katlang may be directed to adjust the X-Gates of Machai Branch & run your respective channels the half of full supply demand please. This report is submitted for information please. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-08-25 | 2025 | 8 | 25 | Malakand-3 HPS | 81 | 37 | 31.73 | 761445 | 752480 | 51 | 21.48 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2154124.5 | 3410964.3 | 8965 | Two units are currently in operation while one unit remains on standby due to low hydrology, as per information from the Irrigation Department the diversion bund at Amandara Headworks meant to divert river water into the main canal was completely washed away during the flood. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-25 | 2025 | 8 | 25 | Pehur HPS | 18 | 12.19 | 9.61 | 230700 | 225000 | 18.39 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 847575 | 779769 | 5700 | Unit#01 was taken on bar at 0913 Hrs along with unit# 02 with total load 12.0 MW as per irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-25 | 2025 | 8 | 25 | Reshun HPS | 4.2 | 2.95 | 2.3 | 53000 | 52400 | 3.32 | 3.24 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 706352 | 652432 | 600 | powerhouse tripped 5times. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-25 | 2025 | 8 | 25 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-26 | 2025 | 8 | 26 | Daral Khwar HPS | 36.6 | 17.7 | 16.07 | 387710 | 385710 | 15.6 | 6.45 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3189165.99 | 4073708.73 | 2000 | Unit No. 2 and 3 were on bar delivering an average load equal to 16.07 MW according to available hydrology | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-26 | 2025 | 8 | 26 | Jabori HPS | 10.2 | 9.1 | 8.36 | 200710 | 198360 | 8.24 | 6.56 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 1132476.91 | 265135.25 | 2350 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-26 | 2025 | 8 | 26 | Koto HPS | 40.8 | 13.88 | 13.45 | 321000 | 319600 | 65.8 | 37.25 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 2633504 | 5435104 | 1400 | The Plant was operational on average load of 13.45MW and maximum load of 13.88MW | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-26 | 2025 | 8 | 26 | Machai HPS | 2.6 | 0.75 | 0.1 | 1764 | 1632 | 25.3 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 7623.07 | 283847.33 | 132 | The Unit after all preliminary checks and started at 1950Hrs Dated 26-08-2025 as rated head was restored due to increase in canal discharge as per new indent of Swabi Irrigation Sub Division. Unit kept on FSNL for an half hour to carryout heat run test and finding everything normal then synchronized with the system at 2030Hrs and load gradually increased according to available inflow and system condition. Due to the recent heavy rainfall, reduced hydrological discharge was maintained by irrigation Deptt in accordance with the demand of the XEN (Swabi Irrigation Division). | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-26 | 2025 | 8 | 26 | Malakand-3 HPS | 81 | 44 | 33.22 | 797224 | 787990 | 51 | 22.73 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2255778.97 | 3309309.83 | 9234 | Two units are currently in operation while one unit remains on standby, as per information from the Irrigation Department the flow will be decreasing day by day. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-26 | 2025 | 8 | 26 | Pehur HPS | 18 | 12.18 | 11.87 | 285000 | 278000 | 18.39 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1047226 | 580118 | 7000 | Plant remained operational through out 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-26 | 2025 | 8 | 26 | Reshun HPS | 4.2 | 3.23 | 2.21 | 50000 | 49390 | 3.08 | 3.06 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 665777.2 | 693006.8 | 610 | outgoing Feeder tripped 3times. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-26 | 2025 | 8 | 26 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-27 | 2025 | 8 | 27 | Daral Khwar HPS | 36.6 | 15.2 | 14.91 | 359850 | 357850 | 15.6 | 5.98 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2958811.16 | 4304063.57 | 2000 | Unit No.02 and 03 were on bar delivering an average load equal to 14.91 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-27 | 2025 | 8 | 27 | Jabori HPS | 10.2 | 10.1 | 8 | 186170 | 183920 | 8.24 | 6.34 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 1050036.06 | 347576.1 | 2250 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-27 | 2025 | 8 | 27 | Koto HPS | 40.8 | 13.07 | 10.56 | 257500 | 254820 | 65.8 | 35.15 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 2099716.8 | 5968891.2 | 2680 | The Plant was operational on average load 10.56MW and maximum load 13.07MW | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-27 | 2025 | 8 | 27 | Machai HPS | 2.6 | 0.5 | 0.01 | 300 | 220 | 25.3 | 10 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 1027.62 | 290442.78 | 80 | Unit Forced Outage due to Reduced Inflow Unit Status: Standby (Precautionary) Reason: Drop in headrace level caused by reduced water supply from the Irrigation Department, due to the damaged Diversion Bund at Amandara Head Works. Details: The unit, while on bar delivering power to the National Grid as per available inflow and system conditions, was shut down as a precautionary measure at 0130 Hrs on 27-08-2025 following a significant drop in the headrace water level, caused by reduced discharge from the Irrigation Department. A telephonic inquiry was made to Mr. Fazli Wahid (Irrigation Department) regarding the decreased inflow. As per his response, the Diversion Bund at Amandara Head Works was fully washed away/damaged in the recent heavy flood, which has severely restricted canal discharge. The reduction in supply is linked with the following official correspondence: 3. Extract from Irrigation Department Communication From: SDO Dargai To: SDO Head Works, c/Sub Engineer Amandara, c/XEN Irrigation Malakand C/W No.: 726 Date: August 27, 2025 Subject: Starting Work on Diversion Bund at Amandara Head Works *“As per the daily gauge slip, the existing discharge of the Main Canal is decreasing day by day, due to which the supply is falling short of indent in both tunnels, resulting in insufficient water for the Abazai and Machai Branch Canals. Therefore, it is requested to kindly direct Sub Engineer Amandara to start work on the Diversion Bund at Amandara Head Works. Once the full diversion is restored, the indented supply for the three irrigation divisions (Malakand, Swabi & Charsadda) as well as the three hydel power stations (Malakand-III HPC Dargai, Jabban, and Dargai Power) will be met accordingly. This report is submitted for information and further necessary action.”* Conclusion: The unit will remain on standby until sufficient inflow is restored by the Irrigation Department following completion of Diversion Bund rehabilitation works at Amandara Head Works. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-27 | 2025 | 8 | 27 | Malakand-3 HPS | 81 | 32 | 26.51 | 636309 | 627160 | 51 | 18.59 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1795370.93 | 3769717.87 | 9149 | Two units are currently in operation while one unit remains on standby, as per information from the Irrigation Department the flow will be decreasing day by day. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-27 | 2025 | 8 | 27 | Pehur HPS | 18 | 12.04 | 11.9 | 285600 | 277000 | 18.39 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1043459 | 583885 | 8600 | plant remained operational throughout 24 hours as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-27 | 2025 | 8 | 27 | Reshun HPS | 4.2 | 2.78 | 2.23 | 54000 | 53387 | 3.31 | 3.3 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 719656.76 | 639127.24 | 613 | powerhouse trippeed 4times. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-27 | 2025 | 8 | 27 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-28 | 2025 | 8 | 28 | Daral Khwar HPS | 36.6 | 14.7 | 13.97 | 337760 | 335360 | 15.6 | 5.61 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2772857.09 | 4490017.63 | 2400 | Units No.02 and 03 were on bar delivering an average load equal to 13.97MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-28 | 2025 | 8 | 28 | Jabori HPS | 10.2 | 9 | 8.23 | 197520 | 195120 | 8.24 | 6.45 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 1113979.1 | 283633.06 | 2400 | Unit 01 was shutdown from 1148 Hrs to 1237 Hrs for changing the seal of Generator radial bearing RTD and tightening its bolts as leakage was observed from it. (PTW # 27/2025) | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-28 | 2025 | 8 | 28 | Koto HPS | 40.8 | 13.32 | 10.88 | 259499 | 257969 | 65.8 | 40.35 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 2125664.56 | 5942943.44 | 1530 | Plant is operational on average load of 10.88 and maximum load of 13.22 due to available hydrology | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-28 | 2025 | 8 | 28 | Machai HPS | 2.6 | 0.5 | 0.05 | 1412 | 1364 | 25.3 | 11.67 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 6371.24 | 285099.16 | 48 | 1. The Unit, after completion of all preliminary checks, was started at 1635 Hrs on 28-08-2025 as the rated head was restored due to increased canal discharge. The Unit was initially maintained at FSNL, and upon finding all parameters normal, it was synchronized with the system at 1953 Hrs. Load was gradually increased in accordance with available inflow and system conditions. However, due to recent heavy rainfall and flooding, the Irrigation Department continued maintaining reduced hydrological discharge owing to the damaged Diversion Bund at Amandara Head Works. 2. The unit, while on bar delivering power to the National Grid as per available inflow and system conditions, was shut down as a precautionary measure at 2105Hrs on 28-08-2025 following a significant drop in the headrace water level, caused by reduced discharge from the Irrigation Department due to the damaged Diversion Bund at Amandara Head Works. As per SDO Dargai C/W No. 726 dated 27-08-2025: Main Canal discharge decreasing daily, short supply to Abazai & Machai Branch Canals. Urgent work required on Diversion Bund to restore supply for irrigation and power generation. The unit will remain on standby until sufficient inflow is restored by the Irrigation Department following completion of Diversion Bund rehabilitation works at Amandara Head Works. | engr.atifwazir@gmail.com | Original | Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-08-28 | 2025 | 8 | 28 | Malakand-3 HPS | 81 | 31 | 28.25 | 678020 | 668690 | 51 | 19.88 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1914258.86 | 3650829.94 | 9330 | Two units are currently in operation while one unit remains on standby, as per information from the Irrigation Department the flow will be decreasing day by day, as the diversion bund at Amandara head works was damaged due to flood. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-28 | 2025 | 8 | 28 | Pehur HPS | 18 | 12.25 | 9.54 | 229000 | 222000 | 18.39 | 14.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 836274 | 791070 | 7000 | plant remained shutdown from 1920 Hrs dt 28-08-25 in search of dead body recovery in the canal as per instruction of irrigation SDO. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-28 | 2025 | 8 | 28 | Reshun HPS | 4.2 | 2.81 | 2.16 | 51000 | 50408 | 3.14 | 3.12 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 679499.84 | 679284.16 | 592 | outgoing feeder tripped 8time due to line faults | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-28 | 2025 | 8 | 28 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-29 | 2025 | 8 | 29 | Daral Khwar HPS | 36.6 | 14 | 13.17 | 319350 | 316150 | 15.6 | 5.29 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2614023.04 | 4648851.68 | 3200 | Unit No.02 and 03 were on bar delivering an average load equal to 13.17 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-29 | 2025 | 8 | 29 | Jabori HPS | 10.2 | 8.3 | 8 | 192510 | 190160 | 8.24 | 6.3 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 1085661.47 | 311950.69 | 2350 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-29 | 2025 | 8 | 29 | Koto HPS | 40.8 | 12.32 | 9.67 | 237000 | 236088 | 65.8 | 33.59 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1945365.12 | 6123242.88 | 912 | Plant was operational on average load of 9.67 MW and a maximum load of 12.32MW as per available hydrology | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-29 | 2025 | 8 | 29 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 25.3 | 13.33 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 2105Hrs on 28-08-2025 due to insufficient hydrology following a significant drop in the headrace water level, caused by reduced discharge from the Irrigation Department due to the damaged Diversion Bund at Amandara Head Works.As per SDO Dargai (C/W No. 726, dated 27-08-2025), the Main Canal discharge is decreasing on a daily basis, resulting in short supply to both the Abazai and Machai Branch Canals. Restoration of normal supply for irrigation and hydropower generation is contingent upon rehabilitation of the Diversion Bund at Amandara Head Works. The unit will remain on standby until sufficient inflow is restored by the Irrigation Department following completion of Diversion Bund rehabilitation works at Amandara Head Works. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-08-29 | 2025 | 8 | 29 | Malakand-3 HPS | 81 | 39 | 32.9 | 789644 | 779840 | 51 | 22.48 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2232447.97 | 3332640.83 | 9804 | Two units are currently in operation while one unit remains on standby, as per information from the Irrigation Department the diversion bund at Amandara head works was damaged due to flood. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-29 | 2025 | 8 | 29 | Pehur HPS | 18 | 12.09 | 7.77 | 186600 | 182000 | 18.39 | 12 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 685594 | 941750 | 4600 | plant remained shutdown from 1920 Hrs dt 28-08-25 to 09:15 hours dt. 29-08-25 in search of dead body recovery as per instruction of irrigation SDO. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-29 | 2025 | 8 | 29 | Reshun HPS | 4.2 | 4.2 | 2.51 | 57000 | 56424 | 3.5 | 3.49 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 760595.52 | 598188.48 | 576 | Outgoing feeder tripped 2times. | zafar.src@gmail.com | Original | Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-08-29 | 2025 | 8 | 29 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-30 | 2025 | 8 | 30 | Daral Khwar HPS | 36.6 | 17.5 | 13.76 | 333010 | 330210 | 15.6 | 5.52 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2730275.34 | 4532599.38 | 2800 | Unit No.02 and 03 were on bar delivering an average load equal to 13.76 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-30 | 2025 | 8 | 30 | Jabori HPS | 10.2 | 8.5 | 7.8 | 188800 | 186520 | 8.24 | 6.17 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 1064879.98 | 332732.18 | 2280 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-30 | 2025 | 8 | 30 | Koto HPS | 40.8 | 14.85 | 10 | 237998 | 237206 | 65.8 | 35.01 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1954577.44 | 6114030.56 | 792 | Plant was operational on average load of 10.00MW and maximum load of 14.85 MW as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-30 | 2025 | 8 | 30 | Machai HPS | 2.6 | 0.78 | 0.23 | 5292 | 5016 | 25.3 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 23429.74 | 268040.66 | 276 | The Unit, after completion of all preliminary checks, was started at 1605 Hrs on 230-08-2025 as the rated head was restored due to increased canal discharge. The Unit was initially maintained at FSNL, and upon finding all parameters normal, it was synchronized with the system at 1627Hrs. Load was gradually increased in accordance with available inflow and system conditions. However, due to recent heavy rainfall and flooding, the Irrigation Department continued maintaining reduced hydrological discharge owing to the damaged Diversion Bund at Amandara Head Works. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-30 | 2025 | 8 | 30 | Malakand-3 HPS | 81 | 46 | 39.71 | 953010 | 944090 | 51 | 26.78 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2702646.44 | 2862442.36 | 8920 | Two units are currently in operation while one unit remains on standby due to less hydrology, as per information from the Irrigation Department the diversion bund at Amandara head works was damaged due to flood. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-30 | 2025 | 8 | 30 | Pehur HPS | 18 | 12.06 | 11.79 | 283100 | 276000 | 18.39 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1039692 | 587652 | 7100 | The plant remained operational for 24 hours as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-30 | 2025 | 8 | 30 | Reshun HPS | 4.2 | 2.94 | 2.32 | 53000 | 52420 | 3.26 | 3.24 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 706621.6 | 652162.4 | 580 | outgoing feeder 6times tripped due to line faults | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-30 | 2025 | 8 | 30 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-31 | 2025 | 8 | 31 | Daral Khwar HPS | 36.6 | 17.5 | 14.81 | 358320 | 355520 | 15.6 | 5.95 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2939546.02 | 4323328.7 | 2800 | Unit No.02 and 03 were on bar delivering an average load equal to 14.81 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-31 | 2025 | 8 | 31 | Jabori HPS | 10.2 | 9.3 | 7.8 | 168430 | 166330 | 8.24 | 6.14 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 949611.24 | 448000.92 | 2100 | Plant was shutdown from 1200 Hrs to 1442 Hrs for cleaning of trash rack, desiltation of sand trap and cleaning of strainers. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-31 | 2025 | 8 | 31 | Koto HPS | 40.8 | 12.82 | 11.03 | 264000 | 261373 | 65.8 | 35.09 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 2153713.52 | 5914894.48 | 2627 | Plant was operational on average load of 11.03 MW and a maximum load of 12.82 MW as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-31 | 2025 | 8 | 31 | Machai HPS | 2.6 | 0.78 | 0.72 | 17540 | 16720 | 25.3 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 78099.12 | 213371.28 | 820 | The unit remained on bar, delivering power to the National Grid as per the available water inflow and system conditions. However, due to recent heavy rainfall and flooding, the Irrigation Department continued maintaining reduced hydrological discharge owing to the damaged Diversion Bund at Amandara Head Works. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-31 | 2025 | 8 | 31 | Malakand-3 HPS | 81 | 44 | 38.5 | 924030 | 915320 | 51 | 26.26 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2620286.56 | 2944802.24 | 8710 | Two units are currently in operation while one unit remains on standby due to less hydrology, as per information from the Irrigation Department the diversion bund at Amandara head works was damaged due to flood. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-31 | 2025 | 8 | 31 | Pehur HPS | 18 | 12.12 | 11.85 | 284600 | 276000 | 18.39 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1039692 | 587652 | 8600 | plant remained operational throughout 24 hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-31 | 2025 | 8 | 31 | Reshun HPS | 4.2 | 3.18 | 2.24 | 52000 | 51423 | 3.18 | 3.19 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 693182.04 | 665601.96 | 577 | outgoing feeder breaker tripped 4times. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-08-31 | 2025 | 8 | 31 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-01 | 2025 | 9 | 1 | Daral Khwar HPS | 36.6 | 16.5 | 13.67 | 331220 | 328020 | 6.47 | 5.49 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2712167.77 | 4550706.95 | 3200 | Unit No.02 and 03 were on bar delivering an average load equal to 13.67 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-01 | 2025 | 9 | 1 | Jabori HPS | 10.2 | 8.2 | 7.28 | 174910 | 172610 | 7.72 | 5.71 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 985465.01 | 412147.15 | 2300 | Plant was operational as per available hydrology. 132 KV line tripped at 1857 Hrs. Line restored at 1919 Hrs. Unit 01 and 02 were resynchronised at 1930 Hrs. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-01 | 2025 | 9 | 1 | Koto HPS | 40.8 | 12.63 | 10.22 | 245500 | 243533 | 65.8 | 34.41 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 2006711.92 | 6061896.08 | 1967 | Plant was operational on average load of 10.22 MW and a maximum load of 12.63 MW as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-01 | 2025 | 9 | 1 | Machai HPS | 2.6 | 0.96 | 0.7 | 17852 | 17160 | 28.6 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 80154.36 | 211316.04 | 692 | The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 2058Hrs dated 01.09.2025 with Reverse power due to high system voltage . Unit synchronized with the system at 2212Hrs as system voltage stabilized. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-01 | 2025 | 9 | 1 | Malakand-3 HPS | 81 | 47 | 38.44 | 922534 | 913430 | 51 | 26.61 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2614876.06 | 2950212.74 | 9104 | Two units are currently in operation while one unit remains on standby due to less hydrology, as per information from the Irrigation Department the diversion bund at Amandara head works was damaged due to flood. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-01 | 2025 | 9 | 1 | Pehur HPS | 18 | 12.43 | 11.84 | 284100 | 276000 | 21.22 | 19.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1039692 | 587652 | 8100 | The plant remained operational for 24 hours as per available hydrology, and the irrigation valve is open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-01 | 2025 | 9 | 1 | Reshun HPS | 4.2 | 3.25 | 2.38 | 55000 | 54429 | 3.38 | 3.37 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 733702.92 | 625081.08 | 571 | outgoing feeder breaker tripped 3times. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-01 | 2025 | 9 | 1 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-02 | 2025 | 9 | 2 | Daral Khwar HPS | 36.6 | 13 | 12.4 | 300080 | 297680 | 6.47 | 4.98 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2461307.54 | 4801567.18 | 2400 | 1. Unit No.02 and 03 were on bar delivering an average load equal to 12.40 MW according to the available hydrology. 2. Unit No.02 was shutdown at 0920Hrs due to low hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-02 | 2025 | 9 | 2 | Jabori HPS | 10.2 | 9.8 | 8.41 | 201900 | 199520 | 7.72 | 7 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 1139099.58 | 258512.58 | 2380 | Plant operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-02 | 2025 | 9 | 2 | Koto HPS | 40.8 | 13.4 | 11.9 | 303000 | 301979 | 65.8 | 34.79 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 2488306.96 | 5580301.04 | 1021 | Plant was operational on average load 11.90 and maximum load of 13.40 | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-02 | 2025 | 9 | 2 | Machai HPS | 2.6 | 1.13 | 0.74 | 18384 | 0 | 28.6 | 15.5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 18384 | 1.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 0640Hrs dated 02.09.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault.Unit synchronized with the system at 0652Hrs as 11KV Machai-HPS line energized at 0645Hrs. 2.The Unit, while on-bar delivering power to the National Grid as per available water inflow and system conditions, was precautionarily shut down at 1600 Hrs on 02-09-2025 for execution of monthly preventive maintenance under PTW. Maintenance activities were carried out in accordance with the prescribed checklist. Upon completion, the Unit was restored to operational readiness, with all critical parameters verified to be within design limits. The Unit was declared ready for recommissioning in line with system demand and irrigation discharge availability. The Unit was synchronized back to the system at 1930 Hrs, and the PTW was formally cancelled at 1900 Hrs | engr.atifwazir@gmail.com | Original | Net = Units - Aux; Avg Historical Hydrology interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-09-02 | 2025 | 9 | 2 | Malakand-3 HPS | 81 | 46 | 37.15 | 891695 | 882590 | 51 | 25.53 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2526590.39 | 3038498.41 | 9105 | Two units are currently in operation while one unit remains on standby due to less hydrology, as per information from the Irrigation Department the diversion bund at Amandara head works was damaged due to flood. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-02 | 2025 | 9 | 2 | Pehur HPS | 18 | 11.99 | 11.79 | 283100 | 275000 | 21.22 | 19 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1035925 | 591419 | 8100 | plant remained operational throughout 24 hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-02 | 2025 | 9 | 2 | Reshun HPS | 4.2 | 3.71 | 2.21 | 53000 | 52432 | 3.26 | 3.24 | 52.58 | 13.48 | 100 | 45 | 100800 | 1358784 | 706783.36 | 652000.64 | 568 | No data submitted for this date | zafar.src@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-09-02 | 2025 | 9 | 2 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-03 | 2025 | 9 | 3 | Daral Khwar HPS | 36.6 | 15.3 | 12.86 | 310620 | 308620 | 6.47 | 5.16 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2551762.75 | 4711111.97 | 2000 | Unit No.02 was on bar delivering an average load equal to 12.86 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-03 | 2025 | 9 | 3 | Jabori HPS | 10.2 | 10.2 | 7.3 | 175322 | 173050 | 7.72 | 5.72 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 987977.06 | 409635.1 | 2272 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-03 | 2025 | 9 | 3 | Koto HPS | 40.8 | 16.08 | 11.57 | 271750 | 270323 | 40.9 | 37 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 2227461.52 | 5841146.48 | 1427 | The Plant was operational on average load 11.57 and maximum load of 16.08 | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-03 | 2025 | 9 | 3 | Machai HPS | 2.6 | 0.89 | 0.71 | 17088 | 16300 | 28.6 | 16 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 76137.3 | 215333.1 | 788 | 1.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 1947Hrs dated 03.09.2025 with Reverse power due to high system voltage . Unit synchronized with the system at 2009Hrs as system voltage stabilized. 2.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 2126Hrs dated 03.09.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault.Unit synchronized with the system at 2156Hrs as 11KV Machai-HPS line energized at 0645Hrs. 3.The unit, while on bar delivering restricted power to the National Grid based on available water, experienced reduced hydrological discharge due to recent heavy rainfall and flooding, the Irrigation Department continued maintaining reduced hydrological discharge owing to the damaged Diversion Bund at Amandara Head Works. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-03 | 2025 | 9 | 3 | Malakand-3 HPS | 81 | 41 | 35.64 | 855300 | 846210 | 51 | 24.85 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2422445.37 | 3142643.43 | 9090 | Two units are currently in operation while one unit remains on standby due to less hydrology, as per information from the Irrigation Department the diversion bund at Amandara head works was damaged due to flood. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-03 | 2025 | 9 | 3 | Pehur HPS | 18 | 11.89 | 11.8 | 283200 | 275000 | 21.22 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1035925 | 591419 | 8200 | Plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-03 | 2025 | 9 | 3 | Reshun HPS | 4.2 | 3.05 | 2.19 | 51000 | 50434 | 3.14 | 3.12 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 679850.32 | 678933.68 | 566 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-03 | 2025 | 9 | 3 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-04 | 2025 | 9 | 4 | Daral Khwar HPS | 36.6 | 15.3 | 13.53 | 326690 | 324690 | 6.47 | 5.43 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2684634.33 | 4578240.39 | 2000 | 1. Unit No.02 and then 03 were on bar delivering an average load equal to 13.53 MW according to the available hydrology. 2. Plant was shutdown at 1240hrs for rectification of air/gas accumulation in isolation transformer and collection of samples for testing. Work executed by OEM of transformer against PTW No. 65/2025 3. After completion of work by OEM Unit# 03 was synchronised with the national grid at 1330hrs. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-04 | 2025 | 9 | 4 | Jabori HPS | 10.2 | 10.2 | 7.44 | 178465 | 176230 | 7.72 | 5.83 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 1006132.32 | 391479.84 | 2235 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-04 | 2025 | 9 | 4 | Koto HPS | 40.8 | 17.58 | 11.08 | 258000 | 257194 | 40.9 | 34.56 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 2119278.56 | 5949329.44 | 806 | The plant was operational on average load of 11.08 MW as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-04 | 2025 | 9 | 4 | Machai HPS | 2.6 | 0.97 | 0.48 | 11492 | 11000 | 28.6 | 12 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 51381 | 240089.4 | 492 | Shutdown Report – Unit Forced Outage due to Reduced Inflow Unit Status: Shut Down (Precautionary) Reason: Drop in headrace level caused by reduced water supply from the Irrigation Department, due to divert the Water Supply to E-Crack at At-works for more Excavation Works.. Details: The unit, while on bar delivering power to the National Grid as per available inflow and system conditions, was shut down as a precautionary measure at 1600Hrs on 04-09-2025 following a significant drop in the headrace water level, caused by reduced discharge from the Irrigation Department. A telephonic inquiry was made to Mr. Fazli Wahid (Irrigation Department) regarding the decreased inflow. As per his response, the Diversion Bund at Amandara Head Works was fully washed away/damaged in the recent heavy flood, which has severely restricted canal discharge. The reduction in supply is linked with the following official correspondence: 3. Extract from Irrigation Department Communication From: SDO Head Works, at Dargai To: Resident Engineer Jabban Power, Resident Engineer MKD-III HPC Dargai, Resident Engineer Dargai Power, c/Project Manager MKD-III HPC Dargai, c/Xen Irrigation Malakand, c/SDO Dargai, c/All Concerned C/W No. 730-7 Dated: September 3, 2025 Subject: Divert the Water Supply to E-Crack at At-works for more Excavation Works. I am writing to bring your attention, Due to high water flows in River Swat, excavation work for creating a diversion at Amandara Head Works has been hindered. To facilitate further excavation, I have diverted the supply to E-Crack at A-Tunnel tomorrow during hours, from 8:00 AM to 4:00 PM reducing the supply to Amandara Head Works. Furthermore if there is any fluctuation in your demand, please inform the Head Regulation Signaller office Dargai accordingly. This report is submitted for your information.” Conclusion: The unit will remain on standby until sufficient inflow is restored by the Irrigation Department. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-04 | 2025 | 9 | 4 | Malakand-3 HPS | 81 | 44 | 18.49 | 444433 | 439870 | 51 | 13.96 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1259215.85 | 4305872.95 | 4563 | Unit 03 & 02 desynchronized from the system at 09:38hrs ,10:28hrs Due to the high water flow in the River Swat, the excavation work for creating a diversion at Amandara Headwork was hindered. To facilitate further excavation, the Irrigation Department diverted the water supply from Auxiliary Tunnel to river swat at 08:00hrs Dated: 04 -09-2025 . The supply was then restored to auxiliary tunnel at 1912 hrs .Unit # 02 & 03 sychronized with system at 22:25Hrs & 22:58Hrs while Unit # 01 kept standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-04 | 2025 | 9 | 4 | Pehur HPS | 18 | 11.89 | 11.76 | 282200 | 274000 | 21.22 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1032158 | 595186 | 8200 | Plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-04 | 2025 | 9 | 4 | Reshun HPS | 4.2 | 3.11 | 2.24 | 54000 | 53446 | 3.31 | 3.3 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 720452.08 | 638331.92 | 554 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-04 | 2025 | 9 | 4 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 100 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original | Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-09-05 | 2025 | 9 | 5 | Daral Khwar HPS | 36.6 | 30.6 | 15.58 | 376330 | 373930 | 6.47 | 6.25 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3091765.42 | 4171109.3 | 2400 | 1. Unit No.02, and 03 were on bar delivering an average load equal to 15.58 MW according to the available hydrology. 2. Unit No.02 was synchronized with the national grid at 1413 Hrs due to rise in hydrology caused by rain. 3. 132 KV Supply line failed at 1552 Hrs and was restored at 1601 Hrs. 4. Unit No.02 and 03 were synchronized with national grid at 1609 Hrs, 1630 Hrs respectively. 5. Unit No.03 was shutdown due to choking of cooling water pumps at 2055Hrs and Unit#01 was synchronised with national grid at 2055 Hrs. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-05 | 2025 | 9 | 5 | Jabori HPS | 10.2 | 9.1 | 7.8 | 85824 | 84480 | 7.72 | 6.11 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 482313.22 | 915298.94 | 1344 | Due to heavy rains in the current week water quality remains bad which ultimately resulted in more accumulation of sand than expected in the sand trap,therefore the power house was shut down for sand trap flushing ,cleaning of strainers,complete cleaning of Trash Racks etc | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-05 | 2025 | 9 | 5 | Koto HPS | 40.8 | 13.45 | 12.24 | 295750 | 291040 | 40.9 | 37.84 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 2398169.6 | 5670438.4 | 4710 | Plant was operational on average load of 12.24 MW and a maximum load of 13.45 MW as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-05 | 2025 | 9 | 5 | Machai HPS | 2.6 | 0.91 | 0.5 | 11688 | 11132 | 28.6 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 51997.57 | 239472.83 | 556 | Unit precautionary standard and synchronized with the system at 1000Hrs dated 05-09-2025 as rated head was restored due to increase in the Canal discharge | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-05 | 2025 | 9 | 5 | Malakand-3 HPS | 81 | 43 | 37.56 | 901531 | 891990 | 51 | 25.08 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2553499.77 | 3011589.03 | 9541 | As per available hydrology from Irrigation Department Unit # 01 & 02 are on bar while Unit # 03 kept standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-05 | 2025 | 9 | 5 | Pehur HPS | 18 | 11.96 | 11.81 | 283500 | 276000 | 21.22 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1039692 | 587652 | 7500 | Plant Operational for 24 Hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-05 | 2025 | 9 | 5 | Reshun HPS | 4.2 | 3.41 | 1.21 | 49000 | 48434 | 3.01 | 3 | 99.97 | 13.48 | 100 | 45 | 100800 | 1358784 | 652890.32 | 705893.68 | 566 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-05 | 2025 | 9 | 5 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-06 | 2025 | 9 | 6 | Daral Khwar HPS | 36.6 | 15 | 10.77 | 260950 | 258550 | 6.47 | 4.32 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2137768.96 | 5125105.76 | 2400 | 1. Unit No.01, and 02 were on bar delivering an average load equal to 10.77 MW according to the available hydrology. 2. Unit No.02 was stopped due to cleaning of sum tank of cooling water system as per PTW# 67/2025 at 0915 Hrs. 3. 132 KV Supply line failed at 1205 Hrs and was restored at 1210 Hrs. 4. Unit No.01 was synchronised with the national grid at 1220 Hrs. 5. Unit No.02 was synchronised with national grid after closing of PTW#67/2025 at 1723 Hrs and Unit#01 was shutdown due to low hydrology at 1727 Hrs. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-06 | 2025 | 9 | 6 | Jabori HPS | 10.2 | 8.5 | 7.26 | 174294 | 171750 | 7.72 | 5.69 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 980555.1 | 417057.06 | 2544 | Due to heavy rains in the current week water quality remains bad which ultimately resulted in more accumulation of sand than expected in the sand trap,therefore the power house was shut down for sand trap flushing ,cleaning of strainers,complete cleaning of Trash Racks etc | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-06 | 2025 | 9 | 6 | Koto HPS | 40.8 | 13.73 | 13.3 | 313458 | 313458 | 40.9 | 36.57 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 2582893.92 | 5485714.08 | 0 | The plant was operational on average load 13.30MW and maximum load of 13.30MW | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-06 | 2025 | 9 | 6 | Machai HPS | 2.6 | 1.67 | 0.85 | 19152 | 18392 | 28.6 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 85909.03 | 205561.37 | 760 | Unit tripped at 0343Hrs Dated 06-09-2025 on Reverse Power due to high system voltage and synchronized with the system at 0455Hrs as system voltage stabilized .However,reduced hydrology discharge was maintained by the irrigation department due to the damaged Band at Amandara Head Works. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-06 | 2025 | 9 | 6 | Malakand-3 HPS | 81 | 45 | 38.68 | 928336 | 919090 | 51 | 25.48 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2631078.94 | 2934009.86 | 9246 | Units # 01 & 02 tripped at 03:00hrs due to failure of 132 kV line supply. After restoration of the 132 kV supply, Unit #01 was synchronized at 03:25 hrs. and Unit # 02 at 03:31 hrs. Unit #03 remained on standby due to low hydrology Now Two units are currently in operation while one unit remains on standby due to low hydrology | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-06 | 2025 | 9 | 6 | Pehur HPS | 18 | 11.79 | 10.63 | 255200 | 247000 | 21.22 | 15.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 930449 | 696895 | 8200 | Unit# 02 was taken off the bar at 1941 Hrs upon the request of irrigation SDO to reduce the discharge for the search of dead body in the canal. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-06 | 2025 | 9 | 6 | Reshun HPS | 4.2 | 2.96 | 2.96 | 47000 | 4644 | 2.98 | 2.88 | 95.9 | 13.48 | 99.5 | 45 | 100296 | 1351990.08 | 62601.12 | 1289388.96 | 42356 | outgoing feeder breaker tripped 6times due line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-06 | 2025 | 9 | 6 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | No data submitted for this date | ibrarahmadmkd@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-09-07 | 2025 | 9 | 7 | Daral Khwar HPS | 36.6 | 14 | 11.13 | 269090 | 267090 | 6.47 | 4.47 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2208380.25 | 5054494.47 | 2000 | 1. Unit No.02 was on bar delivering an average load equal to 11.13 MW according to the available hydrology. 2. 132 KV Supply line failed at 0947 Hrs and was restored at 1237 Hrs. 3. Unit No.02 was synchronised with the national grid at 1244 Hrs. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-07 | 2025 | 9 | 7 | Jabori HPS | 10.2 | 9.5 | 7.57 | 181722 | 179220 | 7.72 | 5.93 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 1023202.82 | 374409.34 | 2502 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-07 | 2025 | 9 | 7 | Koto HPS | 40.8 | 11.65 | 10.02 | 239500 | 237482 | 40.9 | 34.35 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1956851.68 | 6111756.32 | 2018 | The plant was operational on average 10.02 and maximum load of 11.65 | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-07 | 2025 | 9 | 7 | Machai HPS | 2.6 | 1.16 | 0.95 | 22772 | 21916 | 28.6 | 15.5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 102369.64 | 189100.76 | 856 | The unit, while on bar delivering restricted power to the National Grid based on available water, experienced reduced hydrological discharge due to recent heavy rainfall. This reduction was implemented by the Irrigation Department As per C/W No.: 726- SDO Dargai C/W No. 726 dated 27-08-2025: Main Canal discharge decreasing daily, short supply to Abazai & Machai Branch Canals due to recent heavy rainfall and flooding, the Irrigation Department continued maintaining reduced hydrological discharge owing to the damaged Diversion Bund at Amandara Head Works, which further affected water availability for power generation. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-07 | 2025 | 9 | 7 | Malakand-3 HPS | 81 | 50 | 40 | 960050 | 951000 | 51 | 26.67 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2722427.7 | 2842661.1 | 9050 | As per available hydrology from Irrigation Department Unit # 01 & 02 are on bar while Unit # 03 kept standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-07 | 2025 | 9 | 7 | Pehur HPS | 18 | 11.83 | 8.74 | 209800 | 203000 | 21.22 | 13 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 764701 | 862643 | 6800 | Unit# 02 remained off the bar since 1941 Hrs dated 06-09-2025 & unit# 01 was also taken off the bar at 0657 Hrs upon the request of irrigation SDO for the search of dead body in the canal. After the recovery of dead body both units were taken on bar at 0840 & 0846 Hrs with total load 12.0 MW. Unit# 01 & 02 also remained off the bar for 00:28 Hrs due to isolation of gadoon grid from national grid. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-07 | 2025 | 9 | 7 | Reshun HPS | 4.2 | 3.01 | 1.64 | 35000 | 34438 | 2.1 | 2.08 | 69.33 | 13.48 | 69.83 | 45 | 70392 | 948884.16 | 464224.24 | 484659.92 | 562 | work in Transmission line at Kalak area. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-07 | 2025 | 9 | 7 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-08 | 2025 | 9 | 8 | Daral Khwar HPS | 36.6 | 15.3 | 12.37 | 296990 | 294990 | 6.47 | 4.97 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2439065.82 | 4823808.9 | 2000 | Unit No. 02 was on bar delivering an average load equal to 12.37 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-08 | 2025 | 9 | 8 | Jabori HPS | 10.2 | 8 | 7 | 169789 | 167300 | 7.72 | 5.54 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 955149.16 | 442463 | 2489 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-08 | 2025 | 9 | 8 | Koto HPS | 40.8 | 13.18 | 10.01 | 187500 | 185755 | 40.9 | 27.25 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1530621.2 | 6537986.8 | 1745 | Plant was operational on average load of 10.01 MW and a maximum load of 13.18 MW as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-08 | 2025 | 9 | 8 | Machai HPS | 2.6 | 1.03 | 0.88 | 22036 | 21160 | 28.6 | 16 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 98838.36 | 192632.04 | 876 | The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 0734Hrs and 1601Hrs dated 08.09.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault.Unit synchronized with the system at 0804Hrs and 1627Hrs respectively as 11KV Machai-HPS line energized , while to recent heavy rainfall and flooding, the Irrigation Department continued maintaining reduced hydrological discharge owing to the damaged Diversion Bund at Amandara Head Works. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-08 | 2025 | 9 | 8 | Malakand-3 HPS | 81 | 48 | 44.67 | 1072070 | 1063020 | 51 | 29.13 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3043107.35 | 2521981.45 | 9050 | As per available hydrology from Irrigation Department Unit # 01 & 02 are on bar while Unit # 03 kept standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-08 | 2025 | 9 | 8 | Pehur HPS | 18 | 12.01 | 11.85 | 283600 | 275000 | 21.22 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1035925 | 591419 | 8600 | The plant remained operational throughout 24 hours as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-08 | 2025 | 9 | 8 | Reshun HPS | 4.2 | 3.13 | 2.17 | 48000 | 47398 | 2.94 | 2.93 | 97.67 | 13.48 | 98.17 | 45 | 98952 | 1333872.96 | 638925.04 | 694947.92 | 602 | outgoing feeder breaker tripped 5times. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-08 | 2025 | 9 | 8 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-09 | 2025 | 9 | 9 | Daral Khwar HPS | 36.6 | 13 | 11.9 | 285520 | 283120 | 6.47 | 4.73 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2340921.1 | 4921953.62 | 2400 | Unit No.02 was on bar delivering an average load equal to 11.9 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-09 | 2025 | 9 | 9 | Jabori HPS | 10.2 | 7.3 | 6.78 | 162930 | 160410 | 7.72 | 5.32 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 915812.77 | 481799.39 | 2520 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-09 | 2025 | 9 | 9 | Koto HPS | 40.8 | 12.7 | 11.21 | 269000 | 266798 | 40.9 | 37.41 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 2198415.52 | 5870192.48 | 2202 | The plant was operational on average load of 11.21MW and maximum load of 12.70MW as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-09 | 2025 | 9 | 9 | Machai HPS | 2.6 | 1.02 | 0.93 | 21372 | 20460 | 28.6 | 16 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 95568.66 | 195901.74 | 912 | The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 1638Hrs and 2203Hrs dated 09.09.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault and Revrse Power respectively.Unit synchronized with the system at 1648Hrs and 2256Hrs respectively as 11KV Machai-HPS line energized at 1640Hrs and system voltage stabilized. while to recent heavy rainfall and flooding, the Irrigation Department continued maintaining reduced hydrological discharge owing to the damaged Diversion Bund at Amandara Head Works. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-09 | 2025 | 9 | 9 | Malakand-3 HPS | 81 | 51 | 46.91 | 1125874 | 1116570 | 51 | 30.34 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3196404.94 | 2368683.86 | 9304 | As per available hydrology from Irrigation Department Unit # 01 & 02 are on bar while Unit # 03 kept standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-09 | 2025 | 9 | 9 | Pehur HPS | 18 | 11.98 | 11.8 | 283300 | 275000 | 21.22 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1035925 | 591419 | 8300 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-09 | 2025 | 9 | 9 | Reshun HPS | 4.2 | 2.83 | 2.15 | 50000 | 49400 | 3.06 | 3.08 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 665912 | 692872 | 600 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-09 | 2025 | 9 | 9 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-10 | 2025 | 9 | 10 | Daral Khwar HPS | 36.6 | 12 | 11 | 265070 | 262670 | 6.47 | 4.49 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2171834.36 | 5091040.36 | 2400 | Unit No.02 was on bar delivering an average load equal to 11 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-10 | 2025 | 9 | 10 | Jabori HPS | 10.2 | 7.1 | 6.31 | 151550 | 149010 | 7.72 | 4.95 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 850727.89 | 546884.27 | 2540 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-10 | 2025 | 9 | 10 | Koto HPS | 40.8 | 10.15 | 8.94 | 213500 | 211439 | 40.9 | 33.7 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1742257.36 | 6326350.64 | 2061 | Plant was operational on average load of 8.94 MW and a maximum load of 10.15 MW as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-10 | 2025 | 9 | 10 | Machai HPS | 2.6 | 1.12 | 0.97 | 23788 | 22836 | 28.6 | 18 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 106666.96 | 184803.44 | 952 | 1 The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 0436Hrs dated 10.09.2025 with Reverse power due to high system voltage . Unit synchronized with the system at 0513Hrs as system voltage stabilized. 2 The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 1504Hrs dated 10.09.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault.Unit synchronized with the system at 1530Hrs as 11KV Machai-HPS line energized at 1525Hrs. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-10 | 2025 | 9 | 10 | Malakand-3 HPS | 81 | 48 | 43.96 | 1055137 | 1045790 | 51 | 28.82 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2993783.03 | 2571305.77 | 9347 | As per available hydrology from Irrigation Department Unit # 01 & 02 are on bar while Unit # 03 kept standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-10 | 2025 | 9 | 10 | Pehur HPS | 18 | 11.97 | 11.7 | 280900 | 273000 | 21.22 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1028391 | 598953 | 7900 | Plant operational for 24 Hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-10 | 2025 | 9 | 10 | Reshun HPS | 4.2 | 3.04 | 2.17 | 53000 | 52388 | 3.26 | 3.24 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 706190.24 | 652593.76 | 612 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-10 | 2025 | 9 | 10 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-11 | 2025 | 9 | 11 | Daral Khwar HPS | 36.6 | 10.5 | 10.3 | 246610 | 244610 | 6.47 | 4.09 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2022508.86 | 5240365.86 | 2000 | Unit No.02 was on bar delivering an average load equal to 10.3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-11 | 2025 | 9 | 11 | Jabori HPS | 10.2 | 6.4 | 6 | 145142 | 142580 | 6.72 | 4.74 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 814017.74 | 583594.42 | 2562 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-11 | 2025 | 9 | 11 | Koto HPS | 40.8 | 12 | 7.68 | 163250 | 160256 | 40.9 | 26.65 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1320509.44 | 6748098.56 | 2994 | Plant was operational on average load of 7.68 MW and a maximum load of 12.00MW as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-11 | 2025 | 9 | 11 | Machai HPS | 2.6 | 1.16 | 0.9 | 22932 | 22000 | 28.6 | 22 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 102762 | 188708.4 | 932 | Maintenance Completion Report (Precautionary Shutdown) Unit Shutdown, Bearing Oil Contamination, and Restoration: Unit precautionarily shut down Summary: The unit, while on-bar delivering power to the National Grid under prevailing inflow and system conditions, was precautionarily shut down at 2258 Hrs on 11-09-2025 after water contamination was detected in the turbine guide bearing lubricating oil system. A Permit to Work (PTW) was issued, and maintenance staff from Malakand-III HPS were mobilized to carry out a comprehensive inspection and corrective maintenance of the turbine bearing assembly. Corrective Maintenance Actions Executed All repair and maintenance activities were successfully completed in full compliance with standard engineering practices, technical specifications, and quality assurance protocols: 1. Dismantling & Inspection o Turbine upper and lower guide bearing assemblies dismantled, cleaned, and visually/mechanically inspected for integrity. 2. Lubrication System Restoration o Contaminated lubricating oil fully drained from the bearing sump system. o Lubrication circuit, including supply and return lines, flushed to eliminate residual water and impurities. o Fresh turbine-grade lubricating oil, meeting viscosity and quality specifications, charged into sump tank. 3. Bearing Integrity Verification o Bearing clearances, journal surfaces, and oil film formation verified to ensure proper hydrodynamic lubrication. o Oil circulation and pressure flow paths validated under static and dynamic conditions. 4. System Readiness o All auxiliary parameters—bearing metal temperatures, oil pressures, vibration levels, and shaft alignment—confirmed within original equipment manufacturing design tolerances. Post-Maintenance Mechanical Run Test: At 1945Hrs on 12-09-2025, the unit was gradually accelerated to variable speed (“creep mode”) for mechanical run verification. Upon satisfactory inspection, the unit was transitioned to Full Speed No Load (FSNL) and held for 1 hour to conduct a heat run test and detailed mechanical observations. All monitored parameters remained stable and within acceptable limits. At 2050Hrs, the unit was synchronized with the National Grid, and load was incrementally increased in line with system demand and water discharge conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-11 | 2025 | 9 | 11 | Malakand-3 HPS | 81 | 49 | 42.64 | 1023273 | 1014160 | 51 | 28.77 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2903235.83 | 2661852.97 | 9113 | Units were tripped at 1727Hrs due to tripping of 132KV supply lines. After supply restoration Unit # 01 & Unit # 02 were synchronized at 1809Hrs & 1803Hrs respectively with the system, while Unit # 03 kept standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-11 | 2025 | 9 | 11 | Pehur HPS | 18 | 11.78 | 11.63 | 279300 | 273000 | 21.22 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1028391 | 598953 | 6300 | Plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-11 | 2025 | 9 | 11 | Reshun HPS | 4.2 | 3 | 2.19 | 50000 | 49399 | 3.08 | 3.06 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 665898.52 | 692885.48 | 601 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-11 | 2025 | 9 | 11 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.47 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-12 | 2025 | 9 | 12 | Daral Khwar HPS | 36.6 | 10.5 | 10 | 239680 | 237680 | 6.47 | 3.97 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1965209.54 | 5297665.18 | 2000 | Unit No.02 was on bar delivering an average load equal to 10 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-12 | 2025 | 9 | 12 | Jabori HPS | 10.2 | 6 | 5.89 | 141598 | 139030 | 6.72 | 4.62 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 793750.08 | 603862.08 | 2568 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-12 | 2025 | 9 | 12 | Koto HPS | 40.8 | 11.88 | 7.45 | 134999 | 134316 | 40.9 | 20.7 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1106763.84 | 6961844.16 | 683 | Plant was operational on average load of 7.45 MW and a maximum load of 11.88 MW as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-12 | 2025 | 9 | 12 | Machai HPS | 2.6 | 1.18 | 0.16 | 2768 | 2644 | 28.6 | 21 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 12350.12 | 279120.28 | 124 | Maintenance Completion Report (Precautionary Shutdown) Unit Shutdown, Bearing Oil Contamination, and Restoration: Unit precautionarily shut down Summary: The unit, while on-bar delivering power to the National Grid under prevailing inflow and system conditions, was precautionarily shut down at 2258 Hrs on 11-09-2025 after water contamination was detected in the turbine guide bearing lubricating oil system. A Permit to Work (PTW) was issued, and maintenance staff from Malakand-III HPS were mobilized to carry out a comprehensive inspection and corrective maintenance of the turbine bearing assembly. Corrective Maintenance Actions Executed All repair and maintenance activities were successfully completed in full compliance with standard engineering practices, technical specifications, and quality assurance protocols: 1. Dismantling & Inspection o Turbine upper and lower guide bearing assemblies dismantled, cleaned, and visually/mechanically inspected for integrity. 2. Lubrication System Restoration o Contaminated lubricating oil fully drained from the bearing sump system. o Lubrication circuit, including supply and return lines, flushed to eliminate residual water and impurities. o Fresh turbine-grade lubricating oil, meeting viscosity and quality specifications, charged into sump tank. 3. Bearing Integrity Verification o Bearing clearances, journal surfaces, and oil film formation verified to ensure proper hydrodynamic lubrication. o Oil circulation and pressure flow paths validated under static and dynamic conditions. 4. System Readiness o All auxiliary parameters—bearing metal temperatures, oil pressures, vibration levels, and shaft alignment—confirmed within original equipment manufacturing design tolerances. Post-Maintenance Mechanical Run Test: At 1945Hrs on 12-09-2025, the unit was gradually accelerated to variable speed (“creep mode”) for mechanical run verification. Upon satisfactory inspection, the unit was transitioned to Full Speed No Load (FSNL) and held for 1 hour to conduct a heat run test and detailed mechanical observations. All monitored parameters remained stable and within acceptable limits. At 2050Hrs, the unit was synchronized with the National Grid, and load was incrementally increased in line with system demand and water discharge conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-12 | 2025 | 9 | 12 | Malakand-3 HPS | 81 | 46 | 43.08 | 1033967 | 1024160 | 51 | 28.18 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2931862.83 | 2633225.97 | 9807 | As per available hydrology from Irrigation Department Unit # 01 & 02 are on bar while Unit # 03 kept standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-12 | 2025 | 9 | 12 | Pehur HPS | 18 | 11.86 | 11.69 | 280700 | 272000 | 21.22 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1024624 | 602720 | 8700 | Plant remained operational throughout 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-12 | 2025 | 9 | 12 | Reshun HPS | 4.2 | 3.28 | 2.3 | 73000 | 52402 | 3.26 | 3.24 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 706378.96 | 652405.04 | 20598 | outgpomg feeder breaker tripp 2times. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-12 | 2025 | 9 | 12 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-13 | 2025 | 9 | 13 | Daral Khwar HPS | 36.6 | 10.5 | 10.1 | 242040 | 239640 | 6.47 | 4.01 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1981415.41 | 5281459.31 | 2400 | Unit No 02 was on bar delivering an average load equal to 10.1 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-13 | 2025 | 9 | 13 | Jabori HPS | 10.2 | 6.7 | 4.68 | 136480 | 133900 | 6.72 | 4.46 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 764461.88 | 633150.28 | 2580 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-13 | 2025 | 9 | 13 | Koto HPS | 40.8 | 10.6 | 7.65 | 134000 | 133546 | 40.9 | 21.79 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1100419.04 | 6968188.96 | 454 | Plant was operational on average load of 7.65 MW and a maximum load of 10.60 MW as per available hydrology | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-13 | 2025 | 9 | 13 | Machai HPS | 2.6 | 1.21 | 0.91 | 23640 | 22700 | 28.6 | 20 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 106031.7 | 185438.7 | 940 | The unit, while on bar and delivering power to the National Grid as per available water inflow and prevailing system conditions, tripped at 0445Hrs,1304Hrs,1642Hrs and 2253Hrs on 13.09.2025 due to reverse power resulting from high system voltage. Subsequently, the unit remained shut down/standby and could not be synchronized with the system due to persistently high system voltage. The unit was finally synchronized with the system at 0513Hrs,1320Hrs,1821Hrs and 2309Hrs respectively, once the voltage stabilized. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-13 | 2025 | 9 | 13 | Malakand-3 HPS | 81 | 46 | 42.34 | 1016147 | 1006610 | 51 | 27.92 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2881622.45 | 2683466.35 | 9537 | As per available hydrology from Irrigation Department Unit # 01 & 02 are on bar while Unit # 03 kept standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-13 | 2025 | 9 | 13 | Pehur HPS | 18 | 11.82 | 11.7 | 280800 | 272000 | 21.22 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1024624 | 602720 | 8800 | Plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-13 | 2025 | 9 | 13 | Reshun HPS | 4.2 | 2.89 | 2.19 | 52000 | 51410 | 3.19 | 3.18 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 693006.8 | 665777.2 | 590 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-13 | 2025 | 9 | 13 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-14 | 2025 | 9 | 14 | Daral Khwar HPS | 36.6 | 10 | 9 | 216820 | 214820 | 6.47 | 3.59 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1776196.21 | 5486678.51 | 2000 | Unit No 02 was on bar delivering an average load equal to 9 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-14 | 2025 | 9 | 14 | Jabori HPS | 10.2 | 7 | 5.32 | 127680 | 125060 | 6.72 | 4.35 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 713992.55 | 683619.61 | 2620 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-14 | 2025 | 9 | 14 | Koto HPS | 40.8 | 11.27 | 7.97 | 127250 | 125671 | 40.9 | 19.53 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1035529.04 | 7033078.96 | 1579 | Plant was operational on average load of 7.97 MW and a maximum load of 11.27 MW as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-14 | 2025 | 9 | 14 | Machai HPS | 2.6 | 1.18 | 0.96 | 24240 | 23396 | 28.6 | 20 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 109282.72 | 182187.68 | 844 | The unit, while on-bar and delivering power to the National Grid under available water inflow and prevailing system conditions, tripped at 0437 Hrs and 1648 Hrs on 14-09-2025 due to the tripping of the 11 kV Machai-HPS feeder on earth fault and the 132 kV Mardan line, respectively. The 11 kV Machai-HPS feeder was re-energized at 0442 Hrs and 1657 Hrs, after which the unit was successfully synchronized with the system at 0508 Hrs and 1725 Hrs, respectively. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-14 | 2025 | 9 | 14 | Malakand-3 HPS | 81 | 45 | 42.07 | 1009726 | 1000330 | 51 | 27.64 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2863644.69 | 2701444.11 | 9396 | As per available hydrology from Irrigation Department Unit # 01 & 02 are on bar while Unit # 03 kept standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-14 | 2025 | 9 | 14 | Pehur HPS | 18 | 11.81 | 11.68 | 280200 | 273000 | 21.22 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1028391 | 598953 | 7200 | Plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-14 | 2025 | 9 | 14 | Reshun HPS | 4.2 | 3.04 | 2.38 | 57000 | 56395 | 3.5 | 3.49 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 760204.6 | 598579.4 | 605 | nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-14 | 2025 | 9 | 14 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 0 | 3 | 100 | 2.47 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-15 | 2025 | 9 | 15 | Daral Khwar HPS | 36.6 | 10 | 5.1 | 123290 | 122090 | 6.47 | 2.04 | 68 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1009476.75 | 6253397.97 | 1200 | 1. Unit No.02 was on bar delivering an average load equal to 5.1 MW according to the available hydrology. 2. 132KV supply failed at 0714 Hrs. As per RCC HT broken conductor at Chakdara reported. The PESCO maintenance team commenced the work as per PTW No.1461(10:50Hrs) on CBT SWT-3 Controlling 132KV transmission line (SWT/MATTA) Section. 3. 132 KV Supply was restored at 1721 Hrs. 4. Unit No.02 was synchronised with the national grid at 1736 Hrs. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-15 | 2025 | 9 | 15 | Jabori HPS | 10.2 | 9 | 5.4 | 129930 | 127230 | 6.72 | 4.24 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 726381.52 | 671230.64 | 2700 | Plant was operational as per available hydrology | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-15 | 2025 | 9 | 15 | Koto HPS | 40.8 | 10.68 | 6.46 | 153250 | 150844 | 40.9 | 23.14 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1242954.56 | 6825653.44 | 2406 | Not reported | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-15 | 2025 | 9 | 15 | Machai HPS | 2.6 | 1.37 | 1.15 | 29132 | 28052 | 28.6 | 23 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 131030.89 | 160439.51 | 1080 | The unit, while on-bar and delivering power to the National Grid under available water inflow and prevailing system conditions, tripped at 0449Hrs and 0751Hrs on 15-09-2025 due to the tripping of the 11 kV Machai-HPS feeder on earth fault .Unit synchronized with the system at 0530Hrs and 0823Hrs as 11 kV Machai-HPS feeder was re-energized . | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-15 | 2025 | 9 | 15 | Malakand-3 HPS | 81 | 46 | 42.46 | 1019037 | 1009060 | 51 | 27.92 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2888636.06 | 2676452.74 | 9977 | As per available hydrology from Irrigation Department Unit # 01 & 02 are on bar while Unit # 03 kept standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-15 | 2025 | 9 | 15 | Pehur HPS | 18 | 11.86 | 8.4 | 201500 | 194000 | 21.22 | 13 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 730798 | 896546 | 7500 | Plant remained shut down from 1043 hrs to 1715 hrs for search of drowned person in the canal. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-15 | 2025 | 9 | 15 | Reshun HPS | 4.2 | 3.26 | 2.22 | 51000 | 50398 | 3.14 | 3.12 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 679365.04 | 679418.96 | 602 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-15 | 2025 | 9 | 15 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-16 | 2025 | 9 | 16 | Daral Khwar HPS | 36.6 | 10 | 9.8 | 236150 | 233750 | 6.47 | 3.91 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1932715.12 | 5330159.6 | 2400 | 1: Unit No.02 was on bar delivering an average load equal to 9.8MW according to the available hydrology. 2: Unit No.02 was tripped at 16:58 Hrs due to Grid over frequency (51.18Hz). 3: Unit No.02 was synchronized with national Grid at 17:09 Hrs. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-16 | 2025 | 9 | 16 | Jabori HPS | 10.2 | 7 | 5.77 | 138660 | 136080 | 6.72 | 4.53 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 776907.94 | 620704.22 | 2580 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-16 | 2025 | 9 | 16 | Koto HPS | 40.8 | 13.82 | 11.36 | 274250 | 272048 | 40.9 | 33.19 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 2241675.52 | 5826932.48 | 2202 | The plant was operational on average load of 11.36 and maximum load of 13.82 | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-16 | 2025 | 9 | 16 | Machai HPS | 2.6 | 1.2 | 0.17 | 3150 | 2900 | 28.6 | 22 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 13545.9 | 277924.5 | 250 | Tripping Report – Tripping of Unit due to Earth Fault and Instantaneous Fault (Adverse Weather Conditions) The unit, while on-bar and delivering power to the National Grid under available water inflow and system conditions, tripped at 0322Hrs on 16-09-2025. The tripping occurred due to a fault on the 11 kV Machai-HPS feeder, which experienced both earth fault and instantaneous fault conditions, attributed to a heavy windstorm and rainfall. An inquiry call was made to Katlang Grid regarding the tripping and possible restoration. As per their response, the line could not be restored due to the persistence of the fault. The issue was immediately communicated to the PESCO operation staff. The LS-Operation, PESCO (Katlang) was contacted and requested to take prompt action for feeder energization. However, no field team was dispatched by PESCO to clear the fault. Consequently, PEDO staff initiated line patrolling along the 11 kV Machai-HPS feeder to locate and assess the fault. Field updates confirmed that two HT poles had collapsed and three others were bent, which hindered fault rectification and restoration. The matter was formally reported to the SDO-Operation (PESCO) and XEN Construction (PESCO), with a request to urgently replace the damaged poles to enable feeder energization at the earliest possible time. As of this report, the unit has remained on standby since 0322Hrs on 16-09-2025 due to the persisting feeder fault on the 11 kV Machai-HPS line. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-16 | 2025 | 9 | 16 | Malakand-3 HPS | 81 | 51 | 44.54 | 1069035 | 1059180 | 51 | 29.3 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3032114.59 | 2532974.21 | 9855 | As per available hydrology from Irrigation Department Unit # 01 & 02 are on bar while Unit # 03 kept standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-16 | 2025 | 9 | 16 | Pehur HPS | 18 | 11.89 | 11.71 | 281100 | 274000 | 21.22 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1032158 | 595186 | 7100 | Plant remained operational through out 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-16 | 2025 | 9 | 16 | Reshun HPS | 4.2 | 3.08 | 2 | 43000 | 42404 | 2.66 | 2.63 | 87.67 | 13.48 | 88.5 | 45 | 89208 | 1202523.84 | 571605.92 | 630917.92 | 596 | outgoing breaker tripped 7times due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-16 | 2025 | 9 | 16 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-17 | 2025 | 9 | 17 | Daral Khwar HPS | 36.6 | 10 | 9.3 | 223150 | 221150 | 6.47 | 3.7 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1828534.54 | 5434340.18 | 2000 | Unit No.02 was on bar delivering an average load equal to 9.3 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-17 | 2025 | 9 | 17 | Jabori HPS | 10.2 | 6.1 | 5.32 | 127780 | 125200 | 6.72 | 4.18 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 714791.84 | 682820.32 | 2580 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-17 | 2025 | 9 | 17 | Koto HPS | 40.8 | 13.65 | 11.56 | 276250 | 274847 | 40.9 | 34.38 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 2264739.28 | 5803868.72 | 1403 | The plant was operational on average load 11.56MW and maximum load of 13.65MW | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-17 | 2025 | 9 | 17 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 28.6 | 22 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Tripping Report – Tripping of Unit due to Feeder Fault (Adverse Weather Conditions) 1. Incident Summary On 16-09-2025 at 0322 Hrs, the unit, while on-bar and delivering power to the National Grid under available water inflow and system conditions, tripped due to earth fault and instantaneous fault on the 11 kV Machai-HPS feeder, attributed to a heavy windstorm and rainfall. 2. Grid Communication An inquiry with Katlang Grid confirmed that restoration was not possible as the fault persisted. Despite repeated requests to PESCO Operation staff (Katlang), no field team was dispatched to clear the fault. 3. Field Observations PEDO staff initiated patrolling along the 11 kV Machai-HPS feeder and identified two HT poles collapsed and three bent, which prevented immediate restoration. 4. Escalation The matter was formally escalated to the SDO-Operation (PESCO) and XEN Construction, with a request for urgent replacement of the damaged poles to enable feeder energization at the earliest possible time. 5. Current Status As of this report, the unit has remained on standby since 0322 Hrs on 16-09-2025 awaiting rectification of the feeder fault. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-17 | 2025 | 9 | 17 | Malakand-3 HPS | 81 | 45 | 42.88 | 1029007 | 1019590 | 51 | 28.29 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2918780.29 | 2646308.51 | 9417 | As per available hydrology from Irrigation Department Unit # 01 & 02 are on bar while Unit # 03 kept standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-17 | 2025 | 9 | 17 | Pehur HPS | 18 | 11.81 | 11.57 | 277700 | 269000 | 21.22 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1013323 | 614021 | 8700 | plant remained operational throughout 24 hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-17 | 2025 | 9 | 17 | Reshun HPS | 4.2 | 2.89 | 2.12 | 50000 | 49330 | 3.08 | 3.06 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 664968.4 | 693815.6 | 670 | outgoing feeder breaker tripped 4times due to line faults | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-17 | 2025 | 9 | 17 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | No data submitted for this date | ibrarahmadmkd@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-09-18 | 2025 | 9 | 18 | Daral Khwar HPS | 36.6 | 17 | 11.5 | 276820 | 274420 | 6.47 | 4.59 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2268986.89 | 4993887.83 | 2400 | 1. Unit No.01 and 02 were on bar delivering an average load equal to 11.5 MW according to the available hydrology. 2. Unit#01 was synchronised with national grid at 1638 Hrs due to increased hydrology. 3. Unit#01 was shutdown at 2140 Hrs due to low hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-18 | 2025 | 9 | 18 | Jabori HPS | 10.2 | 6.5 | 5.46 | 131060 | 128460 | 6.72 | 4.28 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 733403.83 | 664208.33 | 2600 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-18 | 2025 | 9 | 18 | Koto HPS | 40.8 | 13.45 | 10.75 | 235750 | 234507 | 40.9 | 29.65 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1932337.68 | 6136270.32 | 1243 | The plant was operational on average load 10.753 and maximum load of 13.45 as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-18 | 2025 | 9 | 18 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 28.6 | 22 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Report – Tripping of Unit due to Feeder Fault (Adverse Weather Conditions) 1. Incident Summary On 16-09-2025 at 0322 Hrs, the unit, while on-bar and delivering power to the National Grid under available water inflow and system conditions, tripped due to earth fault and instantaneous fault on the 11 kV Machai-HPS feeder, attributed to a heavy windstorm and rainfall. 2. Grid Communication An inquiry with Katlang Grid confirmed that restoration was not possible as the fault persisted. Despite repeated requests to PESCO Operation staff (Katlang), no field team was dispatched to clear the fault. 3. Field Observations PEDO staff initiated patrolling along the 11 kV Machai-HPS feeder and identified two HT poles collapsed and three bent, which prevented immediate restoration. 4. Escalation The matter was formally escalated to the SDO-Operation (PESCO) and XEN Construction, with a request for urgent replacement of the damaged poles to enable feeder energization at the earliest possible time. 5. Current Status As of this report, the unit has remained on standby since 0322 Hrs on 16-09-2025 awaiting rectification of the feeder fault. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-18 | 2025 | 9 | 18 | Malakand-3 HPS | 81 | 44 | 40.98 | 983510 | 975130 | 51 | 27.02 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2791504.65 | 2773584.15 | 8380 | As per available hydrology from Irrigation Department Unit # 01 & 02 are on bar while Unit # 03 kept standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-18 | 2025 | 9 | 18 | Pehur HPS | 18 | 11.68 | 4.6 | 110500 | 106000 | 21.22 | 7 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 399302 | 1228042 | 4500 | Unit# 01 & 02 were taken off the bar at 0952 & 0939 Hrs upon the request of irrigation SDO due to chocking of trash gates and nil irrigation demand due to heavy rainfall. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-18 | 2025 | 9 | 18 | Reshun HPS | 4.2 | 2.84 | 1.69 | 39000 | 38400 | 2.4 | 2.39 | 79.57 | 13.48 | 79.93 | 45 | 80572.8 | 1086121.34 | 517632 | 568489.34 | 600 | outgoing feeder breaker tripped 10times due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-18 | 2025 | 9 | 18 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-19 | 2025 | 9 | 19 | Daral Khwar HPS | 36.6 | 13 | 11 | 264270 | 262270 | 6.47 | 4.39 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2168527.04 | 5094347.68 | 2000 | Unit No.02 was on bar delivering an average load equal to 11 MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-19 | 2025 | 9 | 19 | Jabori HPS | 10.2 | 6.1 | 5.1 | 123310 | 120780 | 6.72 | 4 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 689557.18 | 708054.98 | 2530 | Plant was operational as per available hydrology | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-19 | 2025 | 9 | 19 | Karora HPS | 11.8 | 5.9 | 5.83 | 134759 | 132906 | 6.4 | 4.42 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1034008.68 | 1169287.32 | 1853 | 1.Unit 2 is currently generating at its full capacity of 5.9 MW, while Unit No.1 is remains on standby primarily due to the community’s resistance to complete water diversion and indequte hydrology. 2.The locals have allowed only partial flow for testing purposes and have conditioned their full consent upon the completion of PESCO’s electrification scheme for the three Union Councils. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-19 | 2025 | 9 | 19 | Koto HPS | 40.8 | 16.98 | 12.64 | 299200 | 298366 | 40.9 | 38.47 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 2458535.84 | 5610072.16 | 834 | The plant was operational on average load of 12.64MW and maximum load of 16.98MW | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-19 | 2025 | 9 | 19 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 28.6 | 21 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0322Hrs on 16-09-2025 awaiting rectification of the feeder fault. However, water will diverted by the Irrigation Department at 0500Hrs on 20-09-2025 from Machai Canal to Aba Zai Canal, as per notification of the Executive Engineer (Irrigation Department) that the rotational turn will be made operational due to low supply in the Swat River | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-09-19 | 2025 | 9 | 19 | Malakand-3 HPS | 81 | 45 | 40.22 | 965297 | 957050 | 51 | 27.2 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2739747.04 | 2825341.76 | 8247 | As per available hydrology from Irrigation Department Unit # 01 & 02 are on bar while Unit # 03 kept standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-19 | 2025 | 9 | 19 | Pehur HPS | 18 | 12.1 | 6.29 | 151000 | 148000 | 21.22 | 9.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 557516 | 1069828 | 3000 | Unit# 01 & 02 were taken on bar at 1045 & 1030 Hrs after receiving a message from irrigation SDO to release 20 cms discharge in the canal after cleaning the trash gates. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-19 | 2025 | 9 | 19 | Reshun HPS | 4.2 | 3.08 | 1.96 | 47000 | 46397 | 2.91 | 2.88 | 95.9 | 13.48 | 96.9 | 45 | 97675.2 | 1316661.7 | 625431.56 | 691230.14 | 603 | outgoing feeder breaker tripped 4times due to lines faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-19 | 2025 | 9 | 19 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-20 | 2025 | 9 | 20 | Daral Khwar HPS | 36.6 | 9.5 | 9.3 | 222610 | 220610 | 6.47 | 3.69 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1824069.66 | 5438805.06 | 2000 | Unit No 02 was on bar delivering an average load equal to 9.3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-20 | 2025 | 9 | 20 | Jabori HPS | 10.2 | 6 | 5.03 | 120720 | 118240 | 6.72 | 3.95 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 675055.81 | 722556.35 | 2480 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-20 | 2025 | 9 | 20 | Karora HPS | 11.8 | 5.96 | 5.9 | 113907 | 112291 | 6.5 | 4.42 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 873623.98 | 1329672.02 | 1616 | At 1046 hrs Unit#2 was smoothly shut down by E&M contractor for punchlist clearance . At 1502 hrs unit#2 was started and synchronized with the system. unit No. 2 is running on full load 5.9 \mw while Unit No.1 is remains on standby primarily due to the community’s resistance to complete water diversion and indequte hydrology. 2.The locals have allowed only partial flow for testing purposes and have conditioned their full consent upon the completion of PESCO’s electrification scheme for the three Union Councils. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-20 | 2025 | 9 | 20 | Koto HPS | 40.8 | 10.83 | 9.86 | 238250 | 235842 | 40.9 | 33.17 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1943338.08 | 6125269.92 | 2408 | The plant was operational on average load of 9.86MW and maximum load of 10.83 MW | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-20 | 2025 | 9 | 20 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 28.6 | 8 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0322Hrs on 16-09-2025 awaiting rectification of the feeder fault. However, water was diverted by the Irrigation Department at 0500Hrs on 20-09-2025 from Machai Canal to Aba Zai Canal, as per notification of the Executive Engineer (Irrigation Department) that the rotational turn will be made operational due to low supply in the Swat River | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-20 | 2025 | 9 | 20 | Malakand-3 HPS | 81 | 35 | 30.12 | 722854 | 714630 | 51 | 21.48 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2045771.3 | 3519317.5 | 8224 | As per available hydrology from Irrigation Department Unit # 01 & 02 are on bar while Unit # 03 kept standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-20 | 2025 | 9 | 20 | Pehur HPS | 18 | 12.02 | 11.64 | 279300 | 272000 | 21.22 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1024624 | 602720 | 7300 | The plant remained operational throughout 24 hours as per available hydrology, and the irrigation valve being is open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-20 | 2025 | 9 | 20 | Reshun HPS | 4.2 | 3.27 | 2.03 | 48000 | 47388 | 2.95 | 2.93 | 97.67 | 13.48 | 98.2 | 45 | 98985.6 | 1334325.89 | 638790.24 | 695535.65 | 612 | nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-20 | 2025 | 9 | 20 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-21 | 2025 | 9 | 21 | Daral Khwar HPS | 36.6 | 8.7 | 8.4 | 200960 | 198560 | 6.47 | 3.32 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1641753.65 | 5621121.07 | 2400 | Unit No 02 was on bar delivering an average load equal to 8.4 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-21 | 2025 | 9 | 21 | Jabori HPS | 10.2 | 5.1 | 4.9 | 117660 | 115130 | 6.72 | 3.85 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 657300.2 | 740311.96 | 2530 | Plant was operational as per available hydrology | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-21 | 2025 | 9 | 21 | Karora HPS | 11.8 | 8.1 | 5.82 | 142043 | 139766 | 5.7 | 4.49 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1087379.48 | 1115916.52 | 2277 | Unit 2 is currently generating at its full capacity of 5.9 MW, while Unit No.1 is remains on standby primarily due to the community’s resistance to complete water diversion and indequte hydrology. 2.UnitNo.1 was started at 10:08 hrs and synchronized with grid. At 13:36 shutdown due to low hydrology 3.The locals have allowed only partial flow for testing purposes and have conditioned their full consent upon the completion of PESCO’s electrification scheme for the three Union Councils. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-21 | 2025 | 9 | 21 | Koto HPS | 40.8 | 8.9 | 8.25 | 197500 | 195319 | 40.9 | 29.88 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1609428.56 | 6459179.44 | 2181 | The plant was operational on average 8.25 and maximum load of 8.9 due to available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-21 | 2025 | 9 | 21 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 28.6 | 9 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0322Hrs on 16-09-2025 awaiting rectification of the feeder fault. However, water was diverted by the Irrigation Department at 0500Hrs on 20-09-2025 from Machai Canal to Aba Zai Canal, as per notification of the Executive Engineer (Irrigation Department) that the rotational turn will be made operational due to low supply in the Swat River. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-21 | 2025 | 9 | 21 | Malakand-3 HPS | 81 | 28 | 26.78 | 642737 | 634540 | 51 | 19.65 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1816497.66 | 3748591.14 | 8197 | As per available hydrology from Irrigation Department Unit # 01 & 02 are on bar while Unit # 03 kept standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-21 | 2025 | 9 | 21 | Pehur HPS | 18 | 11.5 | 11.6 | 279300 | 272000 | 21.22 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1024624 | 602720 | 7300 | Plant remained operational through out 24 Hrs as per available hydrology + Irrigation valve is open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-21 | 2025 | 9 | 21 | Reshun HPS | 4.2 | 3.14 | 2.26 | 55000 | 54380 | 3.38 | 3.37 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 733042.4 | 625741.6 | 620 | nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-21 | 2025 | 9 | 21 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-22 | 2025 | 9 | 22 | Daral Khwar HPS | 36.6 | 8.7 | 8.3 | 199150 | 196750 | 6.47 | 3.29 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1626788.02 | 5636086.7 | 2400 | Unit No 02 was on bar delivering an average load equal to 8.3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-22 | 2025 | 9 | 22 | Jabori HPS | 10.2 | 5.1 | 4.75 | 113990 | 111390 | 5.83 | 3.73 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 635947.79 | 761664.37 | 2600 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-22 | 2025 | 9 | 22 | Karora HPS | 11.8 | 5.93 | 3.91 | 104990 | 103336 | 5.7 | 3.29 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 803954.08 | 1399341.92 | 1654 | 1.Unit 2 is currently generating at its full capacity of 5.84 MW, while Unit No.1 is remains on standby primarily due to the community’s resistance to complete water diversion and indequte hydrology. 2.The locals have allowed only partial flow for testing purposes and have conditioned their full consent upon the completion of PESCO’s electrification scheme for the three Union Councils. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-22 | 2025 | 9 | 22 | Koto HPS | 40.8 | 8.4 | 7.32 | 175250 | 173793 | 40.9 | 27.37 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1432054.32 | 6636553.68 | 1457 | The plant was operational on average load of 7.32 MW and a maximum load of 8.40 MW as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-22 | 2025 | 9 | 22 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 28.6 | 8 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0322Hrs on 16-09-2025 awaiting rectification of the feeder fault. However, water was diverted by the Irrigation Department at 0500Hrs on 20-09-2025 from Machai Canal to Aba Zai Canal, as per notification of the Executive Engineer (Irrigation Department) that the rotational turn will be made operational due to low supply in the Swat River. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-22 | 2025 | 9 | 22 | Malakand-3 HPS | 81 | 30 | 27.2 | 652813 | 644130 | 51 | 19.87 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1843950.95 | 3721137.85 | 8683 | As per available hydrology from Irrigation Department Unit # 02 & 03 are on bar while Unit # 01 kept standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-22 | 2025 | 9 | 22 | Pehur HPS | 18 | 11.86 | 11.56 | 277500 | 269000 | 21.22 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1013323 | 614021 | 8500 | Plant remained operational through out 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-22 | 2025 | 9 | 22 | Reshun HPS | 4.2 | 3.41 | 2.08 | 47000 | 46404 | 2.89 | 2.88 | 95.9 | 13.48 | 96.33 | 45 | 97104 | 1308961.92 | 625525.92 | 683436 | 596 | outgoing feeder breaker tripped 2times due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-22 | 2025 | 9 | 22 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-23 | 2025 | 9 | 23 | Daral Khwar HPS | 36.6 | 8.5 | 8.1 | 193960 | 191960 | 6.47 | 3.21 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1587182.87 | 5675691.85 | 2000 | Unit No 02 was on bar delivering an average load equal to 8.1 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-23 | 2025 | 9 | 23 | Jabori HPS | 10.2 | 4.7 | 4.56 | 109467 | 106880 | 5.83 | 3.57 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 610199.3 | 787412.86 | 2587 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-23 | 2025 | 9 | 23 | Karora HPS | 11.8 | 6 | 5.02 | 123771 | 120993 | 5.6 | 4.06 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 941325.54 | 1261970.46 | 2778 | 1.Unit 2 is currently generating at its full capacity of 5.96 MW, while Unit No.1 is remains on standby primarily due to the community’s resistance to complete water diversion and indequte hydrology. 2.The locals have allowed only partial flow for testing purposes and have conditioned their full consent upon the completion of PESCO’s electrification scheme for the three Union Councils. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-23 | 2025 | 9 | 23 | Koto HPS | 40.8 | 12.02 | 4.95 | 123250 | 122317 | 40.9 | 19.6 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1007892.08 | 7060715.92 | 933 | The plant shutdown due to Less Hydrology at 7.50 AM . And then subsequently for the cleaning of intake trash racks. Plant resynchronized with grid at 15:15 . | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-23 | 2025 | 9 | 23 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 28.6 | 4 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0322Hrs on 16-09-2025, awaiting rectification of the feeder fault while repair work is in progress. However, at 0500Hrs on 20-09-2025, water was diverted by the Irrigation Department from Machai Canal to Aba Zai Canal, as per the notification of the Executive Engineer (Irrigation Department), stating that the rotational turn was to be made operational due to low water supply in the Swat River. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-23 | 2025 | 9 | 23 | Malakand-3 HPS | 81 | 31 | 17.32 | 415770 | 410100 | 51 | 14.5 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1173993.27 | 4391095.53 | 5670 | Due to the recent flood in Upper Swat, the diversion bund at Amandara Headworks was completely washed away. For its reconstruction, the Irrigation Department reduced the water supply at 11:30 a.m. on 23-09-2025, as per their Letter CW No. 65. The letter stated that, owing to high supply pressure, the Excavator was facing difficulty in diverting the supply at Amandara Headworks; therefore, the supply from AT Works had to be reduced, resulting in a shortage in the main canal, and it will not be restored until completion of the work. Consequently, Unit #03 was desynchronized from the system at 13:02 hrs due to decreasing hydrology at the Forebay. Subsequently, with a further reduction in hydrology, Unit #02 was also desynchronized from the system at 15:15 hrs on the same date. Although all three units remain available for generation, due to reduced water supply for bund construction at Amandara Headworks, the required flow is not available; therefore, the units have been kept on standby. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-23 | 2025 | 9 | 23 | Pehur HPS | 18 | 11.92 | 11.74 | 281800 | 274000 | 21.22 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1032158 | 595186 | 7800 | Plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-23 | 2025 | 9 | 23 | Reshun HPS | 4.2 | 3.03 | 1.96 | 44000 | 43480 | 2.71 | 2.69 | 89.77 | 13.48 | 90.27 | 45 | 90988.8 | 1226529.02 | 586110.4 | 640418.62 | 520 | Line faults Mulkhow and Torkhow areas. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-23 | 2025 | 9 | 23 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-24 | 2025 | 9 | 24 | Daral Khwar HPS | 36.6 | 8.8 | 8 | 193150 | 190750 | 6.47 | 3.19 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1577178.22 | 5685696.5 | 2400 | Unit No 02 was on bar delivering an average load equal to 8 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-24 | 2025 | 9 | 24 | Jabori HPS | 10.2 | 4.6 | 4.5 | 108099 | 105500 | 5.83 | 3.53 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 602320.6 | 795291.56 | 2599 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-24 | 2025 | 9 | 24 | Karora HPS | 11.8 | 5.99 | 4 | 101952 | 99583 | 5.7 | 3.33 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 774755.74 | 1428540.26 | 2369 | Unit #1 remained under shutdown condition due to ongoing punch list clearance activities being carried out by the E&M contractor. At 12:00 hrs, Unit #2 was also taken out of service. The contractor team initiated work related to governor speed control adjustments from the LCUs. During the course of the activity, both units were started and shut down multiple times for testing and verification purposes. Finally, at 17:11 hrs, Unit #2 was successfully started and synchronized with the grid. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-24 | 2025 | 9 | 24 | Koto HPS | 40.8 | 11.43 | 6.55 | 156250 | 153691 | 40.9 | 27.28 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1266413.84 | 6802194.16 | 2559 | The plant was operational on average load of 6.55 MW and a maximum load 11.43MW due to low Hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-24 | 2025 | 9 | 24 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 28.6 | 4 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0322Hrs on 16-09-2025, awaiting rectification of the feeder fault while repair work is in progress. However, at 0500Hrs on 20-09-2025, water was diverted by the Irrigation Department from Machai Canal to Aba Zai Canal, as per the notification of the Executive Engineer (Irrigation Department), stating that the rotational turn was to be made operational due to low water supply in the Swat River. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-09-24 | 2025 | 9 | 24 | Malakand-3 HPS | 81 | 25 | 8.64 | 207468 | 202690 | 51 | 7.2 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 580240.66 | 4984848.14 | 4778 | Due to the recent flood in Upper Swat, the diversion bund at Amandara Headworks was completely washed away. For its reconstruction, the Irrigation Department reduced the water supply at 11:30 a.m. on 23-09-2025, as per Letter CW No. 65. As per available hydrology Unit # 03 is on bar while Unit # 01 & 02 kept stand by due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-24 | 2025 | 9 | 24 | Pehur HPS | 18 | 11.8 | 11.6 | 277800 | 270000 | 21.22 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1017090 | 610254 | 7800 | The plant remained operational throughout24 hours as per available hydrology, and the irrigation valve is open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-24 | 2025 | 9 | 24 | Reshun HPS | 4.2 | 2.63 | 1.8 | 41000 | 40420 | 2.53 | 2.51 | 83.67 | 13.48 | 84.2 | 45 | 84873.6 | 1144096.13 | 544861.6 | 599234.53 | 580 | outgoing feeder breaker tripped 6times due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-24 | 2025 | 9 | 24 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-25 | 2025 | 9 | 25 | Daral Khwar HPS | 36.6 | 15 | 9.9 | 236960 | 234560 | 6.47 | 3.92 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1939412.45 | 5323462.27 | 2400 | Unit No 02 was on bar delivering an average load equal to 9.9 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-25 | 2025 | 9 | 25 | Jabori HPS | 10.2 | 5.1 | 4.53 | 108723 | 106120 | 5.8 | 3.55 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 605860.3 | 791751.86 | 2603 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-25 | 2025 | 9 | 25 | Karora HPS | 11.8 | 5.9 | 3.3 | 86001 | 84176 | 4.59 | 2.71 | 90.33 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 654889.28 | 1548406.72 | 1825 | Unit#01 remain on bar delivering power to the system as per available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-25 | 2025 | 9 | 25 | Koto HPS | 40.8 | 13.73 | 5.73 | 140250 | 139698 | 40.9 | 17.32 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1151111.52 | 6917496.48 | 552 | The plant was operational on average load 5.73 MW and a maximum load 13.73 due to low Hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-25 | 2025 | 9 | 25 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 28.6 | 8 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0322Hrs on 16-09-2025, awaiting rectification of the feeder fault while repair work is in progress. However, at 0500Hrs on 20-09-2025, water was diverted by the Irrigation Department from Machai Canal to Aba Zai Canal, as per the notification of the Executive Engineer (Irrigation Department), stating that the rotational turn was to be made operational due to low water supply in the Swat River. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-09-25 | 2025 | 9 | 25 | Malakand-3 HPS | 81 | 66 | 41.59 | 998157 | 988870 | 51 | 28.17 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2830838.15 | 2734250.65 | 9287 | As per available hydrology from Irrigation Department all three units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-25 | 2025 | 9 | 25 | Pehur HPS | 18 | 12.05 | 11.57 | 277700 | 271000 | 21.22 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1020857 | 606487 | 6700 | The plant remained operational throughout 24 hours as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-25 | 2025 | 9 | 25 | Reshun HPS | 4.2 | 2.93 | 1.72 | 38000 | 37306 | 2.34 | 2.33 | 77.53 | 13.48 | 78 | 45 | 78624 | 1059851.52 | 502884.88 | 556966.64 | 694 | outgoing feeder breaker tripped 7times due to line fault at Mulkhow areas. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-25 | 2025 | 9 | 25 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-26 | 2025 | 9 | 26 | Daral Khwar HPS | 36.6 | 10.5 | 8.6 | 207480 | 205080 | 6.47 | 3.43 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1695662.96 | 5567211.76 | 2400 | Unit No 02 was on bar delivering an average load equal to 8.6 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-26 | 2025 | 9 | 26 | Jabori HPS | 10.2 | 5 | 4.46 | 107215 | 14680 | 5.83 | 3.5 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 83811.06 | 1313801.1 | 92535 | Plant was operational as per available hydrology | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-26 | 2025 | 9 | 26 | Karora HPS | 11.8 | 6.9 | 4.3 | 111973 | 110194 | 4.59 | 3.83 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 857309.32 | 1345986.68 | 1779 | Unit#02 remain on bar delivering power to the system as per available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-26 | 2025 | 9 | 26 | Koto HPS | 40.8 | 13.5 | 10.56 | 250000 | 247008 | 40.9 | 31.4 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 2035345.92 | 6033262.08 | 2992 | The plant was operational on average load 10.56 MW and a maximum load of 13.50 MW due to low Hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-26 | 2025 | 9 | 26 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 28.6 | 7 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0322Hrs on 16-09-2025, awaiting rectification of the feeder fault while repair work is in progress. However, at 0500Hrs on 20-09-2025, water was diverted by the Irrigation Department from Machai Canal to Aba Zai Canal, as per the notification of the Executive Engineer (Irrigation Department), stating that the rotational turn was to be made operational due to low water supply in the Swat River. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-09-26 | 2025 | 9 | 26 | Malakand-3 HPS | 81 | 63 | 55.86 | 1340656 | 1331210 | 51 | 36.67 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3810854.87 | 1754233.93 | 9446 | As per available hydrology from Irrigation Department all three units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-26 | 2025 | 9 | 26 | Pehur HPS | 18 | 12.04 | 11.71 | 281000 | 274000 | 21.22 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1032158 | 595186 | 7000 | Plant remained operational through out 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-26 | 2025 | 9 | 26 | Reshun HPS | 4.2 | 3.42 | 2.17 | 51000 | 50360 | 3.14 | 3.12 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 678852.8 | 679931.2 | 640 | nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-26 | 2025 | 9 | 26 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.47 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-27 | 2025 | 9 | 27 | Daral Khwar HPS | 36.6 | 8.2 | 7.6 | 183070 | 181070 | 6.47 | 3.03 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1497141.08 | 5765733.64 | 2000 | Unit No 02 was on bar delivering an average load equal to 7.6 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-27 | 2025 | 9 | 27 | Jabori HPS | 10.2 | 4.3 | 4 | 98143 | 96070 | 5.86 | 3.2 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 548482.84 | 849129.32 | 2073 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-09-27 | 2025 | 9 | 27 | Karora HPS | 11.8 | 5.9 | 5.79 | 130604 | 128901 | 4.59 | 4.32 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1002849.78 | 1200446.22 | 1703 | Unit#02 Remain on bar delivering power to the system as per available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-27 | 2025 | 9 | 27 | Koto HPS | 40.8 | 8.45 | 7.53 | 180750 | 179568 | 40.9 | 26.78 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1479640.32 | 6588967.68 | 1182 | The plant was operational on average load of 7.53 and a maximum load of 8.45 as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-27 | 2025 | 9 | 27 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 28.6 | 7 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The 11 kV Machai-HPS feeder was re-energized at 1900Hrs on 27-09-2025 after clearance of the fault, during which two HT poles were replaced and additional necessary repair works were carried out. However, the Unit was not started and remains on standby due to low hydrology, as canal water was diverted by the Irrigation Department in accordance with the weekly canal closure schedule. The Unit will be recommissioned once sufficient inflow is restored by the Irrigation Department. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-09-27 | 2025 | 9 | 27 | Malakand-3 HPS | 81 | 55 | 50.61 | 1214547 | 1205330 | 51 | 34.53 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3450498.19 | 2114590.61 | 9217 | As per available hydrology from Irrigation Department all three units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-27 | 2025 | 9 | 27 | Pehur HPS | 18 | 11.83 | 11.66 | 279900 | 272000 | 21.22 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1024624 | 602720 | 7900 | Plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-27 | 2025 | 9 | 27 | Reshun HPS | 4.2 | 3.3 | 2.05 | 49000 | 48395 | 3.01 | 3 | 99.97 | 13.48 | 100 | 45 | 100800 | 1358784 | 652364.6 | 706419.4 | 605 | nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-27 | 2025 | 9 | 27 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-28 | 2025 | 9 | 28 | Daral Khwar HPS | 36.6 | 7.7 | 7.3 | 174170 | 172170 | 6.47 | 2.88 | 96 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1423553.21 | 5839321.51 | 2000 | Unit No 02 was on bar delivering an average load equal to 7.3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-28 | 2025 | 9 | 28 | Jabori HPS | 10.2 | 4 | 3.95 | 94821 | 93270 | 5.9 | 3 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 532497.08 | 865115.08 | 1551 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-09-28 | 2025 | 9 | 28 | Karora HPS | 11.8 | 6 | 5.8 | 137309 | 135574 | 4.5 | 4.33 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1054765.72 | 1148530.28 | 1735 | Only Unit no 02 is on bus bar as per available hydrology. While unit no 01 remain shutdown due contractor working on punch list issue resolving. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-28 | 2025 | 9 | 28 | Koto HPS | 40.8 | 11.57 | 5.99 | 136000 | 134629 | 40.9 | 25.78 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1109342.96 | 6959265.04 | 1371 | The Plant was operational on average load of 5.99 MW and a maximum load of 11.57 as per available hydrology | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-28 | 2025 | 9 | 28 | Machai HPS | 2.6 | 0.58 | 0.35 | 6706 | 6346 | 26.8 | 16 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 29642.17 | 261828.23 | 360 | The Unit, after completion of all preliminary checks, was started at 1330 Hrs on 28-09-2025 following restoration of the rated head due to increased canal discharge, as per Irrigation Department notification (C.W No. 813-7, dated 28-09-2025, issued by SDO Dargai to all concerned). The Unit was initially maintained at Full Speed No Load (FSNL) for inspection, and upon confirming that all parameters were normal, it was synchronized with the system at 1400Hrs. Thereafter, load was gradually increased in accordance with available inflow and prevailing system conditions | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-28 | 2025 | 9 | 28 | Malakand-3 HPS | 81 | 56 | 51.99 | 1247871 | 1238740 | 51 | 35.22 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3546141 | 2018947.8 | 9131 | As per available hydrology from Irrigation Department all three units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-28 | 2025 | 9 | 28 | Pehur HPS | 18 | 11.68 | 11.6 | 278300 | 270000 | 21.22 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1017090 | 610254 | 8300 | Plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-28 | 2025 | 9 | 28 | Reshun HPS | 4.2 | 3.3 | 2.36 | 53000 | 52464 | 3.25 | 3.24 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 707214.72 | 651569.28 | 536 | less hydrology | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-28 | 2025 | 9 | 28 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-29 | 2025 | 9 | 29 | Daral Khwar HPS | 36.6 | 7.5 | 7.2 | 173430 | 171030 | 6.47 | 2.86 | 95.33 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1414127.35 | 5848747.37 | 2400 | Unit No 02 was on bar delivering an average load equal to 7.2 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-29 | 2025 | 9 | 29 | Jabori HPS | 10.2 | 4.1 | 3.83 | 92157 | 90600 | 5.93 | 3 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 517253.52 | 880358.64 | 1557 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-29 | 2025 | 9 | 29 | Karora HPS | 11.8 | 6 | 5.42 | 126341 | 124715 | 4.59 | 4.06 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 970282.7 | 1233013.3 | 1626 | Unit no 01 is shut downed due to contractor working on punch list issues .Unit 02 is operational but has been shut downed several times by contractor for clearing punch list issues. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-29 | 2025 | 9 | 29 | Koto HPS | 40.8 | 10.32 | 8.05 | 118500 | 117816 | 40.9 | 19.16 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 970803.84 | 7097804.16 | 684 | Plant was operational on average load of 5.08 MW And a maximum load of 10.32MW As per available hydrology | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-29 | 2025 | 9 | 29 | Machai HPS | 2.6 | 0.65 | 0.48 | 11040 | 10428 | 28.6 | 20 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 48709.19 | 242761.21 | 612 | The unit, while on bar and delivering power to the National Grid as per available water inflow and prevailing system conditions, tripped at 0205Hrs,0344Hrs,0654Hrs,1559Hrs and 2136Hrs on 29.09.2025 due to reverse power resulting from high system voltage. Subsequently, the unit remained shut down/standby and could not be synchronized with the system due to persistently high system voltage. The unit was finally synchronized with the system at 0214Hrs,0459Hrs,0658Hrs,1610Hrs and 2156Hrs once the voltage stabilized. The load could not be increased in accordance with the available inflow due to high system voltage, which led to elevated stator temperatures. The unit remained synchronized, delivering power to the National Grid as per system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-29 | 2025 | 9 | 29 | Malakand-3 HPS | 81 | 54 | 51.34 | 1232228 | 1222720 | 51 | 34.66 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3500280.54 | 2064808.26 | 9508 | As per available hydrology from Irrigation Department all three units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-29 | 2025 | 9 | 29 | Pehur HPS | 18 | 11.95 | 11.52 | 276600 | 270000 | 21.22 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1017090 | 610254 | 6600 | Plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-29 | 2025 | 9 | 29 | Reshun HPS | 4.2 | 3.54 | 2.1 | 49000 | 48428 | 3.01 | 3 | 99.97 | 13.48 | 100 | 45 | 100800 | 1358784 | 652809.44 | 705974.56 | 572 | outgoing feeder breaker tripped 2times due to lines faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-29 | 2025 | 9 | 29 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-30 | 2025 | 9 | 30 | Daral Khwar HPS | 36.6 | 7 | 6.9 | 165850 | 163450 | 6.47 | 2.73 | 91 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1351453.64 | 5911421.08 | 2400 | Unit No 02 was on bar delivering an average load equal to 6.9 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-30 | 2025 | 9 | 30 | Jabori HPS | 10.2 | 3.9 | 3.76 | 90457 | 88890 | 5.83 | 2.9 | 96.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 507490.79 | 890121.37 | 1567 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-30 | 2025 | 9 | 30 | Karora HPS | 11.8 | 5.9 | 4.92 | 114988 | 113157 | 4.5 | 3.7 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 880361.46 | 1322934.54 | 1831 | Unit01 remain Shutdown due to contractor working on punch list issues. While unit no 2 is on bar with average load of 4.92Mw.As load is reduced on demand of local community due more down steam water. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-30 | 2025 | 9 | 30 | Koto HPS | 40.8 | 11.1 | 5.24 | 130250 | 129409 | 40.9 | 17.45 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1066330.16 | 7002277.84 | 841 | The plant was operational on average load of 5.24 MW as per available hydrology | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-30 | 2025 | 9 | 30 | Machai HPS | 2.6 | 0.58 | 0.49 | 11440 | 10724 | 28.6 | 20 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 50091.8 | 241378.6 | 716 | Unit remained on bar delivering power to National Grid as per available inflow and system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-30 | 2025 | 9 | 30 | Malakand-3 HPS | 81 | 54 | 51.02 | 1224529 | 1214590 | 51 | 34.91 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3477006.79 | 2088082.01 | 9939 | As per available hydrology from Irrigation Department all three units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-30 | 2025 | 9 | 30 | Pehur HPS | 18 | 11.59 | 11.41 | 273900 | 266000 | 21.22 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1002022 | 625322 | 7900 | Plant remained operational throughout 24 Hrs as per available hydrology + irrigation valve open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-30 | 2025 | 9 | 30 | Reshun HPS | 4.2 | 3.43 | 2.06 | 49000 | 48435 | 3.01 | 3 | 99.97 | 13.48 | 100 | 45 | 100800 | 1358784 | 652903.8 | 705880.2 | 565 | nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-09-30 | 2025 | 9 | 30 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-01 | 2025 | 10 | 1 | Daral Khwar HPS | 36.6 | 7 | 6.5 | 156820 | 154820 | 4.03 | 2.59 | 86.33 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1280098.21 | 5982776.51 | 2000 | 1. Unit No.02 was on bar delivering an average load equal to 6.5 MW according to the available hydrology. 2. 132 KV Supply line failed at 0725 Hrs and was restored at 0732 Hrs. 3. Unit No.02 was synchronised with the national grid at 0745 Hrs. 4. Unit No.03 synchronised with national grid at 1215 Hrs and Unit No.02 stopped for monthly maintenance as per PTW No.70/2025 issued at 1220 Hrs. 5. Unit No.02 synchronised with national grid at 1628 Hrs and Unit No.03 stopped at 1630 Hrs. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-01 | 2025 | 10 | 1 | Jabori HPS | 10.2 | 4.4 | 3.9 | 83872 | 82360 | 5.61 | 3 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 470209.71 | 927402.45 | 1512 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-01 | 2025 | 10 | 1 | Karora HPS | 11.8 | 5.98 | 4.48 | 106310 | 104582 | 3.62 | 3.39 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 813647.96 | 1389648.04 | 1728 | unit:01shutdowned due to punch list issues. unit 02 on bar delivering 4.3mw load decrease 4.3mw as of local demand.as the transmission line work is not completed.by Pasco so the community so the community is not along fully diversion of water at night time. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-01 | 2025 | 10 | 1 | Koto HPS | 40.8 | 13.3 | 7.21 | 164500 | 162520 | 40.9 | 23.9 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1339164.8 | 6729443.2 | 1980 | The plant was operational on average load 7.21MW and maximum load of 13.30MW | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-01 | 2025 | 10 | 1 | Machai HPS | 2.6 | 0.57 | 0.5 | 11792 | 11100 | 24.5 | 19 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 51848.1 | 239622.3 | 692 | 1.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 0748Hrs dated 01.10.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault.Unit synchronized with the system at 0821Hrs as 11KV Machai-HPS line energized at 0806Hrs. 2.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 2057Hrs and 2205Hrs dated 01.10.2025 with Reverse power due to high system voltage . Unit synchronized with the system at 2132Hrs and 2209Hrs respectively as system voltage stabilized. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-01 | 2025 | 10 | 1 | Malakand-3 HPS | 81 | 54 | 49.94 | 1198639 | 1189640 | 38.59 | 34.4 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3405582.43 | 2159506.37 | 8999 | As per available hydrology from Irrigation Department all three units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-01 | 2025 | 10 | 1 | Pehur HPS | 18 | 12 | 10.21 | 245100 | 239000 | 8.63 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 900313 | 727031 | 6100 | Unit# 01 & 02 load remained less up to 4.0 MW each from 1050 to 2110 Hrs upon the request of irrigation department because of low irrigation demand due to heavy rainfall at downstream of canal. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-01 | 2025 | 10 | 1 | Reshun HPS | 4.2 | 3.47 | 2 | 45000 | 44439 | 2.75 | 2.76 | 92.17 | 13.48 | 91.8 | 45 | 92534.4 | 1247363.71 | 599037.72 | 648325.99 | 561 | outgoingfeeder breaker tripped 3times. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-01 | 2025 | 10 | 1 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | No data submitted for this date | ibrarahmadmkd@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-10-02 | 2025 | 10 | 2 | Daral Khwar HPS | 36.6 | 8 | 6.9 | 165300 | 163300 | 4.03 | 2.73 | 91 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1350213.39 | 5912661.33 | 2000 | Unit No 02 was on bar delivering an average load equal to 6.9 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-02 | 2025 | 10 | 2 | Jabori HPS | 10.2 | 3.9 | 3.7 | 88962 | 87450 | 5.61 | 2.9 | 96.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 499269.54 | 898342.62 | 1512 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-02 | 2025 | 10 | 2 | Karora HPS | 11.8 | 5.94 | 4.69 | 111054 | 109326 | 3.62 | 3.52 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 850556.28 | 1352739.72 | 1728 | unit 01 shutdown due to cleaning of punch list issues. unit 02 operation mode load in 4.4 mw the load was decreased from 5.1mw to 4.4mw at 18:13hrs due to local issues.(the local community is demanding water for their MHPs until the completion of the PESCO electrification scheme for the affected UCs). | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-02 | 2025 | 10 | 2 | Koto HPS | 40.8 | 11.52 | 4.57 | 111000 | 110482 | 40.9 | 26.44 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 910371.68 | 7158236.32 | 518 | This palnt was operational on avg load of 4.57 mwo And maximum load of 11.52 MW is far available hydrology | rekotohpc@gmail.com | Original | Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-10-02 | 2025 | 10 | 2 | Machai HPS | 2.6 | 0.55 | 0.5 | 10184 | 9548 | 24.5 | 19 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 44598.71 | 246871.69 | 636 | 1.The unit, while on bar and delivering power to the National Grid as per available water inflow and prevailing system conditions, tripped at 1506Hrs and 2110Hrs on 02.10.2025 due to reverse power resulting from high system voltage. Subsequently, the unit remained shut down/standby and could not be synchronized with the system due to persistently high system voltage. The unit was finally synchronized with the system at 1755Hr and 2155Hrs respectively, once the voltage stabilized. 2.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 2003Hrs dated 02.10.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault.Unit synchronized with the system at 2015Hrs as 11KV Machai-HPS line energized at 2011Hrs. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-02 | 2025 | 10 | 2 | Malakand-3 HPS | 81 | 55 | 50.36 | 1208678 | 1199480 | 38.59 | 34.76 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3433751.4 | 2131337.4 | 9198 | As per available hydrology from Irrigation Department all three units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-02 | 2025 | 10 | 2 | Pehur HPS | 18 | 12.09 | 11.96 | 287100 | 280000 | 8.63 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1054760 | 572584 | 7100 | The plant remained operational throughout 24 hours as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-02 | 2025 | 10 | 2 | Reshun HPS | 4.2 | 3.47 | 2.1 | 51000 | 50440 | 3.14 | 3.12 | 100 | 13.48 | 100 | 45 | 100800 | 1358784 | 679931.2 | 678852.8 | 560 | outgoing feeder breaker tripped 2times due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-02 | 2025 | 10 | 2 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-03 | 2025 | 10 | 3 | Daral Khwar HPS | 36.6 | 7 | 6.7 | 159650 | 157650 | 4.03 | 2.64 | 88 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1303497.5 | 5959377.22 | 2000 | Unit No 02 was on bar delivering an average load equal to 6.7 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-03 | 2025 | 10 | 3 | Jabori HPS | 10.2 | 6.9 | 4.1 | 98590 | 96930 | 5.61 | 3.2 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 553392.76 | 844219.4 | 1660 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-03 | 2025 | 10 | 3 | Karora HPS | 11.8 | 5.9 | 3.89 | 92680 | 90985 | 3.62 | 2.93 | 97.67 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 707863.3 | 1495432.7 | 1695 | unit#01 shutdown due to punch list clearance and low hydrology unit#02 on bar the load was decrease from 5.2MW to 3MW at 10.00 hrs. as per the directions of the DC shangla and due to the local community's demand for water to operate their MHPs.the local community is demanding continued water access until the completion of the PESCO electrification scheme for the affected UCs. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-03 | 2025 | 10 | 3 | Koto HPS | 40.8 | 11.77 | 8.94 | 213500 | 211303 | 33.9 | 28.99 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1741136.72 | 6327471.28 | 2197 | This palnt was operational on average load of 8.94 MW and maximum load of 11.77 MW is per available hydrology | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-03 | 2025 | 10 | 3 | Machai HPS | 2.6 | 0.72 | 0.5 | 10780 | 10392 | 24.5 | 19 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 48541.03 | 242929.37 | 388 | Unit two times tripped on Reverse Power due to high system voltage | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-03 | 2025 | 10 | 3 | Malakand-3 HPS | 81 | 53 | 50.56 | 1213440 | 1204710 | 38.59 | 34.51 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3448723.32 | 2116365.48 | 8730 | All three units are on bar as per available hydrology from irrigation department. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-03 | 2025 | 10 | 3 | Pehur HPS | 18 | 12.39 | 11.95 | 287000 | 278000 | 8.63 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1047226 | 580118 | 9000 | plant remained operational for 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-03 | 2025 | 10 | 3 | Reshun HPS | 4.2 | 3.67 | 2.25 | 46000 | 45437 | 2.83 | 2.82 | 93.87 | 13.48 | 94.23 | 45 | 94987.2 | 1280427.46 | 612490.76 | 667936.7 | 563 | 1. outgoing Feeder Breaker tripped 6times. 2. low hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-03 | 2025 | 10 | 3 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-04 | 2025 | 10 | 4 | Daral Khwar HPS | 36.6 | 8.5 | 7 | 168580 | 166580 | 4.03 | 2.79 | 93 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1377333.41 | 5885541.31 | 2000 | Unit No.02 was on bar delivering an average load equal to 7.0MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-04 | 2025 | 10 | 4 | Jabori HPS | 10.2 | 6.5 | 4.1 | 97665 | 95090 | 5.61 | 3.19 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 542887.83 | 854724.33 | 2575 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-04 | 2025 | 10 | 4 | Karora HPS | 11.8 | 5.9 | 4.1 | 95487 | 93805 | 3.62 | 3.06 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 729802.9 | 1473493.1 | 1682 | Unit #1 shutdown due to punch list clearance and low hydrology . Unit#2 on bar The load was decreased from 4.5 MW to 3 MW at 17:18 hrs. as per the directions of the DC Shangla and due to the local community’s demand for water to operate their MHPs. The local community is demanding continued water access until the completion of the PESCO electrification scheme for the affected UCs | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-04 | 2025 | 10 | 4 | Koto HPS | 40.8 | 7.25 | 5.53 | 134000 | 133688 | 33.9 | 23.78 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1101589.12 | 6967018.88 | 312 | The plant was operational on average load of 5.53 and maximum load of 7.25 as per available hydrology | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-04 | 2025 | 10 | 4 | Machai HPS | 2.6 | 0.82 | 0.7 | 16484 | 15660 | 24.5 | 19 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 73147.86 | 218322.54 | 824 | Unit tripped two times on Reverse Power due to high system voltage. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-04 | 2025 | 10 | 4 | Malakand-3 HPS | 81 | 52 | 47.01 | 1128339 | 1119590 | 38.59 | 32.99 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3205050.29 | 2360038.51 | 8749 | All three units are on bar as per available hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-04 | 2025 | 10 | 4 | Pehur HPS | 18 | 12.1 | 11.95 | 286800 | 280000 | 8.63 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1054760 | 572584 | 6800 | plant remained operational for 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-04 | 2025 | 10 | 4 | Reshun HPS | 4.2 | 3.33 | 2.1 | 44000 | 43441 | 2.7 | 2.69 | 89.77 | 13.48 | 90.17 | 45 | 90888 | 1225170.24 | 585584.68 | 639585.56 | 559 | outgoing feeder breaker tripped 6times due to lines faults | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-04 | 2025 | 10 | 4 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-05 | 2025 | 10 | 5 | Daral Khwar HPS | 36.6 | 11 | 7.6 | 181480 | 179480 | 4.03 | 3 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1483994.48 | 5778880.24 | 2000 | Unit No 02 was on bar delivering an average load equal to 7.6 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-05 | 2025 | 10 | 5 | Jabori HPS | 10.2 | 7 | 4.26 | 102220 | 99660 | 5.61 | 3.34 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 568978.87 | 828633.29 | 2560 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-05 | 2025 | 10 | 5 | Karora HPS | 11.8 | 5.9 | 3.92 | 98632 | 97004 | 3.62 | 2.96 | 98.73 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 754691.12 | 1448604.88 | 1628 | Unit¦#01 is shutdown due to punch list issues clearance .while unit #02 is on bar but due to local social conflict on water the required hydrology cannot be diverted specially at night time. So generation is less than target. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-05 | 2025 | 10 | 5 | Koto HPS | 40.8 | 7.75 | 6.97 | 169750 | 166515 | 33.9 | 26.18 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1372083.6 | 6696524.4 | 3235 | The plant was operational on average load of 6.97 and maximum load of 7.75 due to low hydrology | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-05 | 2025 | 10 | 5 | Machai HPS | 2.6 | 0.78 | 0.4 | 10484 | 10116 | 24.5 | 18 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 47251.84 | 244218.56 | 368 | 1 The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 0832Hrs dated 05.10.2025 due to reverse power resulting from high system voltage. Subsequently, the unit remained shut down/standby and could not be synchronized with the system due to persistently high system voltage. The unit was finally synchronized with the system at 1222Hr, once the voltage stabilized. 2 "Tripping Report – Tripping of Unit due earth fault and instantaneous fault, attributed to adverse weather conditions. The unit, which was on bar delivering power to the National Grid as per available water inflow and system conditions, tripped at 1719Hrs on 05-09-2025. The tripping occurred due to a fault on the 11 kV MACHAI-HPS feeder, which experienced an earth fault and instantaneous fault, attributed to heavy windstorm and rainfall.An inquiry call was made to Katlang Grid regarding the tripping and possible restoration of power. As per their response, the line could not be restored as the fault was still persistent. The operation staff of PESCO was immediately informed of the issue. The LS-Operation, PESCO (KATLANG) was contacted and requested to take prompt action to energize the feeder. However, no field team was dispatched by PESCO to clear the Machai-HPS line fault. Consequently, PEDO staff initiated line patrolling to locate and rectify the fault along the 11 kV Machai-HPS feeder. According to field updates, the fault persisted, and rectification was hindered by ongoing adverse weather conditions. The unit has remained on standby since 1719hrs Dated 05-09-2025 due to a fault on the 11 kV MACHAI-HPS feeder. " | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-05 | 2025 | 10 | 5 | Malakand-3 HPS | 81 | 51 | 46.49 | 1115699 | 1107720 | 38.59 | 32.61 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3171070.04 | 2394018.76 | 7979 | All three units are on bar as per available hydrology from irrigation department. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-05 | 2025 | 10 | 5 | Pehur HPS | 18 | 12.01 | 11.88 | 285000 | 277000 | 8.63 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1043459 | 583885 | 8000 | Plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-05 | 2025 | 10 | 5 | Reshun HPS | 4.2 | 3.83 | 2.29 | 47000 | 46435 | 2.89 | 2.98 | 99.23 | 13.48 | 96.33 | 45 | 97104 | 1308961.92 | 625943.8 | 683018.12 | 565 | line faults and less hudrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-05 | 2025 | 10 | 5 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-06 | 2025 | 10 | 6 | Daral Khwar HPS | 36.6 | 14 | 11.4 | 273330 | 270930 | 4.03 | 4.53 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2240130.52 | 5022744.2 | 2400 | Unit No 02 was on bar delivering an average load equal to 11.4 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-06 | 2025 | 10 | 6 | Jabori HPS | 10.2 | 9.8 | 7.3 | 175870 | 173040 | 5.61 | 5.75 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 987919.97 | 409692.19 | 2830 | Maximum generation was not possible despite of available hydrology on dated 06-10-2025 due to chocking of main trash rack. There is no Cleaning mechanism of trash rack and also manual cleaning is not possible during heavy water flow. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-06 | 2025 | 10 | 6 | Karora HPS | 11.8 | 5.92 | 5.56 | 134349 | 132575 | 3.62 | 4.16 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1031433.5 | 1171862.5 | 1774 | Unit #1 shutdown due to punch list clearance and low hydrology . Unit#2 on bar The load was decreased from 5.7 MW . The local community is demanding continued water access until the completion of the PESCO electrification scheme for the affected UCs | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-06 | 2025 | 10 | 6 | Koto HPS | 40.8 | 13.68 | 10.71 | 264500 | 263662 | 33.9 | 29.81 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 2172574.88 | 5896033.12 | 838 | The plant was operational on average load 10.71 and maximum load 13.68MW. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-06 | 2025 | 10 | 6 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 24.5 | 15 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Incident / Standby Report – Unit on Standby Due to Feeder Fault and Low Hydrology The unit has remained on standby since 1719 Hrs on 05-09-2025 due to a fault on the 11 kV Machai-HPS feeder. The feeder was eventually re-energized at 1755 Hrs on 06-10-2025, following fault clearance by PEDO staff, who removed tree branches from various locations along the line. However, the unit was not started and remains on standby due to low hydrological inflow, as canal water was diverted by the Irrigation Department in accordance with the weekly canal closure schedule, as informed by SDO Dargai. As per the notification issued by the Executive Engineer, Irrigation Department (C.W No. 823-7, dated October 06, 2025), the Full Supply Turn of Malakand Irrigation Division, Malakand commenced from 07:00 AM on October 06, 2025. The Benton Tunnel is being operated at 3.30 ft = 896 cusec, and the Axil Tunnel at 4.40 ft = 1404 cusec. In case of any shortfall in the main canal, adjustments are to be made in the Axil Tunnel, while the Benton Tunnel will run with the balance flow. As per the existing discharge, the Abazai Branch is running at 3.15 ft = 646 cusec, and the Machai Branch at 3.62 ft = 1506 cusec. The balance supply of approximately 843 cusec is released at RD-95+000 Machai Branch towards Swabi Division. All channels of the Machai Branch and Abazai Branch are directed to be operated at full supply. Sub Engineers Dargai and Katlang are further instructed to ensure the presence of regulation staff at each cross-regulation gate and to avoid unnecessary variation in ponding levels, which may affect the tail reaches of canals. This report is submitted for kind information, please. The unit will be recommissioned once sufficient inflow is restored by the Irrigation Department. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-10-06 | 2025 | 10 | 6 | Malakand-3 HPS | 81 | 54 | 48.95 | 1174896 | 1166350 | 38.59 | 33.81 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3338910.14 | 2226178.65 | 8546 | As per available hydrology from Irrigation Department all three units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-06 | 2025 | 10 | 6 | Pehur HPS | 18 | 12.02 | 7.84 | 188200 | 182000 | 8.63 | 12 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 685594 | 941750 | 6200 | The plant has remained shut down since 1615 hours on 06-10-2025 upon instruction of the irrigation department due to nil irrigation demand because of heavy rainfall. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-06 | 2025 | 10 | 6 | Reshun HPS | 4.2 | 3.15 | 1.95 | 44000 | 43434 | 2.7 | 2.69 | 89.77 | 13.48 | 90.13 | 45 | 90854.4 | 1224717.31 | 585490.32 | 639226.99 | 566 | outgoing feeder breaker tripped 3time due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-06 | 2025 | 10 | 6 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-07 | 2025 | 10 | 7 | Daral Khwar HPS | 36.6 | 13.5 | 12.2 | 293980 | 291580 | 4.03 | 4.88 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2410870.91 | 4852003.81 | 2400 | Unit No 02 was on bar delivering an average load equal to 12.2 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-07 | 2025 | 10 | 7 | Jabori HPS | 10.2 | 9.8 | 6.06 | 145440 | 142800 | 5.61 | 4.75 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 815273.76 | 582338.4 | 2640 | Maximum generation was not possible despite of available hydrology due to chocking of main trash rack. Trash rack was cleaned manually after heavy water flow subsided. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-07 | 2025 | 10 | 7 | Karora HPS | 11.8 | 9.9 | 6.32 | 151215 | 149137 | 3.62 | 3.82 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1160285.86 | 1043010.14 | 2078 | Unit #1 shutdown due to punch list clearance and low hydrology . Unit#2 on bar The load was 5.9 MW ' as per the directions of the DC Shangla and due to the local community’s demand for water to operate their MHPs. The local community is demanding continued water access until the completion of the PESCO electrification scheme for the affected UCs | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-07 | 2025 | 10 | 7 | Koto HPS | 40.8 | 15.15 | 13.14 | 315000 | 311589 | 33.9 | 37.23 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 2567493.36 | 5501114.64 | 3411 | The plant was operational on average load 13.14MW and a maximum load 15.15MW. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-07 | 2025 | 10 | 7 | Machai HPS | 2.6 | 0.79 | 0.4 | 7760 | 7340 | 24.5 | 16 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 34285.14 | 257185.26 | 420 | The Unit, after completion of all preliminary checks, was started as the rated head was restored due to increased canal discharge as per new indent. Unit synchronized with the system at 0856Hrs on 07-10-2025, and load was incrementally increased in accordance with prevailing system demand and operating conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-07 | 2025 | 10 | 7 | Malakand-3 HPS | 81 | 53 | 49.33 | 1183970 | 1175690 | 38.59 | 34.48 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3365647.76 | 2199441.04 | 8280 | As per available hydrology from Irrigation Department all three units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-07 | 2025 | 10 | 7 | Pehur HPS | 18 | 5.94 | 1.92 | 46100 | 45000 | 8.63 | 3 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 169515 | 1457829 | 1100 | Unit #01 was synchronized with a 6.0 MW load, and Unit #02 remains on standby due to low irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-07 | 2025 | 10 | 7 | Reshun HPS | 4.2 | 3.19 | 1.78 | 40000 | 39433 | 2.45 | 2.45 | 81.6 | 13.48 | 81.73 | 45 | 82387.2 | 1110579.46 | 531556.84 | 579022.62 | 567 | outgoing feeder breaker tripped 1time due to line fault. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-07 | 2025 | 10 | 7 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-08 | 2025 | 10 | 8 | Daral Khwar HPS | 36.6 | 12.3 | 10.3 | 247930 | 245530 | 4.03 | 4.11 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2030115.7 | 5232759.02 | 2400 | Unit No 02 was on bar delivering an average load equal to 10.3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-08 | 2025 | 10 | 8 | Jabori HPS | 10.2 | 8.3 | 6.6 | 158260 | 155420 | 5.61 | 5.17 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 887323.86 | 510288.3 | 2840 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-08 | 2025 | 10 | 8 | Karora HPS | 11.8 | 8.8 | 5.74 | 134306 | 132275 | 3.62 | 4.32 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1029099.5 | 1174196.5 | 2031 | Unit#02 remain on bar delivering power to the system as per available flow. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-08 | 2025 | 10 | 8 | Koto HPS | 40.8 | 13.6 | 12.51 | 301250 | 299128 | 33.9 | 34.59 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 2464814.72 | 5603793.28 | 2122 | The plant was operational on average load 12.51 MW and a maximum load 13.60MW due to low Hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-08 | 2025 | 10 | 8 | Machai HPS | 2.6 | 0.59 | 0.48 | 12096 | 11572 | 24.5 | 11 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 54052.81 | 237417.59 | 524 | The unit, while on bar delivering power to the National Grid as per available inflow and system conditions, was shut down as a precautionary measure at 2300Hrs on 08-10-2025 following a significant drop in the headrace water level, caused by reduced discharge from the Irrigation Department as as canal water was diverted by the Irrigation Department in accordance with the weekly canal closure schedule. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-08 | 2025 | 10 | 8 | Malakand-3 HPS | 81 | 53 | 49.64 | 1191384 | 1183160 | 38.59 | 34.45 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3387032.13 | 2178056.67 | 8224 | As per available hydrology from Irrigation Department all three units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-08 | 2025 | 10 | 8 | Pehur HPS | 18 | 7.23 | 6.61 | 158600 | 154000 | 8.63 | 10 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 580118 | 1047226 | 4600 | Unit# 02 was taken on bar at 1025 Hrs along with unit# 01. Both units are on bar with total load 7.20 MW, irrigation demand is low. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-08 | 2025 | 10 | 8 | Reshun HPS | 4.2 | 3.25 | 1.61 | 34000 | 33410 | 2.09 | 2.08 | 69.37 | 13.48 | 69.8 | 45 | 70358.4 | 948431.23 | 450366.8 | 498064.43 | 590 | less hydrology | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-08 | 2025 | 10 | 8 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-09 | 2025 | 10 | 9 | Daral Khwar HPS | 36.6 | 10.4 | 9.3 | 223120 | 220720 | 4.03 | 3.69 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1824979.18 | 5437895.54 | 2400 | Unit No 02 was on bar delivering an average load equal to 9.3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-09 | 2025 | 10 | 9 | Jabori HPS | 10.2 | 8 | 5.45 | 130920 | 128120 | 5.61 | 4.28 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 731462.7 | 666149.46 | 2800 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-09 | 2025 | 10 | 9 | Karora HPS | 11.8 | 5.9 | 2.94 | 73489 | 72256 | 3.62 | 2.2 | 73.33 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 562151.68 | 1641144.32 | 1233 | Unit#01 was already shutdown due to punch list issue clearance, while Unit#02 was shutdown as local opened the gates and diverted water flow. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-09 | 2025 | 10 | 9 | Koto HPS | 40.8 | 11.25 | 9.91 | 238000 | 235300 | 33.9 | 31.24 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1938872 | 6129736 | 2700 | This palnt was operational on average load of 9.91MW and a maximum load of 11.25MW as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-09 | 2025 | 10 | 9 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 24.5 | 13 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 2300Hrs on 08-10-2025 due to low hydrological inflow, as canal water was diverted by the Irrigation Department in accordance with the weekly canal closure schedule. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-10-09 | 2025 | 10 | 9 | Malakand-3 HPS | 81 | 52 | 48.77 | 1170509 | 1162450 | 38.59 | 33.84 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3327745.62 | 2237343.18 | 8059 | Unit # 01 desynchronized from the sytem at 19:01hrs due to less hydrology, As per available hydrology from Irrigation Department Two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-09 | 2025 | 10 | 9 | Pehur HPS | 18 | 7.62 | 7.33 | 176000 | 171000 | 8.63 | 11 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 644157 | 983187 | 5000 | Plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-09 | 2025 | 10 | 9 | Reshun HPS | 4.2 | 2.88 | 1.84 | 40000 | 39404 | 2.45 | 2.45 | 81.6 | 13.48 | 81.8 | 45 | 82454.4 | 1111485.31 | 531165.92 | 580319.39 | 596 | less hydrology | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-09 | 2025 | 10 | 9 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-10 | 2025 | 10 | 10 | Daral Khwar HPS | 36.6 | 8.5 | 7.9 | 189480 | 187080 | 4.03 | 3.13 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1546833.56 | 5716041.16 | 2400 | Unit No 02 was on bar delivering an average load equal to 7.9 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-10 | 2025 | 10 | 10 | Jabori HPS | 10.2 | 6.2 | 4.95 | 119000 | 116360 | 5.61 | 3.88 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 664322.51 | 733289.65 | 2640 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-10 | 2025 | 10 | 10 | Karora HPS | 11.8 | 0 | 0 | 0 | 0 | 3.62 | 0 | 0 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 0 | 2203296 | 0 | The complex was shut down on 09/10/2025 due to a local issue. The local residents are demanding that their transmission line work be completed by the PESCO team. Therefore, the community is not allowing the diversion of water. As a result of the efforts of the PD and RE Karora, a detailed meeting was held today between PESCO and representatives of the local community at karora HPS. During the meeting, it was decided that PESCO will conduct another survey of the actual affected area. At the end of the meeting, the RE Karora HPS requested the diversion of water; however, the locals asked for time until tomorrow to discuss the matter with their community. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-10 | 2025 | 10 | 10 | Koto HPS | 40.8 | 9.18 | 8.22 | 197750 | 197564 | 33.9 | 29.78 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1627927.36 | 6440680.64 | 186 | The plant was operational on average load 8.22MW and a maximum load of 9.18MW due to low Hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-10 | 2025 | 10 | 10 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 24.5 | 11 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 2300Hrs on 08-10-2025 due to low hydrological inflow, as canal water was diverted by the Irrigation Department in accordance with the weekly canal closure schedule. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-10-10 | 2025 | 10 | 10 | Malakand-3 HPS | 81 | 50 | 47.25 | 1133991 | 1126610 | 38.59 | 31.31 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3225146.45 | 2339942.35 | 7381 | As per available hydrology from Irrigation Department two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-10 | 2025 | 10 | 10 | Pehur HPS | 18 | 8.57 | 8.11 | 194800 | 189000 | 8.63 | 12.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 711963 | 915381 | 5800 | Plant operational 24 hrs against less irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-10 | 2025 | 10 | 10 | Reshun HPS | 4.2 | 2.42 | 1.53 | 36000 | 35420 | 2.21 | 2.2 | 73.43 | 13.48 | 73.8 | 45 | 74390.4 | 1002782.59 | 477461.6 | 525320.99 | 580 | less hydrology | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-10 | 2025 | 10 | 10 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-11 | 2025 | 10 | 11 | Daral Khwar HPS | 36.6 | 8 | 7.7 | 185170 | 182370 | 4.03 | 3.05 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1507889.87 | 5754984.85 | 2800 | Unit No 02 was on bar delivering an average load equal to 7.7 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-11 | 2025 | 10 | 11 | Jabori HPS | 10.2 | 6 | 4.66 | 112000 | 109440 | 5.43 | 3.66 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 624814.85 | 772797.31 | 2560 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-11 | 2025 | 10 | 11 | Karora HPS | 11.8 | 0 | 0 | 2042 | 1412 | 3.62 | 0 | 0 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 10985.36 | 2192310.64 | 630 | Unit#01 was started at 1714Hrs to check it status. When the set point increase to 5MW,an abnormal sound was observed around spiral case and the unit was shutdown smoothly at 1736Hrs. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-11 | 2025 | 10 | 11 | Koto HPS | 40.8 | 8.3 | 6.94 | 166250 | 162508 | 33.9 | 28.32 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1339065.92 | 6729542.08 | 3742 | Plant was operational on average load of 6.94 MW and a maximum load of 8.30MW as per available hydrology | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-11 | 2025 | 10 | 11 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 24.6 | 11 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 2300Hrs on 08-10-2025 due to low hydrological inflow, as canal water was diverted by the Irrigation Department in accordance with the weekly canal closure schedule. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-11 | 2025 | 10 | 11 | Malakand-3 HPS | 81 | 46 | 43.95 | 1054894 | 1047570 | 38.59 | 29.35 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2998878.64 | 2566210.16 | 7324 | As per available hydrology from Irrigation Department two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-11 | 2025 | 10 | 11 | Pehur HPS | 18 | 9.29 | 8.95 | 21490 | 210000 | 8.63 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 791070 | 836274 | 188510 | Generation is less because of less discharge as per irrigation department demand. | phpcmw18@gmail.com | Original | CHECK: Net > Units (source me verify karein) | Link_Generation_Data_Summary.xlsx
2025-10-11 | 2025 | 10 | 11 | Reshun HPS | 4.2 | 3.62 | 1.85 | 40000 | 39330 | 2.45 | 2.45 | 81.6 | 13.48 | 81.8 | 45 | 82454.4 | 1111485.31 | 530168.4 | 581316.91 | 670 | less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-11 | 2025 | 10 | 11 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-12 | 2025 | 10 | 12 | Daral Khwar HPS | 36.6 | 8 | 7.5 | 180650 | 178250 | 4.03 | 2.98 | 99.33 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1473824.48 | 5789050.24 | 2400 | Unit No.02 was on bar delivering an average load equal to 7.5MW according to the available hydrology. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-12 | 2025 | 10 | 12 | Jabori HPS | 10.2 | 5.1 | 4.38 | 105300 | 103060 | 5.43 | 3.44 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 588390.15 | 809222.01 | 2240 | Not reported | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-12 | 2025 | 10 | 12 | Karora HPS | 11.8 | 0 | 0 | 1466 | 913 | 3.23 | 0 | 0 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 7103.14 | 2196192.86 | 553 | Unit#01 was started and synchronized with the system at 1731Hrs to check it status. At 1844Hrs Unit#01 was shutdown smoothly.Unit#02 remain shutdown due to the unavailability of water. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-12 | 2025 | 10 | 12 | Koto HPS | 40.8 | 11.32 | 6.5 | 146500 | 144822 | 33.9 | 26.17 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1193333.28 | 6875274.72 | 1678 | This palnt was operational on average load of 6.50 MW and a maximum load 11.32 MW is per available hydrology | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-12 | 2025 | 10 | 12 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 24.5 | 11 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 2300Hrs on 08-10-2025 due to low hydrological inflow, as canal water was diverted by the Irrigation Department in accordance with the weekly canal closure schedule. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-12 | 2025 | 10 | 12 | Malakand-3 HPS | 81 | 43 | 39.65 | 951571 | 944680 | 38.59 | 27.09 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2704335.44 | 2860753.36 | 6891 | As per available hydrology from Irrigation Department two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-12 | 2025 | 10 | 12 | Pehur HPS | 18 | 9.95 | 9.65 | 231700 | 227000 | 8.63 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 855109 | 772235 | 4700 | Generation is less because of less discharge as per irrigation department demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-12 | 2025 | 10 | 12 | Reshun HPS | 4.2 | 2.48 | 1.66 | 39000 | 38411 | 2.4 | 2.39 | 79.57 | 13.48 | 79.87 | 45 | 80505.6 | 1085215.49 | 517780.28 | 567435.21 | 589 | less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-12 | 2025 | 10 | 12 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-13 | 2025 | 10 | 13 | Daral Khwar HPS | 36.6 | 7.7 | 7.2 | 171940 | 169540 | 4.03 | 2.84 | 94.67 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1401807.58 | 5861067.14 | 2400 | Unit No 02 was on bar delivering an average load equal to 7.2 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-13 | 2025 | 10 | 13 | Jabori HPS | 10.2 | 5.1 | 4 | 98360 | 95820 | 5.43 | 3.2 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 547055.54 | 850556.62 | 2540 | Not reported | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-13 | 2025 | 10 | 13 | Karora HPS | 11.8 | 0 | 0 | 0 | 0 | 3.23 | 0 | 0 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 0 | 2203296 | 0 | complex was shutdown on 09/10/2025 due to local issues. local resident are demanding that transmission line work is not completed by pesco team . so the community is not allowing diversion of water | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-13 | 2025 | 10 | 13 | Koto HPS | 40.8 | 9.18 | 5.54 | 137750 | 136456 | 33.9 | 20.14 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1124397.44 | 6944210.56 | 1294 | The plant was operational on average 5.54MW and maximum load of 9.18MW | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-13 | 2025 | 10 | 13 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 24.5 | 13.33 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 2300Hrs on 08-10-2025 due to low hydrological inflow, as canal water was diverted by the Irrigation Department in accordance with the weekly canal closure schedule. | engr.atifwazir@gmail.com | Original | Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-10-13 | 2025 | 10 | 13 | Malakand-3 HPS | 81 | 39 | 36.96 | 887064 | 880200 | 38.59 | 25.79 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2519748.54 | 3045340.26 | 6864 | As per available hydrology from Irrigation Department two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-13 | 2025 | 10 | 13 | Pehur HPS | 18 | 11.96 | 10.99 | 263900 | 256000 | 8.63 | 16.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 964352 | 662992 | 7900 | Generation is less because of less discharge as per irrigation department demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-13 | 2025 | 10 | 13 | Reshun HPS | 4.2 | 2.9 | 1.6 | 37000 | 36414 | 2.27 | 2.26 | 75.5 | 13.48 | 75.8 | 45 | 76406.4 | 1029958.27 | 490860.72 | 539097.55 | 586 | less hydrology and line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-13 | 2025 | 10 | 13 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-14 | 2025 | 10 | 14 | Daral Khwar HPS | 36.6 | 7.2 | 5 | 119470 | 117470 | 4.03 | 1.96 | 65.33 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 971277.2 | 6291597.52 | 2000 | 1. Unit No.02 was on bar delivering an average load equal to 5.0 MW according to the available hydrology. 2. Unit No. 02 was stopped as per NOC for shutdown on 132KV T/L Matta at 0854hrs. 3. 132 KV Supply line failed at 0902 Hrs and was restored at 1505 Hrs. 4. Unit No.02 was synchronized with the national grid at 1534 Hrs. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-14 | 2025 | 10 | 14 | Jabori HPS | 10.2 | 5.1 | 4.3 | 104316 | 102910 | 5.43 | 3.4 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 587533.77 | 810078.39 | 1406 | Not reported | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-14 | 2025 | 10 | 14 | Karora HPS | 11.8 | 5.9 | 2.29 | 49830 | 48611 | 3.23 | 1.7 | 56.67 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 378193.58 | 1825102.42 | 1219 | unit/01 was started and synchronized with national grid at 1001Hrs. unit/01 was shutdown at 1317Hrs due to shaft seal issue. unit/01 was started and synchronized with national grid at 2022Hrs.Unit/01 remain on bar delivering power to system as per available flow | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-14 | 2025 | 10 | 14 | Koto HPS | 40.8 | 8.77 | 5.45 | 126408 | 126408 | 33.9 | 20.73 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1041601.92 | 7027006.08 | 0 | The plant was operational on average load 5.45MW and maximum load of 8.77MW | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-14 | 2025 | 10 | 14 | Machai HPS | 2.6 | 0.22 | 0.16 | 3956 | 3718 | 24.5 | 15.67 | 6.34 | 4.671 | 100 | 70 | 62400 | 291470.4 | 17366.78 | 274103.62 | 238 | No data submitted for this date | engr.atifwazir@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-10-14 | 2025 | 10 | 14 | Malakand-3 HPS | 81 | 40 | 35.36 | 848569 | 841960 | 38.59 | 24.38 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2410278.89 | 3154809.91 | 6609 | Units # 02 & 03 tripped at 10:56hrs due to failure of 132 kV line supply. After restoration of the 132 kV supply, Unit #02 was synchronized at 11:21 hrs and Unit # 03 at 11:25 hrs. Unit #01 remained on standby due to low hydrology Now Two units are currently in operation while one unit remains on standby due to low hydrology | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-14 | 2025 | 10 | 14 | Pehur HPS | 18 | 12.13 | 11.97 | 287400 | 280000 | 8.63 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1054760 | 572584 | 7400 | Plant remained operational throughout 24 hours as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-14 | 2025 | 10 | 14 | Reshun HPS | 4.2 | 3.04 | 1.87 | 40000 | 39360 | 2.45 | 2.45 | 81.6 | 13.48 | 81.73 | 45 | 82387.2 | 1110579.46 | 530572.8 | 580006.66 | 640 | less hydrology | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-14 | 2025 | 10 | 14 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-15 | 2025 | 10 | 15 | Daral Khwar HPS | 36.6 | 7.5 | 6.9 | 164710 | 162310 | 4.03 | 2.71 | 90.33 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1342027.77 | 5920846.95 | 2400 | Unit No.02 was on bar delivering an average load equal to 6.9 MW according to the available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-15 | 2025 | 10 | 15 | Jabori HPS | 10.2 | 5.1 | 4.23 | 101620 | 100180 | 5.43 | 3.32 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 571947.66 | 825664.5 | 1440 | Not reported | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-15 | 2025 | 10 | 15 | Karora HPS | 11.8 | 6 | 6.85 | 99772 | 98090 | 3.23 | 2.86 | 95.33 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 763140.2 | 1440155.8 | 1682 | unit number 01 remain on bar delivering power to the system.And unit number 02 remain shutdown due to less inflow. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-15 | 2025 | 10 | 15 | Koto HPS | 40.8 | 7.63 | 4.4 | 99499 | 97834 | 33.9 | 16.45 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 806152.16 | 7262455.84 | 1665 | Station was operational with Maximum load of 7.63 MW and Average load 4.4 MW as per available hydrology | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-15 | 2025 | 10 | 15 | Machai HPS | 2.6 | 0.77 | 0.4 | 7912 | 7436 | 24.5 | 18 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 34733.56 | 256736.84 | 476 | The Unit after all preliminary checks and started at 1008Hrs Dated 15-10-2025 as rated head was restored due to increase in canal discharge as per new indent of Swabi Irrigation Sub Division. The water diverted to Machai Canal at 0600Hrs by irrigation department. Unit kept on FSNL for an half hour to carryout heat run test and finding everything normal then synchronized with the system at 1050Hrs and load gradually increased according to available inflow and system condition. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-15 | 2025 | 10 | 15 | Malakand-3 HPS | 81 | 37 | 35 | 839999 | 832880 | 38.59 | 24.43 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2384285.58 | 3180803.22 | 7119 | As per available hydrology from Irrigation Department Units # 02 & 03 are on bar while Unit # 01 kept standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-15 | 2025 | 10 | 15 | Pehur HPS | 18 | 12.39 | 11.95 | 286800 | 280000 | 8.63 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1054760 | 572584 | 6800 | Plant remained operational throughout 24 hrs as per available hydrology + Irrigation valve close. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-15 | 2025 | 10 | 15 | Reshun HPS | 4.2 | 2.98 | 1.74 | 39000 | 38409 | 2.4 | 2.39 | 79.57 | 13.48 | 79.83 | 45 | 80472 | 1084762.56 | 517753.32 | 567009.24 | 591 | less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-15 | 2025 | 10 | 15 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-16 | 2025 | 10 | 16 | Daral Khwar HPS | 36.6 | 6.8 | 6.5 | 156650 | 154250 | 4.03 | 2.58 | 86 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1275385.27 | 5987489.44 | 2400 | Unit No 02 was on bar delivering an average load equal to 6.5 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-16 | 2025 | 10 | 16 | Jabori HPS | 10.2 | 4.3 | 4.18 | 100448 | 98960 | 5.43 | 3.28 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 564982.43 | 832629.73 | 1488 | Not reported | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-16 | 2025 | 10 | 16 | Karora HPS | 11.8 | 5.89 | 4.35 | 103701 | 102008 | 3.23 | 3.08 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 793622.24 | 1409673.76 | 1693 | unit number 01 remain on bar delivering power to the system as per Available flow. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-16 | 2025 | 10 | 16 | Koto HPS | 40.8 | 7.48 | 3.94 | 91000 | 94386 | 33.9 | 15.58 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 777740.64 | 7290867.36 | 3386 | The plant was operational at maximum load of 7.48 and average load of 3.94 w.r.t to available hydrology. | rekotohpc@gmail.com | Original | CHECK: Net > Units (source me verify karein) | Link_Generation_Data_Summary.xlsx
2025-10-16 | 2025 | 10 | 16 | Machai HPS | 2.6 | 0.56 | 0.4 | 9928 | 9416 | 24.5 | 18 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 43982.14 | 247488.26 | 512 | The unit, while on bar delivering power to the National Grid as per the available water inflow and system conditions, tripped at 0853Hrs on 16-10-2025 due to the tripping of the 11 kV Machai-HPS feeder, as Permit to Work (PTW) was issued to Mr. Fawad Gul (PESCO Line Superintendent) up to 1400Hrs at Katlang Grid.The 11 kV Machai-HPS line was re-energized at 1323Hrs after the PTW was canceled by the Operation Staff (PESCO). The unit was synchronized with the system at 1337Hrs, and the load was gradually increased according to the available inflow and prevailing system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-16 | 2025 | 10 | 16 | Malakand-3 HPS | 81 | 39 | 35.72 | 857248 | 850060 | 38.59 | 24.92 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2433466.76 | 3131622.04 | 7188 | As per available hydrology from Irrigation Department Units # 02 & 03 are on bar while Unit # 01 kept standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-16 | 2025 | 10 | 16 | Pehur HPS | 18 | 8.11 | 11.77 | 282600 | 275000 | 8.63 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1035925 | 591419 | 7600 | Plant remained operational throughout 24 hrs as per available hydrology + Irrigation valve close. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-16 | 2025 | 10 | 16 | Reshun HPS | 4.2 | 2.97 | 1.66 | 38000 | 37410 | 2.33 | 2.33 | 77.53 | 13.48 | 77.7 | 45 | 78321.6 | 1055775.17 | 504286.8 | 551488.37 | 590 | less hydrology | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-16 | 2025 | 10 | 16 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-17 | 2025 | 10 | 17 | Daral Khwar HPS | 36.6 | 7 | 6.5 | 156390 | 153990 | 4.03 | 2.58 | 86 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1273235.52 | 5989639.2 | 2400 | Unit No 02 was on bar delivering an average load equal to 6.5 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-17 | 2025 | 10 | 17 | Jabori HPS | 10.2 | 4.2 | 4 | 96912 | 95400 | 5.43 | 3.16 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 544657.68 | 852954.48 | 1512 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-17 | 2025 | 10 | 17 | Karora HPS | 11.8 | 5.89 | 4.02 | 97322 | 95579 | 3.23 | 2.9 | 96.67 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 743604.62 | 1459691.38 | 1743 | unit number 01 remain on bar delivering power to the system as per available flow. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-17 | 2025 | 10 | 17 | Koto HPS | 40.8 | 7.35 | 4.38 | 100499 | 100010 | 33.9 | 16.7 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 824082.4 | 7244525.6 | 489 | The plant was operational on maximum load 7.35 and average load 4.38 w.r.t to available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-17 | 2025 | 10 | 17 | Machai HPS | 2.6 | 0.84 | 0.65 | 16280 | 15576 | 24.5 | 19 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 72755.5 | 218714.9 | 704 | Unit remained on bar delivering power to National Grid as per available inflow and system conditions . | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-17 | 2025 | 10 | 17 | Malakand-3 HPS | 81 | 41 | 34.87 | 836760 | 829530 | 38.59 | 24.66 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2374695.53 | 3190393.27 | 7230 | As per available hydrology from Irrigation Department Units # 02 & 03 are on bar while Unit # 01 kept standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-17 | 2025 | 10 | 17 | Pehur HPS | 18 | 10.62 | 8.78 | 210900 | 206000 | 8.63 | 13 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 776002 | 851342 | 4900 | Generation is less because of irrigation department restriction of flow in the canal. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-17 | 2025 | 10 | 17 | Reshun HPS | 4.2 | 2.1 | 1.46 | 33000 | 32412 | 2.03 | 2.02 | 67.33 | 13.48 | 67.67 | 45 | 68208 | 919443.84 | 436913.76 | 482530.08 | 588 | less hydrology | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-17 | 2025 | 10 | 17 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-18 | 2025 | 10 | 18 | Daral Khwar HPS | 36.6 | 7.5 | 6.5 | 155320 | 152920 | 4.03 | 2.56 | 85.33 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1264388.44 | 5998486.28 | 2400 | Unit No 02 was on bar delivering an average load equal to | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-18 | 2025 | 10 | 18 | Jabori HPS | 10.2 | 4.1 | 3.9 | 93761 | 92230 | 5.43 | 3 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 526559.52 | 871052.64 | 1531 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-18 | 2025 | 10 | 18 | Karora HPS | 11.8 | 5.8 | 3.83 | 92763 | 90890 | 3.23 | 2.72 | 90.67 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 707124.2 | 1496171.8 | 1873 | unit¦#01 is on bar delivering power to the system as per Available flow .it is to be noted that full flow is not diverted because of local people resistance.. while unit#02 is shutdown due to low inflow.Scada picture is also not uploaded due to extremely low internet speed. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-18 | 2025 | 10 | 18 | Koto HPS | 40.8 | 7.03 | 3.89 | 90250 | 88785 | 33.9 | 15.3 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 731588.4 | 7337019.6 | 1465 | The Plant was operational on average load of 3.98MW due to available Hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-18 | 2025 | 10 | 18 | Machai HPS | 2.6 | 1 | 0.85 | 21420 | 20636 | 24.5 | 19 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 96390.76 | 195079.64 | 784 | Unit remained on bar delivering power to National Grid as per available inflow and system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-18 | 2025 | 10 | 18 | Malakand-3 HPS | 81 | 40 | 35.53 | 852804 | 845520 | 38.59 | 24.44 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2420470.1 | 3144618.7 | 7284 | As per available hydrology from Irrigation Department Units # 02 & 03 are on bar while Unit # 01 kept standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-18 | 2025 | 10 | 18 | Pehur HPS | 18 | 12.11 | 11.27 | 270400 | 263000 | 8.63 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 990721 | 636623 | 7400 | Plant remained operational throughout 24 hours as per available head. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-18 | 2025 | 10 | 18 | Reshun HPS | 4.2 | 2.79 | 1.64 | 37000 | 36414 | 2.27 | 2.26 | 75.5 | 13.48 | 75.73 | 45 | 76339.2 | 1029052.42 | 490860.72 | 538191.7 | 586 | lines faults and less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-18 | 2025 | 10 | 18 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-19 | 2025 | 10 | 19 | Daral Khwar HPS | 36.6 | 6.3 | 6.3 | 150230 | 147830 | 4.03 | 2.47 | 82.33 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1222302.79 | 6040571.93 | 2400 | Unit No 02 was on bar delivering an average load equal to 6.3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-19 | 2025 | 10 | 19 | Jabori HPS | 10.2 | 4 | 3.7 | 90410 | 88880 | 5.43 | 2.9 | 96.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 507433.7 | 890178.46 | 1530 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-19 | 2025 | 10 | 19 | Karora HPS | 11.8 | 5.8 | 3.46 | 82077 | 80418 | 3.23 | 2.47 | 82.33 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 625652.04 | 1577643.96 | 1659 | Unit#01 remain on bar delivering power to the system as per available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-19 | 2025 | 10 | 19 | Koto HPS | 40.8 | 8.7 | 3.71 | 88749 | 88463 | 33.9 | 13.65 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 728935.12 | 7339672.88 | 286 | The plant was operational on average load 3.71 MW and Maximum load 8.70 as per hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-19 | 2025 | 10 | 19 | Machai HPS | 2.6 | 1.08 | 0.9 | 20616 | 20016 | 24.5 | 19 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 93494.74 | 197975.66 | 600 | Unit remained on bar delivering power to National Grid as per available inflow and system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-19 | 2025 | 10 | 19 | Malakand-3 HPS | 81 | 37 | 36.18 | 868365 | 861280 | 38.59 | 25.04 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2465586.26 | 3099502.54 | 7085 | As per available hydrology from Irrigation Department Units # 02 & 03 are on bar while Unit # 01 kept standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-19 | 2025 | 10 | 19 | Pehur HPS | 18 | 12 | 11.93 | 286300 | 279000 | 8.63 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1050993 | 576351 | 7300 | plant operational 24 hrs | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-19 | 2025 | 10 | 19 | Reshun HPS | 4.2 | 2.4 | 1.64 | 39000 | 38409 | 2.4 | 2.39 | 79.57 | 13.48 | 79.83 | 45 | 80472 | 1084762.56 | 517753.32 | 567009.24 | 591 | less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-19 | 2025 | 10 | 19 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-20 | 2025 | 10 | 20 | Daral Khwar HPS | 36.6 | 6.3 | 6.1 | 146190 | 143790 | 4.03 | 2.4 | 80 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1188898.86 | 6073975.86 | 2400 | Unit No.02 was on bar delivering an average load equal to 6.1 MW according to the available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-20 | 2025 | 10 | 20 | Jabori HPS | 10.2 | 3.8 | 3.6 | 87289 | 85710 | 5.43 | 2.85 | 95 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 489335.53 | 908276.63 | 1579 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-20 | 2025 | 10 | 20 | Karora HPS | 11.8 | 5.5 | 3.76 | 88773 | 87054 | 3.23 | 2.82 | 94 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 677280.12 | 1526015.88 | 1719 | Unit#01 is on bar delivering power to the system as per available flow. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-20 | 2025 | 10 | 20 | Koto HPS | 40.8 | 7.15 | 3.07 | 73220 | 72652 | 33.9 | 16.74 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 598652.48 | 7469955.52 | 568 | The plant was operational on average load 3.07MW and maximum load 7.15 MW. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-20 | 2025 | 10 | 20 | Machai HPS | 2.6 | 0.9 | 0.71 | 17212 | 16500 | 24.5 | 19 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 77071.5 | 214398.9 | 712 | The unit, while on bar and delivering power to the National Grid as per available water inflow and prevailing system conditions, tripped at 1136Hrs on 20.10.2025 due to reverse power resulting from high system voltage.Subsequently, the unit remained shut down/standby and could not be synchronized with the system due to persistently high system voltage while 11KV Machai-HPS line energized at 1158Hrs . The unit was finally synchronized with the system at 1Hr and 1428Hrs respectively, once the voltage stabilized. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-20 | 2025 | 10 | 20 | Malakand-3 HPS | 81 | 36 | 34.89 | 837414 | 830200 | 38.59 | 24.32 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2376613.54 | 3188475.26 | 7214 | Water is fully utilized as per available hydrology from the Irrigation Department and two units are on bar | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-20 | 2025 | 10 | 20 | Pehur HPS | 18 | 12.1 | 11.88 | 285200 | 278000 | 8.63 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1047226 | 580118 | 7200 | Plant remained operational throughout 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-20 | 2025 | 10 | 20 | Reshun HPS | 4.2 | 3.02 | 1.64 | 37000 | 36400 | 2.27 | 2.26 | 75.5 | 13.48 | 75.77 | 45 | 76372.8 | 1029505.34 | 490672 | 538833.34 | 600 | less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-20 | 2025 | 10 | 20 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-21 | 2025 | 10 | 21 | Daral Khwar HPS | 36.6 | 6.3 | 6.1 | 146680 | 143880 | 4.03 | 2.41 | 80.33 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1189643 | 6073231.72 | 2800 | Unit No 02 was on bar delivering an average load equal to 6.1 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-21 | 2025 | 10 | 21 | Jabori HPS | 10.2 | 3.7 | 3.57 | 85892 | 84320 | 4.92 | 2.8 | 93.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 481399.74 | 916212.42 | 1572 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-21 | 2025 | 10 | 21 | Karora HPS | 11.8 | 5.5 | 3.5 | 86770 | 85037 | 3.57 | 2.77 | 92.33 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 661587.86 | 1541708.14 | 1733 | Unit#01 is on bar delivering power to the system as per available flow. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-21 | 2025 | 10 | 21 | Koto HPS | 40.8 | 6.95 | 3.88 | 100000 | 98840 | 33.9 | 16 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 814441.6 | 7254166.4 | 1160 | Plant was operational on average load of 3.88MW and a maximum load of 6.95 MW as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-21 | 2025 | 10 | 21 | Machai HPS | 2.6 | 1 | 0.66 | 16300 | 15712 | 24.5 | 19 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 73390.75 | 218079.65 | 588 | The unit, while on bar delivering power to the National Grid as per the available water inflow and system conditions, tripped at 0828Hrs on 21-10-2025 due to the tripping of the 11 kV Machai-HPS feeder, as Permit to Work (PTW) was issued to Operation staff(PESCO) at Katlang Grid.The 11 kV Machai-HPS line was re-energized at 1301Hrs after the PTW was canceled by the Operation Staff (PESCO). The unit was synchronized with the system at 1310Hrs, and the load was gradually increased according to the available inflow and prevailing system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-21 | 2025 | 10 | 21 | Malakand-3 HPS | 81 | 34 | 32.3 | 775228 | 768050 | 38.59 | 22.86 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2198696.74 | 3366392.06 | 7178 | Water is fully utilized as per available hydrology from the Irrigation Department and two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-21 | 2025 | 10 | 21 | Pehur HPS | 18 | 12.04 | 11.86 | 284600 | 277000 | 8.63 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1043459 | 583885 | 7600 | Plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-21 | 2025 | 10 | 21 | Reshun HPS | 4.2 | 3.15 | 1.68 | 37000 | 36410 | 2.27 | 2.26 | 75.5 | 13.48 | 75.73 | 45 | 76339.2 | 1029052.42 | 490806.8 | 538245.62 | 590 | less hydrology and lines faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-21 | 2025 | 10 | 21 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-22 | 2025 | 10 | 22 | Daral Khwar HPS | 36.6 | 6.8 | 5.9 | 142760 | 140360 | 4.03 | 2.35 | 78.33 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1160538.59 | 6102336.13 | 2400 | Unit No 02 was on bar delivering an average load equal to 5.9 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-22 | 2025 | 10 | 22 | Jabori HPS | 10.2 | 3.6 | 3.47 | 83311 | 81730 | 4.92 | 2.72 | 90.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 466612.92 | 930999.24 | 1581 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-22 | 2025 | 10 | 22 | Karora HPS | 11.8 | 5.9 | 3.59 | 84563 | 82853 | 3.57 | 2.69 | 89.67 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 644596.34 | 1558699.66 | 1710 | unit 01 remain on bar delivering power to the system as per available flow unit no 2 stands still due to less inflow. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-22 | 2025 | 10 | 22 | Koto HPS | 40.8 | 7.53 | 3.64 | 89000 | 88085 | 33.9 | 13.57 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 725820.4 | 7342787.6 | 915 | This palnt was operational on avg load 3.64 Mw and a maximum load off 7.53 MW as per available hydrology | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-22 | 2025 | 10 | 22 | Machai HPS | 2.6 | 0.81 | 0.4 | 8620 | 8228 | 24.5 | 10 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 38432.99 | 253037.41 | 392 | The unit, while on bar delivering power to the National Grid as per available inflow and system conditions, was shut down as a precautionary measure at 1102Hrs on 22-10-2025 following a significant drop in the headrace water level, caused by reduced discharge from the Irrigation Department as water was diverted by the Irrigation Department from Machai Canal to Aba Zai Canal in accordance with the weekly canal closure schedule, as per the notification of the Executive Engineer (Irrigation Department), stating that the rotational turn was to be made operational due to low water supply in the Swat River. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-22 | 2025 | 10 | 22 | Malakand-3 HPS | 81 | 32 | 27.71 | 664949 | 658620 | 38.59 | 18.71 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1885431.47 | 3679657.33 | 6329 | Water is fully utilized as per available hydrology from the Irrigation Department and One units is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-22 | 2025 | 10 | 22 | Pehur HPS | 18 | 12.03 | 10.92 | 262200 | 256000 | 8.63 | 16.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 964352 | 662992 | 6200 | . | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-22 | 2025 | 10 | 22 | Reshun HPS | 4.2 | 2.44 | 0.87 | 19000 | 18645 | 1.18 | 1.16 | 38.77 | 13.48 | 39.17 | 45 | 39480 | 532190.4 | 251334.6 | 280855.8 | 355 | Clearance of Malba from the Reservoir. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-22 | 2025 | 10 | 22 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 0 | 3 | 100 | 2.47 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-23 | 2025 | 10 | 23 | Daral Khwar HPS | 36.6 | 6 | 5.7 | 136680 | 134280 | 4.03 | 2.25 | 75 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1110267.32 | 6152607.4 | 2400 | Unit No 02 was on bar delivering an average load equal to 5.7 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-23 | 2025 | 10 | 23 | Jabori HPS | 10.2 | 3.7 | 3.43 | 82425 | 80840 | 4.92 | 2.69 | 89.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 461531.73 | 936080.43 | 1585 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-23 | 2025 | 10 | 23 | Karora HPS | 11.8 | 5.8 | 3.43 | 78745 | 77077 | 3.57 | 2.54 | 84.67 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 599659.06 | 1603636.94 | 1668 | Unit#01 is on bar delivering power to the system as per available flow. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-23 | 2025 | 10 | 23 | Koto HPS | 40.8 | 7 | 2.99 | 69000 | 65448 | 33.9 | 11.98 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 539291.52 | 7529316.48 | 3552 | This palnt was operational on average load of 2.99Mw and maximum load of 7.00 Mw as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-23 | 2025 | 10 | 23 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 24.5 | 10 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 1102Hrs on 22-10-2025 due to low hydrological inflow, as canal water was diverted by the Irrigation Department on 0600Hrs on 22-10-2025 in accordance with the weekly canal closure schedule. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-23 | 2025 | 10 | 23 | Malakand-3 HPS | 81 | 26 | 24.69 | 592518 | 586650 | 38.59 | 15.98 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1679402.96 | 3885685.84 | 5868 | Water is fully utilized as per available hydrology from the Irrigation Department and One units is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-23 | 2025 | 10 | 23 | Pehur HPS | 18 | 11.79 | 11.49 | 275800 | 268000 | 8.63 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1009556 | 617788 | 7800 | plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-23 | 2025 | 10 | 23 | Reshun HPS | 4.2 | 2.24 | 0.48 | 10000 | 9650 | 1 | 0.61 | 20.4 | 13.48 | 33.33 | 45 | 33600 | 452928 | 130082 | 322846 | 350 | Powerhouse is remained shutdown due to repair works in Penstock Pipe and clearance Malba works in Reservoir. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-23 | 2025 | 10 | 23 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-24 | 2025 | 10 | 24 | Daral Khwar HPS | 36.6 | 6 | 5.3 | 128090 | 125690 | 4.03 | 2.1 | 70 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1039242.63 | 6223632.09 | 2400 | 1. Unit No 02 was on bar delivering an average load equal to 5.3 MW according to available hydrology. 2. 132 KV supply failed at 2220 hrs and was restored at 2227 hrs 3. Unit No 02 synchronized with national grid at 2245 hrs. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-24 | 2025 | 10 | 24 | Jabori HPS | 10.2 | 3.6 | 3.36 | 80710 | 79100 | 4.92 | 2.63 | 87.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 451597.72 | 946014.44 | 1610 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-24 | 2025 | 10 | 24 | Karora HPS | 11.8 | 5.5 | 3.38 | 80802 | 79143 | 3.57 | 2.5 | 83.33 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 615732.54 | 1587563.46 | 1659 | unit 01 remain on bar delivering power to the system as per available flow at 0010hrs unit 02 stands still due to less inflow | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-24 | 2025 | 10 | 24 | Koto HPS | 40.8 | 7.65 | 2.8 | 72646 | 70966 | 33.9 | 11.9 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 584759.84 | 7483848.16 | 1680 | Plant was operational on average load 2.80MW and maximum load of 7.65MW | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-24 | 2025 | 10 | 24 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 24.5 | 10 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 1102Hrs on 22-10-2025 due to low hydrological inflow, as canal water was diverted by the Irrigation Department on 0600Hrs on 22-10-2025 in accordance with the weekly canal closure schedule. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-10-24 | 2025 | 10 | 24 | Malakand-3 HPS | 81 | 24 | 22.87 | 548961 | 543120 | 38.59 | 17.72 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1554789.62 | 4010299.18 | 5841 | Water is fully utilized as per available hydrology from the Irrigation Department and One units is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-24 | 2025 | 10 | 24 | Pehur HPS | 18 | 12.1 | 11.53 | 276600 | 270000 | 8.63 | 17 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1017090 | 610254 | 6600 | Plant remained operational throughout 24 Hrs as per available hydrology + Irrigation valve open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-24 | 2025 | 10 | 24 | Reshun HPS | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.48 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | Penstock Pipe repair and clearance of Malba from the Reservoir. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-24 | 2025 | 10 | 24 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-25 | 2025 | 10 | 25 | Daral Khwar HPS | 36.6 | 5.7 | 5.3 | 126790 | 124390 | 4.03 | 2.08 | 69.33 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1028493.84 | 6234380.88 | 2400 | Unit No 02 was on bar delivering an average load equal to 5.3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-25 | 2025 | 10 | 25 | Jabori HPS | 10.2 | 4.9 | 3.26 | 75080 | 73510 | 4.92 | 2.56 | 85.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 419683.29 | 977928.87 | 1570 | Not reported | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-25 | 2025 | 10 | 25 | Karora HPS | 11.8 | 5 | 3.16 | 77225 | 75574 | 3.57 | 2.38 | 79.33 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 587965.72 | 1615330.28 | 1651 | The plant was operational on average load of 3.16 MW and maximum load of 5.0 MW due to local issue | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-25 | 2025 | 10 | 25 | Koto HPS | 40.8 | 7.85 | 3.48 | 78000 | 77331 | 33.9 | 13.61 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 637207.44 | 7431400.56 | 669 | The plant was operational on average load of 3.48MW and maximum load of 7.85MW | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-25 | 2025 | 10 | 25 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 24.5 | 9 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 1102Hrs on 22-10-2025 due to low hydrological inflow, as canal water was diverted by the Irrigation Department on 0600Hrs on 22-10-2025 in accordance with the weekly canal closure schedule. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-25 | 2025 | 10 | 25 | Malakand-3 HPS | 81 | 24 | 21.87 | 524849 | 519270 | 38.59 | 14.3 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1486514.23 | 4078574.57 | 5579 | Water is fully utilized as per available hydrology from the Irrigation Department and One units is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-25 | 2025 | 10 | 25 | Pehur HPS | 18 | 12.44 | 12 | 288000 | 281000 | 8.63 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1058527 | 568817 | 7000 | Plant remained operational throughout 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-25 | 2025 | 10 | 25 | Reshun HPS | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.48 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | Penstock Pipe repair and clearance of Mala from the Reservoir. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-25 | 2025 | 10 | 25 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-26 | 2025 | 10 | 26 | Daral Khwar HPS | 36.6 | 5.5 | 5.2 | 124930 | 122530 | 4.03 | 2.05 | 68.33 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1013114.8 | 6249759.92 | 2400 | Unit No.02 was on bar delivering an average load equal to 5.2 MW according to the available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-26 | 2025 | 10 | 26 | Jabori HPS | 10.2 | 3.6 | 3.18 | 76415 | 74830 | 4.92 | 2.5 | 83.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 427219.44 | 970392.72 | 1585 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-26 | 2025 | 10 | 26 | Karora HPS | 11.8 | 5 | 3.36 | 79892 | 78179 | 3.57 | 2.5 | 83.33 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 608232.62 | 1595063.38 | 1713 | The plant was operational on average load of 3.36 MW and Maximum load of 5.0 MW due to local issue. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-26 | 2025 | 10 | 26 | Koto HPS | 40.8 | 7.85 | 2.58 | 67500 | 67262 | 33.9 | 10.3 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 554238.88 | 7514369.12 | 238 | The plant was operational on average station load 2.58MW and maximum 7.85MW | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-26 | 2025 | 10 | 26 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 24.5 | 9 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 1102Hrs on 22-10-2025 due to low hydrological inflow, as canal water was diverted by the Irrigation Department on 0600Hrs on 22-10-2025 in accordance with the weekly canal closure schedule. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-26 | 2025 | 10 | 26 | Malakand-3 HPS | 81 | 21 | 19.91 | 477846 | 472280 | 38.59 | 13.08 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1351995.96 | 4213092.84 | 5566 | Water is fully utilized as per available hydrology from the Irrigation Department and One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-26 | 2025 | 10 | 26 | Pehur HPS | 18 | 12.04 | 11.98 | 287500 | 280000 | 8.63 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1054760 | 572584 | 7500 | plant remained operational throughout 24 hours as per available head. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-26 | 2025 | 10 | 26 | Reshun HPS | 4.2 | 1.63 | 0.21 | 5000 | 4850 | 0.31 | 1 | 33.33 | 13.48 | 10.2 | 45 | 10281.6 | 138595.97 | 65378 | 73217.97 | 150 | clearance of Malba from the Reservoir ended and power house energized on date 26/10/2025 at 8:30pm | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-26 | 2025 | 10 | 26 | Shishi HPS | 1.8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.47 | 100 | 49 | 43200 | 106704 | 0 | 106704 | 0 | The powerhouse was shut down on May 17, 2025, due to annual mechanical repair and maintenance, as well as flooded conditions, with the repair and maintenance work on the runner assemblies pending Technical Sanction (TS) approval. | ibrarahmadmkd@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-27 | 2025 | 10 | 27 | Daral Khwar HPS | 36.6 | 6 | 5.3 | 126480 | 124080 | 4.03 | 2.08 | 69.33 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1025930.66 | 6236944.06 | 2400 | 1: Units No.01 and 02 were on bar delivering an average load equal to 5.3 MW according to the available hydrology. 2: Unit No.01 Synchronized with National grid at 12:55 Hrs, And Unit No.02 Stopped at 12:57 Hrs due to low Hydrology. 3: During routine inspection ,oil leakage was observed from the bearing seals of pump No.02 , and its temperature had risen to 49 degree celsius.Pump No.01 is already under PTW.Therefore ,Unit No.02 was started at 22:27Hrs, and Unit No.01 was stopped at 22:28Hrs. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-27 | 2025 | 10 | 27 | Jabori HPS | 10.2 | 3.3 | 3.13 | 75130 | 73540 | 4.92 | 2.45 | 81.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 419854.57 | 977757.59 | 1590 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-27 | 2025 | 10 | 27 | Karora HPS | 11.8 | 5 | 3.27 | 77562 | 75834 | 3.57 | 2.47 | 82.33 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 589988.52 | 1613307.48 | 1728 | The plant was operational on average load of 3.36 MW and Maximum load of 5.0 due to local issue. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-27 | 2025 | 10 | 27 | Koto HPS | 40.8 | 7.1 | 3.32 | 71178 | 70550 | 33.9 | 13.28 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 581332 | 7487276 | 628 | The Plant was operational on maximum load of 7.1 MW and average load of 3.32 MW w.r.t available hydrology | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-27 | 2025 | 10 | 27 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 24.5 | 7 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 1102Hrs on 22-10-2025 due to low hydrological inflow, as canal water was diverted by the Irrigation Department on 0600Hrs on 22-10-2025 in accordance with the weekly canal closure schedule. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-27 | 2025 | 10 | 27 | Malakand-3 HPS | 81 | 21 | 19.59 | 470240 | 464530 | 38.59 | 12.96 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1329810.03 | 4235278.77 | 5710 | Water is fully utilized as per available hydrology from the Irrigation Department and One unit is on bar | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-27 | 2025 | 10 | 27 | Pehur HPS | 18 | 12.07 | 11.73 | 281500 | 274000 | 8.63 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1032158 | 595186 | 7500 | Plant remained operational throughout 24 hrs as per available hydrology + Irrigation valve open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-27 | 2025 | 10 | 27 | Reshun HPS | 4.2 | 3.24 | 1.7 | 39000 | 38360 | 2.39 | 2.4 | 79.83 | 13.48 | 79.57 | 45 | 80203.2 | 1081139.14 | 517092.8 | 564046.34 | 640 | less hydrology and line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-28 | 2025 | 10 | 28 | Daral Khwar HPS | 36.6 | 5.2 | 4.9 | 118650 | 116250 | 4.03 | 1.94 | 64.67 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 961189.88 | 6301684.84 | 2400 | 1. Unit No.01 & 02 were on bar delivering an average load equal to 4.9 MW according to the available hydrology. 2. Unit No.01 was synchronised with the national grid at 20:40 Hrs and Unit No.02 stopped at 20:41 Hrs due to low hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-28 | 2025 | 10 | 28 | Jabori HPS | 10.2 | 3.5 | 3.1 | 74160 | 72560 | 4.92 | 2.42 | 80.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 414259.55 | 983352.61 | 1600 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-28 | 2025 | 10 | 28 | Karora HPS | 11.8 | 3.9 | 3.29 | 75212 | 73401 | 3.57 | 2.49 | 83 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 571059.78 | 1632236.22 | 1811 | The plant was operational on average load of 3.29 MW and Maximum load of 3.9 due to local issue Unit#NO.1 is on bar delivering power to the system Unit#NO.2 is stand by due to less inflow | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-28 | 2025 | 10 | 28 | Koto HPS | 40.8 | 7.15 | 3.02 | 72250 | 71761 | 33.9 | 11.61 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 591310.64 | 7477297.36 | 489 | The plant was operational on average load of 3.02 & Maximum load of 7.15 w.r.t available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-28 | 2025 | 10 | 28 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 24.5 | 3 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 1102Hrs on 22-10-2025 due to low hydrological inflow, as canal water was diverted by the Irrigation Department on 0600Hrs on 22-10-2025 in accordance with the weekly canal closure schedule. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-28 | 2025 | 10 | 28 | Malakand-3 HPS | 81 | 22 | 19.01 | 456328 | 450700 | 38.59 | 12.82 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1290218.89 | 4274869.91 | 5628 | Water is fully utilized as per available hydrology from the Irrigation Department and One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-28 | 2025 | 10 | 28 | Pehur HPS | 18 | 11.97 | 11.62 | 279100 | 271000 | 8.32 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1020857 | 606487 | 8100 | Plant remained operational throughout 24 hrs as per available hydrology + Irrigation valve open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-28 | 2025 | 10 | 28 | Reshun HPS | 4.2 | 3.22 | 1.76 | 39000 | 38434 | 2.39 | 2.39 | 79.57 | 13.48 | 79.8 | 45 | 80438.4 | 1084309.63 | 518090.32 | 566219.31 | 566 | lines faults and less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-29 | 2025 | 10 | 29 | Daral Khwar HPS | 36.6 | 6 | 5.3 | 128270 | 125870 | 4.03 | 2.1 | 70 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1040730.92 | 6222143.8 | 2400 | Unit No 02 was on bar delivering an average load equal to 5.3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-29 | 2025 | 10 | 29 | Jabori HPS | 10.2 | 3.4 | 3.05 | 73210 | 71620 | 4.92 | 2.4 | 80 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 408892.9 | 988719.26 | 1590 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-29 | 2025 | 10 | 29 | Karora HPS | 11.8 | 3.9 | 3.24 | 77493 | 75762 | 3.57 | 2.46 | 82 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 589428.36 | 1613867.64 | 1731 | The plant was operational on average load of 3.24 MW and Maximum load of 3.9 MW due to local issue. UNIT#NO.01 is on bar delivering power to the system | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-29 | 2025 | 10 | 29 | Koto HPS | 40.8 | 7.28 | 3.06 | 71000 | 70351 | 33.9 | 11.84 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 579692.24 | 7488915.76 | 649 | The plant was operational on average load of 3.06 MW and Maximum load of 7.23MW w.r.t available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-29 | 2025 | 10 | 29 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 24.5 | 3 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 1102Hrs on 22-10-2025 due to low hydrological inflow, as canal water was diverted by the Irrigation Department on 0600Hrs on 22-10-2025 in accordance with the weekly canal closure schedule. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-29 | 2025 | 10 | 29 | Malakand-3 HPS | 81 | 20 | 19.25 | 461995 | 456350 | 38.59 | 12.61 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1306393.14 | 4258695.66 | 5645 | Water is fully utilized as per available hydrology from the Irrigation Department and One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-29 | 2025 | 10 | 29 | Pehur HPS | 18 | 11.84 | 11.68 | 280500 | 274000 | 8.63 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1032158 | 595186 | 6500 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-29 | 2025 | 10 | 29 | Reshun HPS | 4.2 | 3.52 | 1.82 | 39000 | 38439 | 2.39 | 2.39 | 79.73 | 13.48 | 79.57 | 45 | 80203.2 | 1081139.14 | 518157.72 | 562981.42 | 561 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-30 | 2025 | 10 | 30 | Daral Khwar HPS | 36.6 | 5.5 | 5.3 | 126680 | 125080 | 4.03 | 2.09 | 69.67 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1034198.96 | 6228675.76 | 1600 | Unit No 02 was on bar delivering an average load equal to 5.3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-30 | 2025 | 10 | 30 | Jabori HPS | 10.2 | 3 | 2.98 | 71640 | 70040 | 4.92 | 2.34 | 78 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 399872.37 | 997739.79 | 1600 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-30 | 2025 | 10 | 30 | Karora HPS | 11.8 | 3.4 | 3.07 | 73049 | 71290 | 3.57 | 2.33 | 77.67 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 554636.2 | 1648659.8 | 1759 | unit#01 remain on bar delivering power to the system as per Available flow.And unit#02 shutdown due to punchlist. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-30 | 2025 | 10 | 30 | Koto HPS | 40.8 | 7.65 | 2.8 | 62999 | 62404 | 33.9 | 10.86 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 514208.96 | 7554399.04 | 595 | The plant was operational on average load of 2.80MW. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-30 | 2025 | 10 | 30 | Machai HPS | 2.6 | 0.5 | 0.5 | 3576 | 3432 | 24.5 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 16030.87 | 275439.53 | 144 | The Unit, after completion of all preliminary checks, was started at 1250Hrs on 30-10-2025 following restoration of the rated head due to increased canal discharge, as per Irrigation Department notification (C.W No. 863-7,Canal Wire No. 03,Supply Turn of Swabi Irrigation Division, . The Unit was initially maintained at Full Speed No Load (FSNL) for observation. After confirming all parameters were normal, it was synchronized with the system at 1325Hrs and load was gradually increased in accordance with available inflow and prevailing system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-30 | 2025 | 10 | 30 | Malakand-3 HPS | 81 | 27 | 23.49 | 563795 | 557700 | 38.59 | 15.42 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1596527.79 | 3968561.01 | 6095 | As per the weekly rotational schedule by the Irrigation Department, hydrology has increased. One unit is on bar as per the available hydrology | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-30 | 2025 | 10 | 30 | Pehur HPS | 18 | 11.72 | 11.62 | 278800 | 271000 | 8.63 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1020857 | 606487 | 7800 | plant remained operational throughout 24 hours as per available hydrology | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-30 | 2025 | 10 | 30 | Reshun HPS | 4.2 | 2.53 | 1.51 | 36000 | 35435 | 2.21 | 2.2 | 73.43 | 13.48 | 73.6 | 45 | 74188.8 | 1000065.02 | 477663.8 | 522401.22 | 565 | less hydrology. | zafar.src@gmail.com | Original | Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-10-31 | 2025 | 10 | 31 | Daral Khwar HPS | 36.6 | 6 | 3.1 | 74130 | 72930 | 4.03 | 1.22 | 40.67 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 603007.12 | 6659867.6 | 1200 | 1. Unit No.01 was on bar delivering an average load equal to 3.1 MW according to the available hydrology. 2. 132KV supply tripped at 1002 Hrs due to broken 132KV phase conductor at Charbagh Swat and consequently plant shutdown. 3. The T-Line restored at 1913 Hrs after the maintenance carried out by PESCO. 4. Unit No.01 was synchronised with the national grid at 1949 Hrs after the stabilisation of the line voltage. 5. During the shutdown flushing and preventive maintenance activities were also carried out at weir site. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-31 | 2025 | 10 | 31 | Jabori HPS | 10.2 | 3.1 | 2.85 | 68555 | 66980 | 4.92 | 2.24 | 74.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 382402.22 | 1015209.94 | 1575 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-31 | 2025 | 10 | 31 | Karora HPS | 11.8 | 3.5 | 3.07 | 73286 | 71540 | 3.57 | 2.32 | 77.33 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 556581.2 | 1646714.8 | 1746 | unit#01 remain on bar delivering power to the system as per available flow.and unit#02 shutdown due to punchlist. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-31 | 2025 | 10 | 31 | Koto HPS | 40.8 | 7.2 | 2.76 | 62000 | 61384 | 33.9 | 10.49 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 505804.16 | 7562803.84 | 616 | The pant was operational on average load of 2.76 and maximum load of 7.20 w.r.t available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-31 | 2025 | 10 | 31 | Machai HPS | 2.6 | 0.85 | 0.63 | 16128 | 15444 | 24.5 | 16 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 72138.92 | 219331.48 | 684 | Unit remained on bar delivering power to National Grid as per available inflow and system conditions | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-31 | 2025 | 10 | 31 | Malakand-3 HPS | 81 | 27 | 24.93 | 598365 | 592160 | 38.59 | 16.5 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1695176.43 | 3869912.37 | 6205 | As per the weekly rotational schedule by the Irrigation Department, hydrology has increased. One unit is on bar as per the available hydrology | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-31 | 2025 | 10 | 31 | Pehur HPS | 18 | 12 | 11.68 | 280300 | 273000 | 8.63 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1028391 | 598953 | 7300 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-10-31 | 2025 | 10 | 31 | Reshun HPS | 4.2 | 2.47 | 1.46 | 34000 | 33419 | 2.08 | 2.08 | 69.37 | 13.48 | 69.47 | 45 | 70022.4 | 943901.95 | 450488.12 | 493413.83 | 581 | less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-01 | 2025 | 11 | 1 | Daral Khwar HPS | 36.6 | 6 | 5 | 119380 | 117380 | 2.58 | 1.96 | 65.33 | 8.2683 | 86 | 48 | 755424 | 6246072.26 | 970533.05 | 5275539.2 | 2000 | Unit No.01 was on bar delivering an average load equal to 5 MW according to the available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-01 | 2025 | 11 | 1 | Jabori HPS | 10.2 | 3 | 2.86 | 68620 | 67060 | 4.86 | 2.24 | 74.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 382858.95 | 1014753.21 | 1560 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-01 | 2025 | 11 | 1 | Karora HPS | 11.8 | 3.2 | 2.97 | 70285 | 68480 | 3.34 | 2.24 | 74.67 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 532774.4 | 1670521.6 | 1805 | unit#01 remain on bar delivering power to the system as per available flow.And unit#02 shutdown due to punchlist. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-01 | 2025 | 11 | 1 | Koto HPS | 40.8 | 7.2 | 2.78 | 60499 | 59920 | 27.5 | 10.59 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 493740.8 | 7574867.2 | 579 | The Plant was operational on average load of 2.78 MW & Maximum load of 7.20 MW w.r.t available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-01 | 2025 | 11 | 1 | Machai HPS | 2.6 | 0.94 | 0.74 | 17996 | 17380 | 18.4 | 16 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 81181.98 | 210288.42 | 616 | Unit remained on bar delivering power to National Grid as per available inflow and system conditions | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-01 | 2025 | 11 | 1 | Malakand-3 HPS | 81 | 25 | 24.26 | 582286 | 576350 | 32.39 | 16.08 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1649917.14 | 3915171.66 | 5936 | As per the weekly rotational schedule by the Irrigation Department, hydrology has increased. One unit is on bar as per the available hydrology | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-01 | 2025 | 11 | 1 | Pehur HPS | 18 | 12.1 | 11.93 | 286400 | 280000 | 12.8 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1054760 | 572584 | 6400 | Plant remained operational throughout 24 hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-01 | 2025 | 11 | 1 | Reshun HPS | 4.2 | 2.38 | 1.59 | 36000 | 35482 | 2.21 | 2.2 | 73.43 | 13.48 | 73.53 | 45 | 74121.6 | 999159.17 | 478297.36 | 520861.81 | 518 | lines fault and less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-02 | 2025 | 11 | 2 | Daral Khwar HPS | 36.6 | 5 | 4.9 | 117760 | 115760 | 2.58 | 1.94 | 64.67 | 8.2683 | 86 | 48 | 755424 | 6246072.26 | 957138.41 | 5288933.85 | 2000 | Unit No 01 was on bar delivering an average load equal to 4.9 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-02 | 2025 | 11 | 2 | Jabori HPS | 10.2 | 3 | 2.76 | 66236 | 64700 | 4.86 | 2.16 | 72 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 369385.24 | 1028226.92 | 1536 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-02 | 2025 | 11 | 2 | Karora HPS | 11.8 | 3.5 | 2.83 | 65115 | 63356 | 3.34 | 2.13 | 71 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 492909.68 | 1710386.32 | 1759 | unit#01 was in operation until 12:32 hrs,after which it was shutdown smoothly.And unit#02 was synchronized with grid at 14:10 hrs and is presently in operation. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-02 | 2025 | 11 | 2 | Koto HPS | 40.8 | 7.48 | 2.79 | 61037 | 60217 | 27.5 | 11 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 496188.08 | 7572419.92 | 820 | The plant was operation on average load of 2.79MW and maximum load of 7.48 MW as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-02 | 2025 | 11 | 2 | Machai HPS | 2.6 | 0.92 | 0.86 | 21016 | 20284 | 18.4 | 16 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 94746.56 | 196723.84 | 732 | Unit remained on bar delivering power to National Grid as per available inflow and system conditions | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-02 | 2025 | 11 | 2 | Malakand-3 HPS | 81 | 25 | 24.09 | 578206 | 572470 | 32.39 | 15.24 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1638809.87 | 3926278.93 | 5736 | As per the weekly rotational schedule by the Irrigation Department, hydrology has increased. One unit is on bar as per the available hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-02 | 2025 | 11 | 2 | Pehur HPS | 18 | 12.08 | 11.98 | 287500 | 280000 | 12.8 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1054760 | 572584 | 7500 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-02 | 2025 | 11 | 2 | Reshun HPS | 4.2 | 2.47 | 1.76 | 42000 | 41428 | 2.57 | 2.58 | 85.83 | 13.48 | 85.67 | 45 | 86352 | 1164024.96 | 558449.44 | 605575.52 | 572 | nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-03 | 2025 | 11 | 3 | Daral Khwar HPS | 36.6 | 5 | 4.8 | 114140 | 112140 | 2.58 | 1.88 | 62.67 | 8.2683 | 86 | 48 | 755424 | 6246072.26 | 927207.16 | 5318865.1 | 2000 | Unit No 01 was on bar delivering an average load equal to 4.8 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-03 | 2025 | 11 | 3 | Jabori HPS | 10.2 | 2.8 | 2.7 | 65041 | 63490 | 4.86 | 2.15 | 71.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 362477.11 | 1035135.05 | 1551 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-03 | 2025 | 11 | 3 | Karora HPS | 11.8 | 3.1 | 2.71 | 62642 | 60820 | 3.34 | 2 | 66.67 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 473179.6 | 1730116.4 | 1822 | unit#01is on stand by due to low hydrology.And unit#02 is on bar delivring power to the system as per available flow. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-03 | 2025 | 11 | 3 | Koto HPS | 40.8 | 6.83 | 2.33 | 56500 | 55875 | 27.5 | 8.4 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 460410 | 7608198 | 625 | The plant was operational on average load of 2.33 and maximum load of 6.83 as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-03 | 2025 | 11 | 3 | Machai HPS | 2.6 | 0.82 | 0.74 | 18144 | 17512 | 18.4 | 16 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 81798.55 | 209671.85 | 632 | Unit remained on bar delivering power to National Grid as per available inflow and system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-03 | 2025 | 11 | 3 | Malakand-3 HPS | 81 | 25 | 23.54 | 564842 | 558940 | 32.39 | 15.53 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1600077.54 | 3965011.26 | 5902 | As per available hydrology from the Irrigation Department, One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-03 | 2025 | 11 | 3 | Pehur HPS | 18 | 12.01 | 11.91 | 285900 | 279000 | 12.8 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1050993 | 576351 | 6900 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-03 | 2025 | 11 | 3 | Reshun HPS | 4.2 | 2.52 | 1.64 | 40000 | 39421 | 2.45 | 2.45 | 81.7 | 13.48 | 81.6 | 45 | 82252.8 | 1108767.74 | 531395.08 | 577372.66 | 579 | nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-04 | 2025 | 11 | 4 | Daral Khwar HPS | 36.6 | 7.5 | 4.6 | 109840 | 107840 | 2.58 | 1.8 | 60 | 8.2683 | 86 | 48 | 755424 | 6246072.26 | 891653.47 | 5354418.79 | 2000 | 1. Unit No.01 was on bar delivering an average load equal to 4.6 MW according to the available hydrology. 2. At 1011 Hrs 132KV supply failed, RCC was informed. Due to bad weather conditions the supply was not restored until 1244 Hrs even after isolation of the fault area at Chakdara Grid as per the instructions of the RCC to PESCO. 3. After restoration of the 132KV supply line at 1244Hrs, Unit#01 was synchronized with the national grid at 1253Hrs at 6MW according to the available hydrology. 4. At 1400Hrs Unit No.02 was synchronized with the national grid due to increased hydrology. At 1401Hrs Unit No.01 was put on standby. 5. At 1857Hrs Unit No.01 was synchronized with the national grid due to decreased hydrology and Unit No.02 was put on standby. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-04 | 2025 | 11 | 4 | Jabori HPS | 10.2 | 3.5 | 2.8 | 68385 | 66770 | 4.86 | 2.2 | 73.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 381203.28 | 1016408.88 | 1615 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-04 | 2025 | 11 | 4 | Karora HPS | 11.8 | 3.1 | 2.63 | 61136 | 59256 | 3.34 | 1.98 | 66 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 461011.68 | 1742284.32 | 1880 | unit#1 is on bar delivering power to the system as per available flow. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-04 | 2025 | 11 | 4 | Koto HPS | 40.8 | 10.48 | 7.19 | 170000 | 168027 | 27.5 | 24.65 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1384542.48 | 6684065.52 | 1973 | Plant was operational on average load 7.19MW and maximum load 10.48MW | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-04 | 2025 | 11 | 4 | Machai HPS | 2.6 | 1.42 | 0.68 | 1716 | 16544 | 18.4 | 17 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 77277.02 | 214193.38 | 14828 | The unit, while on bar delivering power to the National Grid as per available water inflow and system conditions, tripped at 0941Hrs on 04-11-2025 due to a fault on the 11 kV Machai-HPS feeder, which experienced an earth fault and instantaneous fault attributed to a heavy windstorm.The feeder was re-energized at 1008Hrs, and the unit was synchronized at 1017Hrs, after which load was gradually increased in accordance with system demand and operating conditions.The unit tripped again at 1058Hrs due to another earth fault and instantaneous fault on the 11 kV Machai-HPS feeder, again attributed to heavy windstorm conditions. The feeder was re-energized at 1148Hrs; however, the unit remained shut down / on standby and could not be synchronized with the system due to persistently high system voltage. The unit was finally synchronized with the system at 1454Hr, once the voltage stabilized. | engr.atifwazir@gmail.com | Original | CHECK: Net > Units (source me verify karein) | Link_Generation_Data_Summary.xlsx
2025-11-04 | 2025 | 11 | 4 | Malakand-3 HPS | 81 | 40 | 26.07 | 625659 | 619330 | 32.39 | 18.31 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1772955.99 | 3792132.81 | 6329 | As per available hydrology from the Irrigation Department, Two units is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-04 | 2025 | 11 | 4 | Pehur HPS | 18 | 11.72 | 11.84 | 284300 | 277000 | 12.8 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1043459 | 583885 | 7300 | Plant Operational 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-04 | 2025 | 11 | 4 | Reshun HPS | 4.2 | 2.42 | 1.68 | 38000 | 37425 | 2.33 | 2.33 | 77.67 | 13.48 | 77.53 | 45 | 78153.6 | 1053510.53 | 504489 | 549021.53 | 575 | outgoing feeder breaker tripped 2times due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-05 | 2025 | 11 | 5 | Daral Khwar HPS | 36.6 | 7.5 | 5.6 | 134930 | 132130 | 2.58 | 2.21 | 73.67 | 8.2683 | 86 | 48 | 755424 | 6246072.26 | 1092490.48 | 5153581.78 | 2800 | 1. Unit No 01 and 02 were on bar delivering an average load equal to 5.6 MW according to available hydrology. 2. Unit No 02 started at 1553 Hrs due to increased hydrology while Unit No 01 stopped at 1554 Hrs. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-05 | 2025 | 11 | 5 | Jabori HPS | 10.2 | 3.8 | 3.02 | 72518 | 70870 | 4.86 | 2.3 | 76.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 404611 | 993001.16 | 1648 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-05 | 2025 | 11 | 5 | Karora HPS | 11.8 | 3.4 | 2.97 | 71150 | 69229 | 3.34 | 2.29 | 76.33 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 538601.62 | 1664694.38 | 1921 | Unit#01 remain on bar delivering power to the system as per available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-05 | 2025 | 11 | 5 | Koto HPS | 40.8 | 15.14 | 5.79 | 139032 | 138133 | 27.5 | 17.77 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 1138215.92 | 6930392.08 | 899 | This palnt was operational on average load 5.79MW and maximum load of 15.14MW as per available hydrology | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-05 | 2025 | 11 | 5 | Machai HPS | 2.6 | 0.9 | 0.5 | 13052 | 12408 | 18.4 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 57957.77 | 233512.63 | 644 | The unit, while on bar and delivering power to the National Grid, was shut down at 2143Hrs Dated 05.11.2025 as a precautionary measure due to a significant reduction in canal inflow as communicated by the Irrigation Department. As per Canal Wire No. 889-7 dated 05-11-2025 from SDO Dargai, water supply to Machai Branch was reduced to 1305 cusecs, with 579 cusecs diverted at RD 95+000 towards Swabi Division, and the weekly canal closure for Machai scheduled on 07-11-2025. In view of the reduced discharge, the unit was safely taken off-bar and will remain on standby until restoration of adequate canal flow by the Irrigation Department. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-05 | 2025 | 11 | 5 | Malakand-3 HPS | 81 | 42 | 34.53 | 828615 | 820990 | 32.39 | 24.6 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2350248.07 | 3214840.73 | 7625 | As per available hydrology from the Irrigation Department two units is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-05 | 2025 | 11 | 5 | Pehur HPS | 18 | 11.97 | 11.83 | 283900 | 276000 | 12.8 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1039692 | 587652 | 7900 | Plant remained operational throughout 24 hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-05 | 2025 | 11 | 5 | Reshun HPS | 4.2 | 2.7 | 1.7 | 39000 | 38434 | 2.39 | 2.39 | 79.57 | 13.48 | 79.7 | 45 | 80337.6 | 1082950.85 | 518090.32 | 564860.53 | 566 | line works at village Sonoghor. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-06 | 2025 | 11 | 6 | Daral Khwar HPS | 36.6 | 6 | 5.1 | 121910 | 119110 | 2.58 | 1.99 | 66.33 | 8.2683 | 86 | 48 | 755424 | 6246072.26 | 984837.21 | 5261235.05 | 2800 | 1. Unit No 01 and 02 were on bar delivering an average load equal to 5.1 MW according to available hydrology. 2. Unit No 01 synchronized with the national grid at 1237 Hrs while Unit No 02 stopped at 1239 Hrs due to low hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-06 | 2025 | 11 | 6 | Jabori HPS | 10.2 | 3.7 | 3.07 | 73687 | 72050 | 4.86 | 2.4 | 80 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 411347.86 | 986264.3 | 1637 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-06 | 2025 | 11 | 6 | Karora HPS | 11.8 | 3.5 | 3.02 | 69271 | 67372 | 3.34 | 2.26 | 75.33 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 524154.16 | 1679141.84 | 1899 | Unit#01 is on bar delivering power to the system as per available flow. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-06 | 2025 | 11 | 6 | Koto HPS | 40.8 | 8.38 | 4.32 | 99750 | 98619 | 27.5 | 25.39 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 812620.56 | 7255987.44 | 1131 | The plant was operational on average load of 4.32and maximum load of 8.38 | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-06 | 2025 | 11 | 6 | Machai HPS | 2.6 | 0.68 | 0.4 | 9124 | 8668 | 18.4 | 15.5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 40488.23 | 250982.17 | 456 | The Unit, after completion of all preliminary checks, was started as the rated head was restored due to increased canal discharge as per new indent. Unit synchronized with the system at 0839Hrs on 06-11-2025, and load was incrementally increased in accordance with prevailing system demand and operating conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-06 | 2025 | 11 | 6 | Malakand-3 HPS | 81 | 37 | 33.24 | 797865 | 790520 | 32.39 | 23.64 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2263021.6 | 3302067.2 | 7345 | As per available hydrology from the Irrigation Department two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-06 | 2025 | 11 | 6 | Pehur HPS | 18 | 12.25 | 11.6 | 278300 | 271000 | 12.8 | 17.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1020857 | 606487 | 7300 | At 2140 Hrs, Unit# 01 & 02 load was reduced to 4.5 MW each upon the request of irrigation SDO to reduce the discharge to 10 cms due to choking of canal gate causing overtop. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-06 | 2025 | 11 | 6 | Reshun HPS | 4.2 | 2.6 | 1.84 | 44000 | 43421 | 2.7 | 2.69 | 89.77 | 13.48 | 89.83 | 45 | 90552 | 1220640.96 | 585315.08 | 635325.88 | 579 | nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-07 | 2025 | 11 | 7 | Daral Khwar HPS | 36.6 | 6 | 5.1 | 123500 | 121100 | 2.58 | 2.03 | 67.67 | 8.2683 | 86 | 48 | 755424 | 6246072.26 | 1001291.13 | 5244781.13 | 2400 | Unit No 01 was on bar delivering an average load equal to 5.1 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-07 | 2025 | 11 | 7 | Jabori HPS | 10.2 | 3.1 | 2.89 | 69597 | 67960 | 4.86 | 2.27 | 75.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 387997.23 | 1009614.93 | 1637 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-07 | 2025 | 11 | 7 | Karora HPS | 11.8 | 3 | 2.76 | 65574 | 63636 | 3.34 | 2.08 | 69.33 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 495088.08 | 1708207.92 | 1938 | Unit#01 remain on bar delivering power to the system as per available hydrology & Unit#02 is stands till due to low hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-07 | 2025 | 11 | 7 | Koto HPS | 40.8 | 7.72 | 3.39 | 77250 | 76177 | 27.5 | 13.49 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 627698.48 | 7440909.52 | 1073 | Plant was operational on average load of 3.39 MW and a maximum load of 7.72MW as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-07 | 2025 | 11 | 7 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 18.4 | 5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0856Hrs on 07-11-2025 due to low hydrological inflow, as canal water was diverted by the Irrigation Department in accordance with the weekly canal closure schedule. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-07 | 2025 | 11 | 7 | Malakand-3 HPS | 81 | 36 | 28.18 | 676406 | 669800 | 32.39 | 18.94 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1917436.46 | 3647652.34 | 6606 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-07 | 2025 | 11 | 7 | Pehur HPS | 18 | 11.97 | 10.14 | 243300 | 238000 | 12.8 | 15.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 896546 | 730798 | 5300 | Plant remained on partial load due to canal gates problem for 15 hours. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-07 | 2025 | 11 | 7 | Reshun HPS | 4.2 | 2.69 | 1.82 | 43000 | 42390 | 2.63 | 2.63 | 87.67 | 13.48 | 87.77 | 45 | 88468.8 | 1192559.42 | 571417.2 | 621142.22 | 610 | nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-08 | 2025 | 11 | 8 | Daral Khwar HPS | 36.6 | 6 | 5 | 120220 | 117820 | 2.58 | 1.97 | 65.67 | 8.2683 | 86 | 48 | 755424 | 6246072.26 | 974171.11 | 5271901.15 | 2400 | Unit No.01 was on bar delivering an average load equal to 5 MW according to the available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-08 | 2025 | 11 | 8 | Jabori HPS | 10.2 | 2.9 | 2.78 | 66938 | 65260 | 4.86 | 2.18 | 72.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 372582.39 | 1025029.77 | 1678 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-08 | 2025 | 11 | 8 | Karora HPS | 11.8 | 3.1 | 2.66 | 73089 | 61212 | 3.34 | 2 | 66.67 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 476229.36 | 1727066.64 | 11877 | Unit#01 is bar delivering power to the system as per available hydrology & Unit#02 is stands still due to less inflow. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-08 | 2025 | 11 | 8 | Koto HPS | 40.8 | 8.32 | 3.15 | 74552 | 73572 | 27.5 | 11.42 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 606233.28 | 7462374.72 | 980 | Koto Hydropower Complex was operational during the day. However low hydrology is affecting power generation. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-08 | 2025 | 11 | 8 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 18.4 | 5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0856Hrs on 07-11-2025 due to low hydrological inflow, as canal water was diverted by the Irrigation Department in accordance with the weekly canal closure schedule. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-08 | 2025 | 11 | 8 | Malakand-3 HPS | 81 | 26 | 24.1 | 578372 | 572460 | 32.39 | 15.86 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1638781.24 | 3926307.56 | 5912 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-08 | 2025 | 11 | 8 | Pehur HPS | 18 | 12 | 11.63 | 279200 | 271000 | 12.8 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1020857 | 606487 | 8200 | Plant remained operational throughout 24 hrs as per available hydrology + Irrigation valve open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-08 | 2025 | 11 | 8 | Reshun HPS | 4.2 | 2.83 | 1.85 | 43000 | 42385 | 2.63 | 2.63 | 87.67 | 13.48 | 87.77 | 45 | 88468.8 | 1192559.42 | 571349.8 | 621209.62 | 615 | line faults | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-09 | 2025 | 11 | 9 | Daral Khwar HPS | 36.6 | 6 | 4.8 | 115590 | 113190 | 2.58 | 1.89 | 63 | 8.2683 | 86 | 48 | 755424 | 6246072.26 | 935888.88 | 5310183.38 | 2400 | Unit No 01 was on bar delivering an average load equal to 4.8 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-09 | 2025 | 11 | 9 | Jabori HPS | 10.2 | 3 | 2.76 | 66332 | 64610 | 4.86 | 2.16 | 72 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 368871.41 | 1028740.75 | 1722 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-09 | 2025 | 11 | 9 | Karora HPS | 11.8 | 3 | 2.27 | 53534 | 51307 | 3.34 | 1.7 | 56.67 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 399168.46 | 1804127.54 | 2227 | the plant was operational on average load 2.27MW and a maximum load 3.0MW as per available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-09 | 2025 | 11 | 9 | Koto HPS | 40.8 | 7.22 | 3.85 | 95811 | 94731 | 27.5 | 14.88 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 780583.44 | 7288024.56 | 1080 | The plant was operational during the day and load was delivered to the system according to available hydrology. Low hydrology is the main issue of less generation. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-09 | 2025 | 11 | 9 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 18.4 | 5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0856Hrs on 07-11-2025 due to low hydrological inflow, as canal water was diverted by the Irrigation Department in accordance with the weekly canal closure schedule. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-09 | 2025 | 11 | 9 | Malakand-3 HPS | 81 | 23 | 22.16 | 531758 | 525910 | 32.39 | 14.38 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1505522.56 | 4059566.24 | 5848 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-09 | 2025 | 11 | 9 | Pehur HPS | 18 | 11.49 | 11.39 | 273400 | 268000 | 12.8 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 1009556 | 617788 | 5400 | Plant remained operational throughout 24 hrs as per available hydrology + Irrigation valve open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-09 | 2025 | 11 | 9 | Reshun HPS | 4.2 | 2.78 | 1.78 | 42000 | 41400 | 2.58 | 2.57 | 85.67 | 13.48 | 85.83 | 45 | 86520 | 1166289.6 | 558072 | 608217.6 | 600 | nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-10 | 2025 | 11 | 10 | Daral Khwar HPS | 36.6 | 5.8 | 4.7 | 112260 | 109860 | 2.58 | 1.84 | 61.33 | 8.2683 | 86 | 48 | 755424 | 6246072.26 | 908355.44 | 5337716.82 | 2400 | Unit No 01 was on bar delivering an average load equal to 4.7 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-10 | 2025 | 11 | 10 | Jabori HPS | 10.2 | 2.8 | 2.69 | 64611 | 62910 | 4.86 | 2.11 | 70.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 359165.77 | 1038446.39 | 1701 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-10 | 2025 | 11 | 10 | Karora HPS | 11.8 | 2.9 | 2.6 | 59825 | 57440 | 3.34 | 1.96 | 65.33 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 446883.2 | 1756412.8 | 2385 | The plant was operational on average load 2.6MW and a maximum load 2.9MW as per available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-10 | 2025 | 11 | 10 | Koto HPS | 40.8 | 7.25 | 3.58 | 90508 | 89428 | 27.5 | 13.57 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 736886.72 | 7331721.28 | 1080 | The Plant was operation on average load of 3.58 MW and Maximum load of 7.25 MW w.r.t available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-10 | 2025 | 11 | 10 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 18.4 | 3 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0856Hrs on 07-11-2025 due to low hydrological inflow, as canal water was diverted by the Irrigation Department in accordance with the weekly canal closure schedule. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-10 | 2025 | 11 | 10 | Malakand-3 HPS | 81 | 23 | 21.51 | 516286 | 510530 | 32.39 | 13.99 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1461494.23 | 4103594.57 | 5756 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-10 | 2025 | 11 | 10 | Pehur HPS | 18 | 11.35 | 11.29 | 270900 | 263000 | 12.8 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 990721 | 636623 | 7900 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-10 | 2025 | 11 | 10 | Reshun HPS | 4.2 | 2.79 | 1.69 | 40000 | 39410 | 2.45 | 2.45 | 81.6 | 13.48 | 81.7 | 45 | 82353.6 | 1110126.53 | 531246.8 | 578879.73 | 590 | work on Transmission line. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-11 | 2025 | 11 | 11 | Daral Khwar HPS | 36.6 | 5.5 | 4.5 | 108560 | 106960 | 2.58 | 1.79 | 59.67 | 8.2683 | 86 | 48 | 755424 | 6246072.26 | 884377.37 | 5361694.89 | 1600 | Unit No 01 was on bar delivering an average load equal to 4.5 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-11 | 2025 | 11 | 11 | Jabori HPS | 10.2 | 2.9 | 2.66 | 63937 | 62230 | 4.7 | 2.08 | 69.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 355283.52 | 1042328.64 | 1707 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-11 | 2025 | 11 | 11 | Karora HPS | 11.8 | 2.9 | 2.25 | 53459 | 51599 | 5.91 | 1.65 | 55 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 401440.22 | 1801855.78 | 1860 | the plant was operational on average load 2.25MW and a maximum load 2.9MW as per available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-11 | 2025 | 11 | 11 | Koto HPS | 40.8 | 7.4 | 3.54 | 84877 | 83557 | 27.5 | 12.48 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 688509.68 | 7380098.32 | 1320 | The plant was operational at average load of 3.54 and maximum load of 7.40 as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-11 | 2025 | 11 | 11 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 18.4 | 3 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0856Hrs on 07-11-2025 due to low hydrological inflow, as canal water was diverted by the Irrigation Department in accordance with the weekly canal closure schedule. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-11 | 2025 | 11 | 11 | Malakand-3 HPS | 81 | 21 | 20.4 | 489703 | 483530 | 32.39 | 13.21 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1384201.33 | 4180887.47 | 6173 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-11 | 2025 | 11 | 11 | Pehur HPS | 18 | 11.23 | 11.15 | 267500 | 260000 | 12.8 | 19 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 979420 | 647924 | 7500 | Plant remained operational throughout 24 hours as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-11 | 2025 | 11 | 11 | Reshun HPS | 4.2 | 2.81 | 1.83 | 44000 | 43400 | 2.7 | 2.69 | 89.77 | 13.48 | 89.83 | 45 | 90552 | 1220640.96 | 585032 | 635608.96 | 600 | nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-12 | 2025 | 11 | 12 | Daral Khwar HPS | 36.6 | 5.5 | 4.4 | 105770 | 102570 | 2.58 | 1.72 | 57.33 | 8.2683 | 86 | 48 | 755424 | 6246072.26 | 848079.53 | 5397992.73 | 3200 | Unit No 01 was on bar delivering an average load equal to 4.4 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-12 | 2025 | 11 | 12 | Jabori HPS | 10.2 | 3.2 | 2.5 | 61684 | 59970 | 4.7 | 2.01 | 67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 342380.72 | 1055231.44 | 1714 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-12 | 2025 | 11 | 12 | Karora HPS | 11.8 | 2.9 | 2.35 | 55538 | 53644 | 5.91 | 2.35 | 78.33 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 417350.32 | 1785945.68 | 1894 | the plant was operational on average load 2.32mw and maximum load 2.9mw as per available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-12 | 2025 | 11 | 12 | Koto HPS | 40.8 | 8.5 | 3.49 | 83787 | 82507 | 27.5 | 12.01 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 679857.68 | 7388750.32 | 1280 | The plant was operational with average load of 3.49 MW and maximum load of 8.5 MW. Insufficient hydrology is affecting the power generation. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-12 | 2025 | 11 | 12 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 18.4 | 3 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0856Hrs on 07-11-2025 due to low hydrological inflow, as canal water was diverted by the Irrigation Department in accordance with the weekly canal closure schedule. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-12 | 2025 | 11 | 12 | Malakand-3 HPS | 81 | 21 | 20.3 | 487124 | 480780 | 32.39 | 13.21 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1376328.91 | 4188759.89 | 6344 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-12 | 2025 | 11 | 12 | Pehur HPS | 18 | 11.12 | 11.05 | 265300 | 259000 | 12.8 | 19 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 975653 | 651691 | 6300 | Plant remained operational throughout 24 hours as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-12 | 2025 | 11 | 12 | Reshun HPS | 4.2 | 2.79 | 1.82 | 43000 | 42388 | 2.63 | 2.63 | 87.67 | 13.48 | 87.77 | 45 | 88468.8 | 1192559.42 | 571390.24 | 621169.18 | 612 | line works in Transmission Line. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-13 | 2025 | 11 | 13 | Daral Khwar HPS | 36.6 | 5.6 | 4.4 | 104850 | 102450 | 2.58 | 1.71 | 57 | 8.2683 | 86 | 48 | 755424 | 6246072.26 | 847087.34 | 5398984.92 | 2400 | Unit No 01 was on bar delivering an average load equal to 4.4 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-13 | 2025 | 11 | 13 | Jabori HPS | 10.2 | 3.7 | 2.5 | 61188 | 59510 | 4.7 | 1.99 | 66.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 339754.49 | 1057857.67 | 1678 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-13 | 2025 | 11 | 13 | Karora HPS | 11.8 | 2.8 | 2.36 | 53733 | 51875 | 5.91 | 1.78 | 59.33 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 403587.5 | 1799708.5 | 1858 | The plant was operational on average load 2.36MW and a Maximum load 2.85MW as per available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-13 | 2025 | 11 | 13 | Koto HPS | 40.8 | 7.83 | 3.61 | 86540 | 85200 | 27.5 | 11.14 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 702048 | 7366560 | 1340 | The plant was operational with maximum load of 8.70 MW and average load of 3.61 MW. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-13 | 2025 | 11 | 13 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 18.4 | 3 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0856Hrs on 07-11-2025 due to low hydrological inflow, as canal water was diverted by the Irrigation Department in accordance with the weekly canal closure schedule. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-13 | 2025 | 11 | 13 | Malakand-3 HPS | 81 | 21 | 19.86 | 476664 | 470160 | 32.39 | 12.89 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1345927.03 | 4219161.77 | 6504 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-13 | 2025 | 11 | 13 | Pehur HPS | 18 | 11.06 | 10.77 | 258500 | 252000 | 12.8 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 949284 | 678060 | 6500 | Plant remained operational throughout 24 hrs as per available hydrology + Irrigation valve open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-13 | 2025 | 11 | 13 | Reshun HPS | 4.2 | 2.81 | 1.8 | 42000 | 41388 | 2.57 | 2.57 | 85.67 | 13.48 | 85.8 | 45 | 86486.4 | 1165836.67 | 557910.24 | 607926.43 | 612 | nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-14 | 2025 | 11 | 14 | Daral Khwar HPS | 36.6 | 5.5 | 4.3 | 102170 | 99770 | 2.58 | 1.67 | 55.67 | 8.2683 | 86 | 48 | 755424 | 6246072.26 | 824928.29 | 5421143.97 | 2400 | Unit No 01 was on bar delivering an average load equal to 4.3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-14 | 2025 | 11 | 14 | Jabori HPS | 10.2 | 5.1 | 2.1 | 52688 | 51020 | 4.7 | 1.7 | 56.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 291283.38 | 1106328.78 | 1668 | Unit # 01 tripped once on dated 14-11-2025 due to fault in generator surface air cooler. Unit # 01 was synchronized with the National grid after replacing flow switch of generator surface air cooler which was found faulty. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-14 | 2025 | 11 | 14 | Karora HPS | 11.8 | 2.9 | 2.12 | 52877 | 51076 | 5.91 | 1.5 | 50 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 397371.28 | 1805924.72 | 1801 | the plant was operational mode max load.2.9MW at 19:00Hrs min load.0MW at 05:00Hrs average flow.1.50 Cumecs. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-14 | 2025 | 11 | 14 | Koto HPS | 40.8 | 7.45 | 3.4 | 81625 | 80125 | 27.5 | 10.5 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 660230 | 7408378 | 1500 | The plant was operational on average load of 3.40 MW and maximum load of 7.40 MW as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-14 | 2025 | 11 | 14 | Machai HPS | 2.6 | 0.12 | 0.09 | 2064 | 1956 | 18.4 | 9 | 3.31 | 4.671 | 100 | 70 | 62400 | 291470.4 | 9136.48 | 282333.92 | 108 | No data submitted for this date | engr.atifwazir@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-11-14 | 2025 | 11 | 14 | Malakand-3 HPS | 81 | 20 | 19.26 | 462295 | 456070 | 32.38 | 12.54 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1305591.59 | 4259497.21 | 6225 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-14 | 2025 | 11 | 14 | Pehur HPS | 18 | 10.87 | 10.8 | 259000 | 252000 | 12.8 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 949284 | 678060 | 7000 | Plant operational 24 hrs plus irrigation valves opening | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-14 | 2025 | 11 | 14 | Reshun HPS | 4.2 | 2.89 | 1.91 | 46000 | 45380 | 2.82 | 2.82 | 93.87 | 13.48 | 93.97 | 45 | 94718.4 | 1276804.03 | 611722.4 | 665081.63 | 620 | nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-15 | 2025 | 11 | 15 | Daral Khwar HPS | 36.6 | 5 | 4.3 | 102470 | 99670 | 2.58 | 1.67 | 55.67 | 8.2683 | 86 | 48 | 755424 | 6246072.26 | 824101.46 | 5421970.8 | 2800 | Unit No 01 was on bar delivering an average load equal to 4.3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-15 | 2025 | 11 | 15 | Jabori HPS | 10.2 | 2.8 | 2.4 | 57770 | 55980 | 4.7 | 1.82 | 60.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 319601.02 | 1078011.14 | 1790 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-15 | 2025 | 11 | 15 | Karora HPS | 11.8 | 2.9 | 2.1 | 49758 | 48001 | 5.91 | 1.58 | 52.67 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 373447.78 | 1829848.22 | 1757 | 1: Unit#01 is on bar delivering power to the system as per available flow. 2: Unit#01 was shutdown due to low hydrology at 05:40Hrs,12:20Hrs and 18:24Hrs, And synchronized to the system at 00:25Hrs,07:26Hrs ,14:05Hrs and 20:33Hrs Respectively.3: AT 19:28Hrs CB11 and CB12 tripped due to jerk from both line ( Dubair khwar and khan khwar)and DG set did not operat.E1Q1 and E2Q1 were opened on direction of RCC.The fault was on Allie,HPC line.4: Unit#02 is stand still due to low hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-15 | 2025 | 11 | 15 | Koto HPS | 40.8 | 7.07 | 2.62 | 62784 | 61264 | 27.5 | 8.08 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 504815.36 | 7563792.64 | 1520 | the plant was operational load of average load 2..62 and maximum load of 7.07 MW as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-15 | 2025 | 11 | 15 | Machai HPS | 2.6 | 0.57 | 0.2 | 4128 | 3912 | 18.4 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 18272.95 | 273197.45 | 216 | The Unit, after completion of all preliminary checks, was started as the rated head was restored due to increased canal discharge as per new indent. Unit synchronized with the system at 1242Hrs on 15-11-2025, and load was incrementally increased in accordance with prevailing system demand and operating conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-15 | 2025 | 11 | 15 | Malakand-3 HPS | 81 | 25 | 22.92 | 550095 | 544070 | 32.39 | 14.95 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1557509.19 | 4007579.61 | 6025 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-15 | 2025 | 11 | 15 | Pehur HPS | 18 | 10.79 | 10.67 | 256200 | 250000 | 12.8 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 941750 | 685594 | 6200 | Plant operational 24 hrs + irrigation valve open | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-15 | 2025 | 11 | 15 | Reshun HPS | 4.2 | 2.8 | 1.86 | 43000 | 42404 | 2.63 | 2.63 | 87.67 | 13.48 | 87.77 | 45 | 88468.8 | 1192559.42 | 571605.92 | 620953.5 | 596 | transmission lines works. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-16 | 2025 | 11 | 16 | Daral Khwar HPS | 36.6 | 5 | 4.2 | 101820 | 99420 | 2.58 | 1.66 | 55.33 | 8.2683 | 86 | 48 | 755424 | 6246072.26 | 822034.39 | 5424037.87 | 2400 | Unit No 01 was on bar delivering an average load equal to 4.2 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-16 | 2025 | 11 | 16 | Jabori HPS | 10.2 | 2.6 | 2.36 | 56680 | 54880 | 4.7 | 1.85 | 61.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 313320.9 | 1084291.26 | 1800 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-16 | 2025 | 11 | 16 | Karora HPS | 11.8 | 2.9 | 1.97 | 46850 | 45049 | 5.9 | 1.31 | 43.67 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 350481.22 | 1852814.78 | 1801 | unit#01 is on bar delivering power to the system as per available flow.while unit#02 is stands still due to low hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-16 | 2025 | 11 | 16 | Koto HPS | 40.8 | 7.55 | 2.71 | 64937 | 63577 | 27.5 | 8.36 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 523874.48 | 7544733.52 | 1360 | The plant was operational on average load of 2.71 MW and maximum load of 7.55 MW as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-16 | 2025 | 11 | 16 | Machai HPS | 2.6 | 0.54 | 0.6 | 11696 | 11000 | 18.4 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 51381 | 240089.4 | 696 | Unit remained on bar delivering power to National Grid tripped at 0804Hrs dated 16.11.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault. Unit synchronized with the system at 0832Hrs as 11KV Machai-HPS line re-energized at 0813Hrs | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-16 | 2025 | 11 | 16 | Malakand-3 HPS | 81 | 25 | 24.24 | 581806 | 576130 | 32.39 | 16 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1649287.35 | 3915801.45 | 5676 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-16 | 2025 | 11 | 16 | Pehur HPS | 18 | 11.41 | 10.65 | 255600 | 249000 | 12.8 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 937983 | 689361 | 6600 | Plant remained operational throughout 24 hrs as per available hydrology + Irrigation valve open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-16 | 2025 | 11 | 16 | Reshun HPS | 4.2 | 2.91 | 1.91 | 45000 | 44400 | 2.76 | 2.75 | 91.8 | 13.48 | 91.83 | 45 | 92568 | 1247816.64 | 598512 | 649304.64 | 600 | less hydrology | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-17 | 2025 | 11 | 17 | Daral Khwar HPS | 36.6 | 5 | 4.2 | 101230 | 98830 | 2.58 | 1.65 | 55 | 8.2683 | 86 | 48 | 755424 | 6246072.26 | 817156.09 | 5428916.17 | 2400 | Unit No 01 was on bar delivering an average load equal to 4.2 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-17 | 2025 | 11 | 17 | Jabori HPS | 10.2 | 2.5 | 2.34 | 56205 | 54400 | 4.7 | 1.84 | 61.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 310580.48 | 1087031.68 | 1805 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-17 | 2025 | 11 | 17 | Karora HPS | 11.8 | 2.9 | 2.12 | 45063 | 43356 | 5.9 | 1.41 | 47 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 337309.68 | 1865986.32 | 1707 | 1: unit#01 is on bar delivering power to the system as per available flow. 2:unit#01 was shutdown due to low hydrology at 01:16Hrs,08:06Hrs and 19:19Hrs,And synchronized to the system at 03:59Hrs,09:38Hrs,15:29Hrs and 21:19Hrs Respectively. 3: unit#02 shutdown due to punch list issues. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-17 | 2025 | 11 | 17 | Koto HPS | 40.8 | 7.2 | 3.07 | 73250 | 72178 | 27.5 | 10.93 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 594746.72 | 7473861.28 | 1072 | The plant was operational on average load of 3.07 and maximum load of 7.20 | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-17 | 2025 | 11 | 17 | Machai HPS | 2.6 | 0.54 | 0.5 | 8820 | 8276 | 18.4 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 38657.2 | 252813.2 | 544 | Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tipped at 0902Hrs dated 17-11-2025 due to the tripping of 11KV Machai-HPC feeder as PTW has been issued to Operation staff (PESCO) on KATLANG Grid..The 11 kV Machai-HPS line was re-energized at 1430Hrs after the PTW was canceled by the Operation Staff (PESCO). The unit was synchronized with the system at 1444Hrs, and the load was gradually increased according to the available inflow and prevailing system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-17 | 2025 | 11 | 17 | Malakand-3 HPS | 81 | 25 | 23.83 | 571940 | 565950 | 32.39 | 15.48 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1620145.06 | 3944943.74 | 5990 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-17 | 2025 | 11 | 17 | Pehur HPS | 18 | 11.44 | 9.83 | 236000 | 230000 | 12.8 | 17 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 866410 | 760934 | 6000 | At 1520 Hrs load on u#01 & 02 was reduced to 3.5 MW each upon the request of irrigation SDO to reduce the discharge up to 10 cms for the search of dead body in the canal. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-17 | 2025 | 11 | 17 | Reshun HPS | 4.2 | 2.84 | 1.78 | 43000 | 42424 | 2.63 | 2.63 | 87.67 | 13.48 | 87.77 | 45 | 88468.8 | 1192559.42 | 571875.52 | 620683.9 | 576 | nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-18 | 2025 | 11 | 18 | Daral Khwar HPS | 36.6 | 5 | 4.2 | 100020 | 97620 | 2.58 | 1.63 | 54.33 | 8.2683 | 86 | 48 | 755424 | 6246072.26 | 807151.45 | 5438920.81 | 2400 | Unit No 01 was on bar delivering an average load equal to 4.2 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-18 | 2025 | 11 | 18 | Jabori HPS | 10.2 | 2.4 | 2.3 | 55355 | 53520 | 4.7 | 1.8 | 60 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 305556.38 | 1092055.78 | 1835 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-18 | 2025 | 11 | 18 | Karora HPS | 11.8 | 2.9 | 1.89 | 88505 | 85069 | 5.9 | 1.25 | 41.67 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 661836.82 | 1541459.18 | 3436 | 1: unit#01 is on bar delivering power to the system as per available flow. 2:unit#01 was shutdown due to low hydrology at 07:22Hrs,12:14Hrs,unit#01 tripped due to -ne sequence 13:26Hrs and synchronized to the system at 03:40Hrs,12:18Hrs,15:56Hrs and 21:15Hrs Respectively. 3: unit#02 shutdown due to punch list issues. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-18 | 2025 | 11 | 18 | Koto HPS | 40.8 | 7.05 | 3.15 | 75250 | 74294 | 27.5 | 12.53 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 612182.56 | 7456425.44 | 956 | Plant was operational on average load of 3.15 and maximum load of 7.05 | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-18 | 2025 | 11 | 18 | Machai HPS | 2.6 | 0.6 | 0.45 | 10380 | 9768 | 18.4 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 45626.33 | 245844.07 | 612 | Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tipped at 0950Hrs dated 18-11-2025 due to the tripping of 11KV Machai-HPC feeder as PTW has been issued to Operation staff (PESCO) on KATLANG Grid.The 11 kV Machai-HPS line was re-energized at 1329Hrs after the PTW was canceled by the Operation Staff (PESCO). The unit was synchronized with the system at 1335Hrs, and the load was gradually increased according to the available inflow and prevailing system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-18 | 2025 | 11 | 18 | Malakand-3 HPS | 81 | 25 | 23.43 | 562317 | 556730 | 32.39 | 15.2 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1593750.97 | 3971337.83 | 5587 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-18 | 2025 | 11 | 18 | Pehur HPS | 18 | 11.6 | 8.46 | 203100 | 198000 | 12.8 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 745866 | 881478 | 5100 | At 0935 Hrs u#01 & 02 were taken off the bar upon the request of irrigation SDO to completely stop the discharge for the search of dead body in the canal. After the recovery of dead body, both the units were taken on bar at 1125 & 1210 Hrs with total load 11.40 MW. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-18 | 2025 | 11 | 18 | Reshun HPS | 4.2 | 2.92 | 1.77 | 42000 | 41404 | 2.58 | 2.57 | 85.67 | 13.48 | 85.83 | 45 | 86520 | 1166289.6 | 558125.92 | 608163.68 | 596 | work in transmission line at Village Awi. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-19 | 2025 | 11 | 19 | Daral Khwar HPS | 36.6 | 5 | 4 | 95760 | 93360 | 2.58 | 1.56 | 52 | 8.2683 | 86 | 48 | 755424 | 6246072.26 | 771928.49 | 5474143.77 | 2400 | Unit No 01 was on bar delivering an average load equal to 4 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-19 | 2025 | 11 | 19 | Jabori HPS | 10.2 | 2.4 | 2.3 | 56100 | 54240 | 4.7 | 1.83 | 61 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 309667.01 | 1087945.15 | 1860 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-19 | 2025 | 11 | 19 | Karora HPS | 11.8 | 2.9 | 1.88 | 39273 | 37643 | 5.9 | 1.33 | 44.33 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 292862.54 | 1910433.46 | 1630 | unit #01 is on bar delivering power to the system as per available flow.while unit#02 shutdown due to punch list. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-19 | 2025 | 11 | 19 | Koto HPS | 40.8 | 7.78 | 3 | 71000 | 70757 | 27.5 | 9.06 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 583037.68 | 7485570.32 | 243 | Plant was operational on average load of 3.00 and maximum load of 7.78 | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-19 | 2025 | 11 | 19 | Machai HPS | 2.6 | 0.7 | 0.5 | 11596 | 10800 | 18.4 | 16 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 50446.8 | 241023.6 | 796 | 1.The unit, while on bar and delivering power to the National Grid as per available water inflow and prevailing system conditions, tripped at 0856Hrs on 19.11.2025 due to reverse power resulting from high system voltage. Subsequently, the unit remained shut down/standby and could not be synchronized with the system due to persistently high system voltage. The unit was finally synchronized with the system at 0926Hr, once the voltage stabilized. 2.The Unit being on bar delivering power to National Grid as per available water inflow and system conditions, got tripped at 1059Hrs dated 19.11.2025 due to the tripping of 11KV Machai-HPS feeder on earth fault.11KV Machai-HPS line energized at 1104Hrs. Subsequently, the unit remained shut down/standby and could not be synchronized with the system due to persistently high system voltage. The unit was finally synchronized with the system at 1236Hr, once the voltage stabilized. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-19 | 2025 | 11 | 19 | Malakand-3 HPS | 81 | 24 | 23.12 | 554897 | 549230 | 32.39 | 15.15 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1572280.72 | 3992808.08 | 5667 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-19 | 2025 | 11 | 19 | Pehur HPS | 18 | 11.27 | 11.11 | 266700 | 260000 | 12.8 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 979420 | 647924 | 6700 | Plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-19 | 2025 | 11 | 19 | Reshun HPS | 4.2 | 2.89 | 1.84 | 43000 | 42419 | 2.57 | 2.57 | 85.67 | 13.48 | 85.8 | 45 | 86486.4 | 1165836.67 | 571808.12 | 594028.55 | 581 | Nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-20 | 2025 | 11 | 20 | Daral Khwar HPS | 36.6 | 4.3 | 4 | 96250 | 93450 | 2.58 | 1.56 | 52 | 8.2683 | 86 | 48 | 755424 | 6246072.26 | 772672.64 | 5473399.62 | 2800 | 1. Unit No.01 were on bar delivering an average load equal to 4.0 MW according to the available hydrology. 2. Unit No. 01 was stopped at 11:03 Hrs as per NOC for annual maintenance of transmission line 132KV Barikot Swat T/Line controlling breaker BKT-1 at 132 KV GSS Barikot and isolator-101 at 132 KV GSS Swat. 3. 132 KV Supply line was restored at 11:20 Hrs and Unit No.01 was synchronized with the national grid at 11:28 Hrs. 4. Unit No. 01 was stopped again at 14:51 Hrs as per NOC for annual maintenance of transmission line 132KV Barikot Swat T/Line controlling breaker BKT-1 at 132 KV GSS Barikot and isolator-101 at 132 KV GSS Swat. 5. 132 KV Supply line was restored at 15:03 Hrs and Unit No.01 was synchronized with the national grid at 15:09 Hrs. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-20 | 2025 | 11 | 20 | Jabori HPS | 10.2 | 2.4 | 2.27 | 54570 | 52800 | 4.7 | 1.78 | 59.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 301445.76 | 1096166.4 | 1770 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-20 | 2025 | 11 | 20 | Karora HPS | 11.8 | 2.9 | 2 | 46459 | 44692 | 5.9 | 1.5 | 50 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 347703.76 | 1855592.24 | 1767 | 1: unit#01 is on bar delivering power to the system as per available flow. 2: unit#01 was shut down due to low hydrology at 03:53Hrs,09:37Hrs,14:26Hrs,18;46Hrs,and 23;28Hrs.And synchronized to the system at 00;35Hrs,06:11Hrs 11:03Hrs,15:26Hrs and 20:18Hrs Respectively. 3: unit#02 shutdown due to punch list issue. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-20 | 2025 | 11 | 20 | Koto HPS | 40.8 | 7.1 | 3 | 71933 | 70593 | 27.5 | 9.26 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 581686.32 | 7486921.68 | 1340 | The plant was operational on average load of 3.00 MW and maximum load of 7.10 MW as per available hydrology. | rekotohpc@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-11-20 | 2025 | 11 | 20 | Machai HPS | 2.6 | 0.62 | 0.5 | 12448 | 11728 | 18.4 | 16 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 54781.49 | 236688.91 | 720 | Unit remained on bar delivering power to National Grid as per available inflow and system conditions | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-20 | 2025 | 11 | 20 | Malakand-3 HPS | 81 | 24 | 23.05 | 553100 | 547320 | 32.39 | 15.06 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1566812.96 | 3998275.84 | 5780 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-20 | 2025 | 11 | 20 | Pehur HPS | 18 | 11.01 | 10.95 | 262800 | 256000 | 12.8 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 964352 | 662992 | 6800 | Plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-20 | 2025 | 11 | 20 | Reshun HPS | 4.2 | 2.86 | 1.76 | 42000 | 41390 | 2.57 | 2.57 | 85.67 | 13.48 | 85.77 | 45 | 86452.8 | 1165383.74 | 557937.2 | 607446.54 | 610 | outgoing feeder breaker tripped due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-21 | 2025 | 11 | 21 | Daral Khwar HPS | 36.6 | 4.2 | 3.8 | 91070 | 89070 | 2.58 | 1.49 | 49.67 | 8.2683 | 86 | 48 | 755424 | 6246072.26 | 736457.48 | 5509614.78 | 2000 | Unit No 01 was on bar delivering an average load equal to 3.8 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-21 | 2025 | 11 | 21 | Jabori HPS | 10.2 | 2.4 | 2.2 | 53540 | 51740 | 4.42 | 1.75 | 58.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 295394.01 | 1102218.15 | 1800 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-21 | 2025 | 11 | 21 | Karora HPS | 11.8 | 2.9 | 2.23 | 48277 | 46415 | 2.95 | 1.59 | 53 | 7.78 | 98.33 | 0.69 | 278480 | 2166574.4 | 361108.7 | 1805465.7 | 1862 | 1: unit#01 is on bar delivering power to the system as per available flow. 2: unit#01 was normaly shut down due to low hydrology at 03:09Hrs,07:59Hrs,12:43Hrs,17:22Hrs and 21:58Hrs. And unit#01 start and synchronized to the system at 00:18Hrs,04:36Hrs,09:10Hrs,13:51Hrs,18:44Hrs and 23:11Hrs Respectively.3: Unit#01 tripped on GCB open -ve sequence at 10:35Hrs and 16:34Hrs Again synch to the system. 4: unit#02 shut down due to punch list issue. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-21 | 2025 | 11 | 21 | Koto HPS | 40.8 | 7.15 | 2.93 | 70227 | 68787 | 27.5 | 9.04 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 566804.88 | 7501803.12 | 1440 | The plant was operational with average load of 2.93 and maximum load of 7.15 with reference to available hydrology | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-21 | 2025 | 11 | 21 | Machai HPS | 2.6 | 0.57 | 0.5 | 11896 | 11068 | 18.4 | 15.5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 51698.63 | 239771.77 | 828 | Unit remained on bar delivering power to National Grid as per available inflow and system conditions | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-21 | 2025 | 11 | 21 | Malakand-3 HPS | 81 | 24 | 22.74 | 545766 | 539470 | 32.39 | 14.82 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1544340.77 | 4020748.03 | 6296 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-21 | 2025 | 11 | 21 | Pehur HPS | 18 | 10.89 | 10.05 | 241200 | 235 | 12.8 | 17 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 885.24 | 1626458.76 | 240965 | Plant remained operational throughout 24 hrs as per available hydrology and Irrigation valve is open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-21 | 2025 | 11 | 21 | Reshun HPS | 4.2 | 3.04 | 1.88 | 43000 | 42398 | 2.63 | 2.63 | 87.67 | 13.48 | 87.77 | 45 | 88468.8 | 1192559.42 | 571525.04 | 621034.38 | 602 | nil | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-22 | 2025 | 11 | 22 | Daral Khwar HPS | 36.6 | 4.5 | 3.8 | 90320 | 87920 | 2.58 | 1.47 | 49 | 8.2683 | 86 | 48 | 755424 | 6246072.26 | 726948.94 | 5519123.32 | 2400 | Unit No 01 was on bar delivering an average load equal to 3.8 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-22 | 2025 | 11 | 22 | Jabori HPS | 10.2 | 2.3 | 2.19 | 52572 | 50750 | 4.42 | 1.71 | 57 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 289741.9 | 1107870.26 | 1822 | Plant was operational as per available hydrology | faizanbabar5@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-11-22 | 2025 | 11 | 22 | Karora HPS | 11.8 | 2.9 | 2.36 | 48179 | 46280 | 2.95 | 1.6 | 53.33 | 7.78 | 98.33 | 0.69 | 278480 | 2166574.4 | 360058.4 | 1806516 | 1899 | the plant was operation mode. Max load 2.9MW Min load 0MW due to low hydrology | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-22 | 2025 | 11 | 22 | Koto HPS | 40.8 | 7.22 | 2.89 | 69252 | 67872 | 27.5 | 8.91 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 559265.28 | 7509342.72 | 1380 | The plant was operational on average load of 2.89 MW and maximum load of 7.22 MW, with reference to available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-22 | 2025 | 11 | 22 | Machai HPS | 2.6 | 0.5 | 0.39 | 9372 | 8888 | 18.4 | 9 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 41515.85 | 249954.55 | 484 | The unit, while on bar and delivering power to the National Grid, was shut down at 2200Hrs on 22-11-2025 as a precautionary measure due to a significant reduction in canal inflow as communicated by the Irrigation Department. As per Canal Wire No. 929-7 dated 21-11-2025 issued by SDO Dargai, water supply to Machai Branch was reduced to 488 cusecs, and Abazai Branch was to be operated at 2.80 = 532 cusecs. It was further instructed that RD-95+000 Machai Branch towards Swabi Division be kept closed, while the weekly canal closure for Machai was scheduled on 23-11-2025. In view of the reduced discharge, the unit was safely taken off-bar and will remain on standby until restoration of adequate canal flow by the Irrigation Department. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-22 | 2025 | 11 | 22 | Malakand-3 HPS | 81 | 24 | 22.53 | 540730 | 534710 | 32.39 | 14.7 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1530714.32 | 4034374.48 | 6020 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-22 | 2025 | 11 | 22 | Pehur HPS | 18 | 9.57 | 9.4 | 225700 | 220000 | 12.8 | 16.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 828740 | 798604 | 5700 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-22 | 2025 | 11 | 22 | Reshun HPS | 4.2 | 2.92 | 1.96 | 42000 | 41405 | 2.57 | 2.57 | 85.67 | 13.48 | 85.77 | 45 | 86452.8 | 1165383.74 | 558139.4 | 607244.34 | 595 | less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-23 | 2025 | 11 | 23 | Daral Khwar HPS | 36.6 | 4.5 | 3.6 | 86300 | 83900 | 2.58 | 1.4 | 46.67 | 8.2683 | 86 | 48 | 755424 | 6246072.26 | 693710.37 | 5552361.89 | 2400 | Unit No 01 was on bar delivering an average load equal to 3.6 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-23 | 2025 | 11 | 23 | Jabori HPS | 10.2 | 2.2 | 2.18 | 52459 | 50590 | 4.42 | 1.71 | 57 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 288828.43 | 1108783.73 | 1869 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-23 | 2025 | 11 | 23 | Karora HPS | 11.8 | 2.9 | 2.11 | 46380 | 44481 | 2.95 | 1.59 | 53 | 7.78 | 98.33 | 0.69 | 278480 | 2166574.4 | 346062.18 | 1820512.22 | 1899 | the plant was operation mode on power delivering to the system Max load 2.9MW Min load 0MW Average 2.11 | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-23 | 2025 | 11 | 23 | Koto HPS | 40.8 | 6.88 | 2.89 | 68728 | 67308 | 27.5 | 8.84 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 554617.92 | 7513990.08 | 1420 | The plant was operational on average load of 2.89 MW and maximum load of 6.88 MW, with reference to available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-23 | 2025 | 11 | 23 | Machai HPS | 2.6 | 0.26 | 0.2 | 4686 | 4444 | 18.4 | 6 | 7.51 | 4.671 | 100 | 70 | 62400 | 291470.4 | 20757.92 | 270712.48 | 242 | No data submitted for this date | engr.atifwazir@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-11-23 | 2025 | 11 | 23 | Malakand-3 HPS | 81 | 23 | 17.76 | 426290 | 420110 | 32.39 | 11.82 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1202648.9 | 4362439.9 | 6180 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-23 | 2025 | 11 | 23 | Pehur HPS | 18 | 9.86 | 9.3 | 223100 | 217000 | 12.8 | 16.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 817439 | 809905 | 6100 | plant operational 24 hours plus irrigation valve open | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-23 | 2025 | 11 | 23 | Reshun HPS | 4.2 | 2.86 | 1.9 | 42000 | 41398 | 2.57 | 2.57 | 85.67 | 13.48 | 85.73 | 45 | 86419.2 | 1164930.82 | 558045.04 | 606885.78 | 602 | less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-24 | 2025 | 11 | 24 | Daral Khwar HPS | 36.6 | 4.5 | 3.5 | 85180 | 82780 | 2.58 | 1.38 | 46 | 8.2683 | 86 | 48 | 755424 | 6246072.26 | 684449.87 | 5561622.38 | 2400 | Unit No 01 was on bar delivering an average load equal to 3.5 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-24 | 2025 | 11 | 24 | Jabori HPS | 10.2 | 2.2 | 2.17 | 52151 | 50340 | 4.42 | 1.7 | 56.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 287401.13 | 1110211.03 | 1811 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-24 | 2025 | 11 | 24 | Karora HPS | 11.8 | 2.9 | 2.12 | 45791 | 43849 | 2.95 | 1.42 | 47.33 | 7.78 | 98.33 | 0.69 | 278480 | 2166574.4 | 341145.22 | 1825429.18 | 1942 | the plant was operational on average load of 2.12 mw and maximum load of 2.9 mw as per available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-24 | 2025 | 11 | 24 | Koto HPS | 40.8 | 7.13 | 3.39 | 81355 | 79835 | 27.5 | 10.47 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 657840.4 | 7410767.6 | 1520 | The plant was operational on average load of 3.39 MW and maximum load of 7.13 MW, according to the available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-24 | 2025 | 11 | 24 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 18.4 | 3 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 2200 Hrs on 22-11-2025 due to low hydrological inflow, as canal water was diverted by the Irrigation Department on 23-11-2025 from Machai Canal to Abazai Canal in accordance with the weekly canal closure schedule | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-24 | 2025 | 11 | 24 | Malakand-3 HPS | 81 | 17 | 15.89 | 381307 | 374560 | 32.39 | 10.69 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1072252.91 | 4492835.89 | 6747 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-24 | 2025 | 11 | 24 | Pehur HPS | 18 | 8.78 | 8.22 | 197400 | 193000 | 12.8 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 727031 | 900313 | 4400 | The plant remained operational throughout 24 hours as per available hydrology and irrigation valve is open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-24 | 2025 | 11 | 24 | Reshun HPS | 4.2 | 3.09 | 1.79 | 41000 | 40410 | 2.51 | 2.51 | 83.67 | 13.48 | 83.73 | 45 | 84403.2 | 1137755.14 | 544726.8 | 593028.34 | 590 | Transmission line work at Parwak. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-25 | 2025 | 11 | 25 | Daral Khwar HPS | 36.6 | 4.5 | 3.4 | 82650 | 80250 | 2.58 | 1.34 | 44.67 | 8.2683 | 86 | 48 | 755424 | 6246072.26 | 663531.07 | 5582541.18 | 2400 | Unit No 01 was on bar delivering an average load equal to 3.4 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-25 | 2025 | 11 | 25 | Jabori HPS | 10.2 | 2.3 | 2.15 | 51764 | 49790 | 4.42 | 1.69 | 56.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 284261.07 | 1113351.09 | 1974 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-25 | 2025 | 11 | 25 | Karora HPS | 11.8 | 2.9 | 2.12 | 46855 | 44785 | 2.95 | 1.51 | 50.33 | 7.78 | 98.33 | 0.69 | 278480 | 2166574.4 | 348427.3 | 1818147.1 | 2070 | the plant was operational on average load 2.12 mw and maximum load of 2.9 mw as per available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-25 | 2025 | 11 | 25 | Koto HPS | 40.8 | 7.28 | 2.75 | 66026 | 64406 | 27.5 | 8.5 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 530705.44 | 7537902.56 | 1620 | The plant was operational on average load of 2.75 MW and maximum load of 7.28 MW, according to the available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-25 | 2025 | 11 | 25 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 18.4 | 3 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 2200 Hrs on 22-11-2025 due to low hydrological inflow, as canal water was diverted by the Irrigation Department on 23-11-2025 from Machai Canal to Abazai Canal in accordance with the weekly canal closure schedule | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-11-25 | 2025 | 11 | 25 | Malakand-3 HPS | 81 | 17 | 15.63 | 375077 | 368350 | 32.39 | 10.55 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1054475.54 | 4510613.26 | 6727 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-25 | 2025 | 11 | 25 | Pehur HPS | 18 | 8.07 | 7.99 | 191800 | 186000 | 12.8 | 16 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 700662 | 926682 | 5800 | Plant remained operational 24 hrs as per available hydrology and Generation is less because of Irrigation valve opening. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-25 | 2025 | 11 | 25 | Reshun HPS | 4.2 | 3.07 | 1.8 | 43000 | 42400 | 2.53 | 2.63 | 87.67 | 13.48 | 84.37 | 45 | 85041.6 | 1146360.77 | 571552 | 574808.77 | 600 | Transmission lines works at village Parwak. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-26 | 2025 | 11 | 26 | Daral Khwar HPS | 36.6 | 4.5 | 3.4 | 82460 | 79660 | 2.58 | 1.33 | 44.33 | 8.2683 | 86 | 48 | 755424 | 6246072.26 | 658652.78 | 5587419.48 | 2800 | Unit No 01 was on bar delivering an average load equal to 3.4 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-26 | 2025 | 11 | 26 | Jabori HPS | 10.2 | 2.3 | 2.15 | 51737 | 49780 | 4.42 | 1.69 | 56.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 284203.98 | 1113408.18 | 1957 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-26 | 2025 | 11 | 26 | Karora HPS | 11.8 | 2.9 | 2.12 | 46015 | 43975 | 2.95 | 1.51 | 50.33 | 7.78 | 98.33 | 0.69 | 278480 | 2166574.4 | 342125.5 | 1824448.9 | 2040 | the plant was operational on average load of 2.12 mw and maximum load of 2.9 mw as per available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-26 | 2025 | 11 | 26 | Koto HPS | 40.8 | 7.03 | 3.27 | 78400 | 76760 | 27.5 | 10.09 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 632502.4 | 7436105.6 | 1640 | The plant was operational an average load of 3.27 MW as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-26 | 2025 | 11 | 26 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 18.4 | 3 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 2200 Hrs on 22-11-2025 due to low hydrological inflow, as canal water was diverted by the Irrigation Department on 23-11-2025 from Machai Canal to Abazai Canal in accordance with the weekly canal closure schedule | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-11-26 | 2025 | 11 | 26 | Malakand-3 HPS | 81 | 16 | 15.29 | 367045 | 360360 | 32.39 | 10.38 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1031602.57 | 4533486.23 | 6685 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-26 | 2025 | 11 | 26 | Pehur HPS | 18 | 8.08 | 7.96 | 191000 | 186000 | 12.8 | 16 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 700662 | 926682 | 5000 | Plant operational 24 hours + valve open | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-26 | 2025 | 11 | 26 | Reshun HPS | 4.2 | 3.15 | 1.89 | 43000 | 42388 | 2.53 | 2.63 | 87.67 | 13.48 | 84.33 | 45 | 85008 | 1145907.84 | 571390.24 | 574517.6 | 612 | outgoing feeder breaker remained off for 01hour due to less hydrology.. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-27 | 2025 | 11 | 27 | Daral Khwar HPS | 36.6 | 4.5 | 3.5 | 84350 | 81550 | 2.58 | 1.36 | 45.33 | 8.2683 | 86 | 48 | 755424 | 6246072.26 | 674279.86 | 5571792.39 | 2800 | Unit No 01 was on bar delivering an average load equal to 3.5 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-27 | 2025 | 11 | 27 | Jabori HPS | 10.2 | 2.3 | 2.12 | 50951 | 48990 | 4.42 | 1.66 | 55.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 279693.71 | 1117918.45 | 1961 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-27 | 2025 | 11 | 27 | Karora HPS | 11.8 | 2.9 | 2.13 | 44590 | 42595 | 2.95 | 1.51 | 50.33 | 7.78 | 98.33 | 0.69 | 278480 | 2166574.4 | 331389.1 | 1835185.3 | 1995 | the plant was operational on average load of 2.13 mw and maximum load of 2.9mw as per available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-27 | 2025 | 11 | 27 | Koto HPS | 40.8 | 7 | 2.64 | 63331 | 61631 | 27.5 | 8.15 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 507839.44 | 7560768.56 | 1700 | The plant was operational an average load of 2.64 MW and maximum load of 7.0 MW as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-27 | 2025 | 11 | 27 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 18.4 | 3 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 2200 Hrs on 22-11-2025 due to low hydrological inflow, as canal water was diverted by the Irrigation Department on 23-11-2025 from Machai Canal to Abazai Canal in accordance with the weekly canal closure schedule | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load; Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-11-27 | 2025 | 11 | 27 | Malakand-3 HPS | 81 | 16 | 15.19 | 364661 | 357960 | 32.39 | 10.21 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1024732.09 | 4540356.71 | 6701 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-27 | 2025 | 11 | 27 | Pehur HPS | 18 | 8.13 | 7.98 | 191500 | 186000 | 12.8 | 16 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 700662 | 926682 | 5500 | Plant operational 24 hrs + valve open | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-27 | 2025 | 11 | 27 | Reshun HPS | 4.2 | 3.02 | 1.87 | 42000 | 41419 | 2.52 | 2.57 | 85.67 | 13.48 | 84.17 | 45 | 84840 | 1143643.2 | 558328.12 | 585315.08 | 581 | less hydrology, Booni and Mastuj Line section connected with Feeder No. II for 2 hours (9:00am to. 11:05 am).. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-28 | 2025 | 11 | 28 | Daral Khwar HPS | 36.6 | 4.5 | 3.2 | 76120 | 73320 | 2.58 | 1.23 | 41 | 8.2683 | 86 | 48 | 755424 | 6246072.26 | 606231.76 | 5639840.5 | 2800 | Unit No 01 was on bar delivering an average load equal to 3.2 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-28 | 2025 | 11 | 28 | Jabori HPS | 10.2 | 2.1 | 2.09 | 50297 | 48400 | 4.42 | 1.64 | 54.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 276325.28 | 1121286.88 | 1897 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-28 | 2025 | 11 | 28 | Karora HPS | 11.8 | 2.9 | 1.89 | 42807 | 40778 | 2.95 | 1.33 | 44.33 | 7.78 | 98.33 | 0.69 | 278480 | 2166574.4 | 317252.84 | 1849321.56 | 2029 | the plant was operational on average load of 1.89mw and maximum load of 2.9mw as per available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-28 | 2025 | 11 | 28 | Koto HPS | 40.8 | 6.93 | 3.05 | 73215 | 71535 | 27.5 | 9.42 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 589448.4 | 7479159.6 | 1680 | The plant was operational an average load of 3.05 MW and maximum load of 6.93 MW as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-28 | 2025 | 11 | 28 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 18.4 | 3 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | No data submitted for this date | engr.atifwazir@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-11-28 | 2025 | 11 | 28 | Malakand-3 HPS | 81 | 16 | 14.94 | 358506 | 351720 | 32.39 | 10.17 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1006868.84 | 4558219.96 | 6786 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-28 | 2025 | 11 | 28 | Pehur HPS | 18 | 8.03 | 8 | 192300 | 188000 | 12.8 | 16 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 708196 | 919148 | 4300 | Plant remained operational 24 hrs as per available hydrology and Generation is less because of Irrigation valve opening. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-28 | 2025 | 11 | 28 | Reshun HPS | 4.2 | 3.17 | 1.93 | 41000 | 40410 | 2.5 | 2.51 | 83.67 | 13.48 | 83.33 | 45 | 84000 | 1132320 | 544726.8 | 587593.2 | 590 | (1). outgoing feeder breaker tripped 01time. (2). outoing feeder breaker remaind Off 2 times for storage of water due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-29 | 2025 | 11 | 29 | Daral Khwar HPS | 36.6 | 4.5 | 3.2 | 77670 | 74870 | 2.58 | 1.25 | 41.67 | 8.2683 | 86 | 48 | 755424 | 6246072.26 | 619047.62 | 5627024.64 | 2800 | Unit No 01 was on bar delivering an average load equal to 3.2 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-29 | 2025 | 11 | 29 | Jabori HPS | 10.2 | 2.1 | 2.07 | 49880 | 48070 | 4.42 | 1.63 | 54.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 274441.24 | 1123170.92 | 1810 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-29 | 2025 | 11 | 29 | Karora HPS | 11.8 | 2.9 | 1.88 | 44245 | 42271 | 2.95 | 1.33 | 44.33 | 7.78 | 98.33 | 0.69 | 278480 | 2166574.4 | 328868.38 | 1837706.02 | 1974 | the plant was operational on average load of 1.88mw and maximum load of 2.9mw is per available hydrology | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-29 | 2025 | 11 | 29 | Koto HPS | 40.8 | 7.07 | 2.73 | 65605 | 64265 | 27.5 | 10.88 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 529543.6 | 7539064.4 | 1340 | Plant was operational on average load of 2.73 and maximum load of 7.07 | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-29 | 2025 | 11 | 29 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 18.4 | 3 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | No data submitted for this date | engr.atifwazir@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-11-29 | 2025 | 11 | 29 | Malakand-3 HPS | 81 | 15 | 14.56 | 349374 | 342800 | 32.39 | 9.9 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 981333.56 | 4583755.24 | 6574 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-29 | 2025 | 11 | 29 | Pehur HPS | 18 | 8.19 | 8.03 | 192800 | 188000 | 12.8 | 16 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 708196 | 919148 | 4800 | Plant remained operational throughout 24 Hrs as per available hydrology + irrigation valve open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-29 | 2025 | 11 | 29 | Reshun HPS | 4.2 | 3.13 | 1.64 | 40000 | 39419 | 2.45 | 2.45 | 81.6 | 13.48 | 81.7 | 45 | 82353.6 | 1110126.53 | 531368.12 | 578758.41 | 581 | due to less hydrology the Booni Mastuj Section connected with Feeder No. II for 3.25hours. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-30 | 2025 | 11 | 30 | Daral Khwar HPS | 36.6 | 4.2 | 3.2 | 77060 | 74260 | 2.58 | 1.24 | 41.33 | 8.2683 | 86 | 48 | 755424 | 6246072.26 | 614003.96 | 5632068.3 | 2800 | Unit No 01 was on bar delivering an average load equal to 3.2 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-30 | 2025 | 11 | 30 | Jabori HPS | 10.2 | 2.1 | 2.05 | 49414 | 47570 | 4.42 | 1.61 | 53.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 271586.64 | 1126025.52 | 1844 | Plant was operational as per available hydrology | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-30 | 2025 | 11 | 30 | Karora HPS | 11.8 | 2.9 | 1.88 | 42324 | 40349 | 2.95 | 1.42 | 47.33 | 7.78 | 98.33 | 0.69 | 278480 | 2166574.4 | 313915.22 | 1852659.18 | 1975 | the plant was aperationl on average load of 1.88mw and maximum load of 2.9mw as per available hydrology | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-30 | 2025 | 11 | 30 | Koto HPS | 40.8 | 7.22 | 2.28 | 53750 | 52977 | 27.5 | 10.12 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 436530.48 | 7632077.52 | 773 | Plant was operational on average load of 2.28 MW and maximum load of 7.22 MW | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-30 | 2025 | 11 | 30 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 18.4 | 3 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 2200 Hrs on 22-11-2025 due to low hydrological inflow, as canal water was diverted by the Irrigation Department on 23-11-2025 from Machai Canal to Abazai Canal in accordance with the weekly canal closure schedule | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-11-30 | 2025 | 11 | 30 | Malakand-3 HPS | 81 | 15 | 14.47 | 347280 | 341330 | 32.39 | 9.87 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 977125.39 | 4587963.41 | 5950 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-30 | 2025 | 11 | 30 | Pehur HPS | 18 | 8.1 | 7.92 | 190000 | 184000 | 12.8 | 16.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 693128 | 934216 | 6000 | Plant remained operational throughout 24 Hrs as per available hydrology + Irrigation valve open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-11-30 | 2025 | 11 | 30 | Reshun HPS | 4.2 | 3.07 | 1.79 | 44000 | 43415 | 2.45 | 2.69 | 89.77 | 13.48 | 81.67 | 45 | 82320 | 1109673.6 | 585234.2 | 524439.4 | 585 | outgoing feeder breaker reamained Off 3time due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-01 | 2025 | 12 | 1 | Daral Khwar HPS | 36.6 | 4.5 | 3.2 | 151340 | 75670 | 1.62 | 1.22 | 17.23 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 625662.26 | 3296290.09 | 75670 | Unit No 01 was on bar delivering an average load equal to 3.2 MW according to available hydrology. | passion.to.programe@gmail.com | Original | Units = Net + Aux; Plant factor recalculated | Link_Generation_Data_Summary.xlsx
2025-12-01 | 2025 | 12 | 1 | Jabori HPS | 10.2 | 2.1 | 2.01 | 48338 | 46500 | 4.66 | 1.57 | 52.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 265477.8 | 1132134.36 | 1838 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-01 | 2025 | 12 | 1 | Karora HPS | 11.8 | 2.9 | 1.65 | 40837 | 38908 | 2.21 | 1.24 | 41.33 | 7.78 | 73.67 | 0.69 | 208624 | 1623094.72 | 302704.24 | 1320390.48 | 1929 | The plant was operational on average load of 1.65 MW and maximum load of 2.9MW as per available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-01 | 2025 | 12 | 1 | Koto HPS | 40.8 | 10.32 | 2.5 | 59499 | 58516 | 11.4 | 5.88 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 482171.84 | 7586436.16 | 983 | Plant was operational on average load of 2.50 MW and maximum load of 10.32 MW | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-01 | 2025 | 12 | 1 | Machai HPS | 2.6 | 0.51 | 0.08 | 2220 | 2024 | 16 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 9454.1 | 282016.3 | 196 | The Unit, after completion of all preliminary checks, was started at 1300Hrs on 01-12-2025 following restoration of the rated head due to increased canal discharge, as per Irrigation Department notification (C.W No. 954-7,Supply Turn of Swabi Irrigation Division, . The Unit was initially maintained at Full Speed No Load (FSNL) for observation. After confirming all parameters were normal, it was synchronized with the system at 1343Hrs and load was gradually increased in accordance with available inflow and prevailing system conditions. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-01 | 2025 | 12 | 1 | Malakand-3 HPS | 81 | 18 | 15.45 | 370771 | 364370 | 20.52 | 10.31 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1043082 | 4522006.8 | 6401 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-01 | 2025 | 12 | 1 | Pehur HPS | 18 | 7.97 | 7.56 | 181600 | 177000 | 12.5 | 15.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 666759 | 960585 | 4600 | Plant operational 24 hrs + irrigation valve open | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-01 | 2025 | 12 | 1 | Reshun HPS | 4.2 | 3.06 | 1.78 | 40000 | 39422 | 2.44 | 2.45 | 81.6 | 13.48 | 81.33 | 45 | 81984 | 1105144.32 | 531408.56 | 573735.76 | 578 | outgoing feeder breaker remained Off 2 times due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-02 | 2025 | 12 | 2 | Daral Khwar HPS | 36.6 | 5 | 3.1 | 75520 | 72320 | 1.62 | 1.21 | 40.33 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 597963.46 | 3323988.89 | 3200 | Unit No 01 was on bar delivering an average load equal to 3.1 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-02 | 2025 | 12 | 2 | Jabori HPS | 10.2 | 2.1 | 2.03 | 48650 | 46790 | 4.66 | 1.58 | 52.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 267133.47 | 1130478.69 | 1860 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-02 | 2025 | 12 | 2 | Karora HPS | 11.8 | 2.9 | 1.65 | 39563 | 37607 | 2.21 | 1.24 | 41.33 | 7.78 | 73.67 | 0.69 | 208624 | 1623094.72 | 292582.46 | 1330512.26 | 1956 | the plant was operational on average load of 1.65mw and maximum load of 2.9mw as per available haydrology | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-02 | 2025 | 12 | 2 | Koto HPS | 40.8 | 7.03 | 2.73 | 65417 | 63277 | 11.4 | 8.42 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 521402.48 | 7547205.52 | 2140 | The plant was operational on average load of 2.73 MW and maximum load of 7.03 MW, according to the available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-02 | 2025 | 12 | 2 | Machai HPS | 2.6 | 0.5 | 0.17 | 3980 | 3696 | 16 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 17264.02 | 274206.38 | 284 | The unit, while on bar and delivering power to the National Grid with a restricted load, experienced a significant reduction in canal inflow | engr.atifwazir@gmail.com | Original | Avg load = Units / 24h | Link_Generation_Data_Summary.xlsx
2025-12-02 | 2025 | 12 | 2 | Malakand-3 HPS | 81 | 17 | 15.93 | 382228 | 375290 | 20.52 | 10.82 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1074342.68 | 4490746.12 | 6938 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-02 | 2025 | 12 | 2 | Pehur HPS | 18 | 7.38 | 7.28 | 174800 | 170000 | 12.5 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 640390 | 986954 | 4800 | Plant remained operational 24 hrs as per available hydrology and Generation is less because of Irrigation valve opening. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-02 | 2025 | 12 | 2 | Reshun HPS | 4.2 | 3.23 | 1.76 | 42000 | 41415 | 2.44 | 2.57 | 85.67 | 13.48 | 81.33 | 45 | 81984 | 1105144.32 | 558274.2 | 546870.12 | 585 | outgoing Feeder breaker remained Off 3times due to less hydrology and also tripped 3times due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-03 | 2025 | 12 | 3 | Daral Khwar HPS | 36.6 | 4.8 | 2.9 | 70520 | 67720 | 1.62 | 1.13 | 37.67 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 559929.28 | 3362023.07 | 2800 | Unit No 01 was on bar delivering an average load equal to 2.9 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-03 | 2025 | 12 | 3 | Jabori HPS | 10.2 | 2.1 | 2 | 43500 | 41700 | 4.66 | 1.58 | 52.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 238073.64 | 1159538.52 | 1800 | Unit 01 tripped at 1615 Hrs due to 132kv supply failure. 132kv supply restored at 1713 Hrs and subsequently unit 01 was synchronized with national grid. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-03 | 2025 | 12 | 3 | Karora HPS | 11.8 | 2.9 | 1.89 | 40306 | 38331 | 2.21 | 1.33 | 44.33 | 7.78 | 73.67 | 0.69 | 208624 | 1623094.72 | 298215.18 | 1324879.54 | 1975 | the plant was operational on average load of 1.89mw and maximum load of 2.9mw as per available hydrology | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-03 | 2025 | 12 | 3 | Koto HPS | 40.8 | 9.52 | 2.63 | 63179 | 61319 | 11.4 | 8.13 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 505268.56 | 7563339.44 | 1860 | The plant was operational on average load of 2.63 MW and maximum load of 9.52 MW, according to the available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-03 | 2025 | 12 | 3 | Machai HPS | 2.6 | 0.53 | 0.13 | 3272 | 3080 | 16 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 14386.68 | 277083.72 | 192 | The unit, while on bar and delivering power to the National Grid with a restricted load, experienced a significant reduction in canal inflow | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-03 | 2025 | 12 | 3 | Malakand-3 HPS | 81 | 19 | 16.43 | 394362 | 387130 | 20.52 | 11.17 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1108237.05 | 4456851.75 | 7232 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-03 | 2025 | 12 | 3 | Pehur HPS | 18 | 7.3 | 7.2 | 173600 | 169000 | 12.5 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 636623 | 990721 | 4600 | Plant remained operational 24 hrs as per available hydrology and Generation is less because of Irrigation valve opening. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-03 | 2025 | 12 | 3 | Reshun HPS | 4.2 | 3.2 | 1.74 | 41000 | 40422 | 2 | 2.45 | 81.6 | 13.48 | 66.67 | 45 | 67200 | 905856 | 544888.56 | 360967.44 | 578 | outgoing feeder breaker remain Off for storage of water | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-04 | 2025 | 12 | 4 | Daral Khwar HPS | 36.6 | 4 | 3.1 | 73890 | 71090 | 1.62 | 1.19 | 39.67 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 587793.45 | 3334158.9 | 2800 | Unit No 01 was on bar delivering an average load equal to 3.1 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-04 | 2025 | 12 | 4 | Jabori HPS | 10.2 | 3 | 2 | 48840 | 47040 | 4.66 | 1.6 | 53.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 268560.77 | 1129051.39 | 1800 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-04 | 2025 | 12 | 4 | Karora HPS | 11.8 | 0 | 0 | 0 | 0 | 2.21 | 0 | 0 | 7.78 | 73.67 | 0.69 | 208624 | 1623094.72 | 0 | 1623094.72 | 0 | Unit#01 shut down due to SCADA communication fault where as unit#02 unavailable due to punch list. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-04 | 2025 | 12 | 4 | Koto HPS | 40.8 | 6.68 | 2.21 | 53146 | 51206 | 11.4 | 10.18 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 421937.44 | 7646670.56 | 1940 | The plant was operational on an average load of 2.21 and Maximum load of 6.68 w.r.t available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-04 | 2025 | 12 | 4 | Machai HPS | 2.6 | 0.5 | 0.32 | 7512 | 6996 | 16 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 32678.32 | 258792.08 | 516 | Not reported | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-04 | 2025 | 12 | 4 | Malakand-3 HPS | 81 | 18 | 17.11 | 410727 | 403160 | 20.52 | 11.57 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1154126.13 | 4410962.67 | 7567 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-04 | 2025 | 12 | 4 | Pehur HPS | 18 | 9.2 | 7.97 | 191400 | 186000 | 12.5 | 16 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 700662 | 926682 | 5400 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-04 | 2025 | 12 | 4 | Reshun HPS | 4.2 | 3.2 | 1.74 | 43000 | 42423 | 2 | 2.33 | 77.53 | 13.48 | 66.67 | 45 | 67200 | 905856 | 571862.04 | 333993.96 | 577 | outgoing feeder breaker remained Off 2times due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-05 | 2025 | 12 | 5 | Daral Khwar HPS | 36.6 | 3.5 | 3.1 | 75080 | 72280 | 1.62 | 1.21 | 40.33 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 597632.72 | 3324319.62 | 2800 | Unit No 01 was on bar delivering an average load equal to 3.1 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-05 | 2025 | 12 | 5 | Jabori HPS | 10.2 | 2.1 | 2 | 48110 | 46080 | 4.66 | 1.57 | 52.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 263079.94 | 1134532.22 | 2030 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-05 | 2025 | 12 | 5 | Karora HPS | 11.8 | 0 | 0 | 0 | 0 | 2.21 | 0 | 0 | 7.78 | 73.67 | 0.69 | 208624 | 1623094.72 | 0 | 1623094.72 | 0 | Unit no.01 shutdown due to scada communication system fault . Unit no.02 unavailable due to governor issue resulting in a complete shutdown of the plan | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-05 | 2025 | 12 | 5 | Koto HPS | 40.8 | 7.53 | 2.54 | 60848 | 58828 | 11.4 | 7.83 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 484742.72 | 7583865.28 | 2020 | The plant was operational on average load of 2.54 MW and maximum load of 7.53 MW, according to the available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-05 | 2025 | 12 | 5 | Machai HPS | 2.6 | 0.5 | 0.26 | 6148 | 57 | 16 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 265.13 | 291205.27 | 6091.24 | Unit remained on bar delivering power to National Grid as per available inflow and system conditions | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-05 | 2025 | 12 | 5 | Malakand-3 HPS | 81 | 18 | 16.66 | 399793 | 392490 | 20.52 | 11.32 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1123581.12 | 4441507.68 | 7303 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-05 | 2025 | 12 | 5 | Pehur HPS | 18 | 9.18 | 9.1 | 218200 | 213000 | 12.5 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 802371 | 824973 | 5200 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-05 | 2025 | 12 | 5 | Reshun HPS | 4.2 | 3.16 | 1.73 | 40000 | 39443 | 2 | 2.39 | 79.57 | 13.48 | 66.67 | 45 | 67200 | 905856 | 531691.64 | 374164.36 | 557 | outgoing feeder breaker tripped 01 time due to line faults and remained Off due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-06 | 2025 | 12 | 6 | Daral Khwar HPS | 36.6 | 4 | 2.9 | 70690 | 67890 | 1.62 | 1.14 | 38 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 561334.89 | 3360617.46 | 2800 | Unit No 01 was on bar delivering an average load equal to 2.9 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-06 | 2025 | 12 | 6 | Jabori HPS | 10.2 | 2.4 | 2 | 44290 | 42480 | 4.66 | 1.45 | 48.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 242526.82 | 1155085.34 | 1810 | Plant was shutdown from 0808 Hrs to 1039 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-06 | 2025 | 12 | 6 | Karora HPS | 11.8 | 0 | 0 | 0 | 0 | 2.21 | 0 | 0 | 7.78 | 73.67 | 0.69 | 208624 | 1623094.72 | 0 | 1623094.72 | 0 | Unit no.01 shutdown due to scada communication system fault . Unit no.02 unavailable due to governor issue resulting in a complete shutdown of the plant | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-06 | 2025 | 12 | 6 | Koto HPS | 40.8 | 6.9 | 2.43 | 58423 | 56583 | 11.4 | 7.52 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 466243.92 | 7602364.08 | 1840 | The Plant was operational on average load of 2.43 MW and maximum load of 6.90 w.r.t available Hydrology | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-06 | 2025 | 12 | 6 | Machai HPS | 2.6 | 0.5 | 0.3 | 6604 | 6204 | 16 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 28978.88 | 262491.52 | 400 | Not reported | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-06 | 2025 | 12 | 6 | Malakand-3 HPS | 81 | 18 | 15.9 | 381590 | 374950 | 20.52 | 10.84 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1073369.36 | 4491719.43 | 6640 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-06 | 2025 | 12 | 6 | Pehur HPS | 18 | 9.14 | 9.05 | 217200 | 211000 | 12.5 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 794837 | 832507 | 6200 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-06 | 2025 | 12 | 6 | Reshun HPS | 4.2 | 3.08 | 1.68 | 41000 | 40422 | 2 | 2.51 | 83.67 | 13.48 | 66.67 | 45 | 67200 | 905856 | 544888.56 | 360967.44 | 578 | Outgoing Feeder Breaker remained Off 3times for 2.40 hours. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-07 | 2025 | 12 | 7 | Daral Khwar HPS | 36.6 | 4 | 2.9 | 69860 | 67060 | 1.62 | 1.12 | 37.33 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 554472.2 | 3367480.15 | 2800 | Unit No 01 was on bar delivering an average load equal to 2.9 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-07 | 2025 | 12 | 7 | Jabori HPS | 10.2 | 3 | 2 | 40694 | 38880 | 4.66 | 1.33 | 44.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 221973.7 | 1175638.46 | 1814 | Plqnt was shutdown from 1010 Hrs to 1230 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-07 | 2025 | 12 | 7 | Karora HPS | 11.8 | 2.9 | 0.23 | 6914 | 5451 | 2.21 | 0.17 | 5.67 | 7.78 | 73.67 | 0.69 | 208624 | 1623094.72 | 42408.78 | 1580685.94 | 1463 | the plant was operation mode delivering power to the system max load 2.9MW min load 0 MW average load 0.23 | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-07 | 2025 | 12 | 7 | Koto HPS | 40.8 | 7.53 | 2.64 | 63378 | 61498 | 11.4 | 6.28 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 506743.52 | 7561864.48 | 1880 | The Plant was operational on average load of 2.64 & Maximum load of 7.53 w.r.t available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-07 | 2025 | 12 | 7 | Machai HPS | 2.6 | 0.54 | 0.38 | 8516 | 7876 | 16 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 36788.8 | 254681.6 | 640 | Not reported | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-07 | 2025 | 12 | 7 | Malakand-3 HPS | 81 | 15 | 13.7 | 328894 | 322540 | 20.52 | 9.62 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 923335.26 | 4641753.54 | 6354 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-07 | 2025 | 12 | 7 | Pehur HPS | 18 | 9.14 | 9.03 | 216700 | 211000 | 12.5 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 794837 | 832507 | 5700 | Plant remained operational throughout 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-07 | 2025 | 12 | 7 | Reshun HPS | 4.2 | 2.88 | 1.75 | 40000 | 39410 | 2 | 2.39 | 79.57 | 13.48 | 66.67 | 45 | 67200 | 905856 | 531246.8 | 374609.2 | 590 | outgoing feeder breaker remained Off 2hours for storage of water. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-08 | 2025 | 12 | 8 | Daral Khwar HPS | 36.6 | 4 | 2.9 | 69650 | 66450 | 1.62 | 1.11 | 37 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 549428.54 | 3372523.81 | 3200 | Unit No 01 was on bar delivering an average load equal to 2.9 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-08 | 2025 | 12 | 8 | Jabori HPS | 10.2 | 2.4 | 2 | 45840 | 43920 | 4.66 | 1.5 | 50 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 250748.06 | 1146864.1 | 1920 | Plant was shutdown from 1033 Hrs to 1132 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-08 | 2025 | 12 | 8 | Karora HPS | 11.8 | 2.9 | 1.52 | 37183 | 35200 | 2.21 | 1.15 | 38.33 | 7.78 | 73.67 | 0.69 | 208624 | 1623094.72 | 273856 | 1349238.72 | 1983 | the plant was operation mode delivering power to the system max load 2.9MW min load 0MW average load 1.52MW. average flow 1.15 cumecs | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-08 | 2025 | 12 | 8 | Koto HPS | 40.8 | 7.13 | 2.33 | 55887 | 54007 | 11.4 | 7.19 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 445017.68 | 7623590.32 | 1880 | The plant was operational on average load 2.33 and maximum load of 7.13 as per available hydrology | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-08 | 2025 | 12 | 8 | Machai HPS | 2.6 | 0.5 | 0.42 | 9732 | 9108 | 16 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 42543.47 | 248926.93 | 624 | Not reported | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-08 | 2025 | 12 | 8 | Malakand-3 HPS | 81 | 15 | 13.83 | 331898 | 325440 | 20.52 | 9.37 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 931637.09 | 4633451.71 | 6458 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-08 | 2025 | 12 | 8 | Pehur HPS | 18 | 9.14 | 9 | 216100 | 210000 | 12.5 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 791070 | 836274 | 6100 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-08 | 2025 | 12 | 8 | Reshun HPS | 4.2 | 3.4 | 1.72 | 41000 | 40399 | 2 | 2.51 | 83.67 | 13.48 | 66.67 | 45 | 67200 | 905856 | 544578.52 | 361277.48 | 601 | outgoing feeder breaker remained Off 3hour for the storage of water. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-09 | 2025 | 12 | 9 | Daral Khwar HPS | 36.6 | 4 | 2.8 | 68370 | 65570 | 1.62 | 1.1 | 36.67 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 542152.43 | 3379799.92 | 2800 | Unit No 01 was on bar delivering an average load equal to 2.8 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-09 | 2025 | 12 | 9 | Jabori HPS | 10.2 | 2.5 | 2 | 43600 | 41760 | 4.66 | 1.42 | 47.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 238416.19 | 1159195.97 | 1840 | Plant was shutdown from 0800 Hrs to 0941 Hrs and from 2002 Hrs to 2117 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-09 | 2025 | 12 | 9 | Karora HPS | 11.8 | 2.9 | 1.64 | 37053 | 35002 | 2.21 | 1.27 | 42.33 | 7.78 | 73.67 | 0.69 | 208624 | 1623094.72 | 272315.56 | 1350779.16 | 2051 | unit#01 remain on bar delivering power to the system as per available flow.And unit#02 shut down due to punch list issue. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-09 | 2025 | 12 | 9 | Koto HPS | 40.8 | 11.88 | 1.98 | 47500 | 46740 | 11.4 | 6.11 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 385137.6 | 7683470.4 | 760 | The plant was operational on average load of 1.98 MW and maximum load of 11.88 MW as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-09 | 2025 | 12 | 9 | Machai HPS | 2.6 | 0.5 | 0.1 | 2616 | 2376 | 18 | 7 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 11098.3 | 280372.1 | 240 | The unit, while on bar and delivering power to the National Grid, was shut down at 0608Hrs on 09-12-2025 as a precautionary measure following a significant drop in the headrace water level. The reduced discharge resulted from the diversion of water by the Irrigation Department from Machai Canal to Aba Zai Canal in accordance with the weekly canal closure schedule. As per Canal Wire No. 966-7 dated 08-12-2025 issued by SDO Dargai (Full Supply Turn of Malakand Irrigation Division), the weekly canal closure for Machai was scheduled on 09-12-2025. In view of the reduced discharge, the unit was safely taken off-bar and will remain on standby until adequate canal flow is restored by the Irrigation Department | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-09 | 2025 | 12 | 9 | Malakand-3 HPS | 81 | 14 | 6.11 | 144263 | 140500 | 20.52 | 5.27 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 402209.35 | 5162879.45 | 3763 | Unit # 02 desynchronized from the system at 14:31Hrs Dated 09.12.2025 due to low hydrology, as the Irrigation Department diverted water from the auxiliary tunnel because of a shortage in the main canal. Consequently, the unit has been placed on standby | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-09 | 2025 | 12 | 9 | Pehur HPS | 18 | 9.16 | 8.97 | 215200 | 210000 | 12.5 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 791070 | 836274 | 5200 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-09 | 2025 | 12 | 9 | Reshun HPS | 4.2 | 3.16 | 1.58 | 36000 | 35510 | 2 | 2.2 | 73.43 | 13.48 | 66.67 | 45 | 67200 | 905856 | 478674.8 | 427181.2 | 490 | Booni and Mastuj section connected with Feeder No. II from 10:00am to 2:30pm due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-10 | 2025 | 12 | 10 | Daral Khwar HPS | 36.6 | 3.5 | 2.8 | 68060 | 65260 | 1.62 | 1.09 | 36.33 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 539589.26 | 3382363.09 | 2800 | Unit No 01 was on bar delivering an average load equal to 2.8 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-10 | 2025 | 12 | 10 | Jabori HPS | 10.2 | 2.3 | 2 | 46080 | 44160 | 4.66 | 1.51 | 50.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 252118.27 | 1145493.89 | 1920 | Plant was shutdown from 1415 Hrs to 1530 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-10 | 2025 | 12 | 10 | Karora HPS | 11.8 | 3 | 1.3 | 34843 | 32990 | 2.21 | 0.97 | 32.33 | 7.78 | 73.67 | 0.69 | 208624 | 1623094.72 | 256662.2 | 1366432.52 | 1853 | Unit#01 remain on bar delivering power to the system as per available flow. Unit#02 shut down due to punch list. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-10 | 2025 | 12 | 10 | Koto HPS | 40.8 | 6.82 | 1.06 | 25500 | 25122 | 11.4 | 3.28 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 207005.28 | 7861602.72 | 378 | The plant was operational on average load of 1.06 MW and maximum load of 6.82 MW as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-10 | 2025 | 12 | 10 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 16 | 2 | 66.67 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0608Hrs on 09-12-2025 due to low hydrological inflow, as canal water was diverted by the Irrigation Department in accordance with the weekly canal closure schedule. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-10 | 2025 | 12 | 10 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 20.52 | 0 | 0 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 0 | 5565088.8 | 0 | As the Irrigation Department diverted water from the auxiliary tunnel because of a shortage in the main canal. Consequently, the units has been placed on standby | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-10 | 2025 | 12 | 10 | Pehur HPS | 18 | 9.07 | 9 | 214800 | 209000 | 12.5 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 787303 | 840041 | 5800 | Plant remained operational throughout 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-10 | 2025 | 12 | 10 | Reshun HPS | 4.2 | 2.64 | 1.57 | 38000 | 37400 | 2 | 2.33 | 77.5 | 13.48 | 66.67 | 45 | 67200 | 905856 | 504152 | 401704 | 600 | outgoing feeder breaker remained off 3times (4hours) for storage of water in the reservoir. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-11 | 2025 | 12 | 11 | Daral Khwar HPS | 36.6 | 3.5 | 2.8 | 67110 | 64310 | 1.62 | 1.08 | 36 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 531734.37 | 3390217.98 | 2800 | Unit No 01 was on bar delivering an average load equal to 2.8 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-11 | 2025 | 12 | 11 | Jabori HPS | 10.2 | 2.4 | 2 | 43335 | 41520 | 4.59 | 1.42 | 47.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 237045.98 | 1160566.18 | 1815 | Plant was shutdown from 0900 Hrs to 1133 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-11 | 2025 | 12 | 11 | Karora HPS | 11.8 | 2.9 | 1.3 | 30273 | 28352 | 2.39 | 0.89 | 29.67 | 7.78 | 79.67 | 0.69 | 225616 | 1755292.48 | 220578.56 | 1534713.92 | 1921 | Unit#01 remain on bar delivering power to the system as per available flow. And unit#02 shut down due to punch list. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-11 | 2025 | 12 | 11 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11.4 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remain shut down due to box channel repair work as requested by the EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-11 | 2025 | 12 | 11 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 16 | 2 | 66.67 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0608Hrs on 09-12-2025 due to low hydrological inflow, as canal water was diverted by the Irrigation Department in accordance with the weekly canal closure schedule. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-11 | 2025 | 12 | 11 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 20.52 | 0 | 0 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 0 | 5565088.8 | 0 | As the Irrigation Department diverted water from the auxiliary tunnel because of a shortage in the main canal. Consequently the units have been placed on standby. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-11 | 2025 | 12 | 11 | Pehur HPS | 18 | 9.09 | 8.93 | 214400 | 208000 | 12.5 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 783536 | 843808 | 6400 | Plant remained operational throughout 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-11 | 2025 | 12 | 11 | Reshun HPS | 4.2 | 3.12 | 1.68 | 40000 | 39396 | 2 | 2.39 | 79.57 | 13.48 | 66.67 | 45 | 67200 | 905856 | 531058.08 | 374797.92 | 604 | 1. Mastuj and Booni Section has been connected with Feeder No.II from 09:00am to 02:00pm due to less hydrology. 2. outgoing feeder breaker remained Off from 04:00pm to 04:50pm for storage of water in the reservoir. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-12 | 2025 | 12 | 12 | Daral Khwar HPS | 36.6 | 4 | 2.9 | 69130 | 66330 | 1.62 | 1.11 | 37 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 548436.34 | 3373516.01 | 2800 | Unit No 01 was on bar delivering an average load equal to 2.9 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-12 | 2025 | 12 | 12 | Jabori HPS | 10.2 | 2 | 2 | 49754 | 47940 | 4.59 | 1.63 | 54.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 273699.05 | 1123913.11 | 1814 | Plant was shutdown from 0600 Hrs to 0730 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-12 | 2025 | 12 | 12 | Karora HPS | 11.8 | 2.9 | 0.24 | 8249 | 6745 | 2.39 | 0.17 | 5.67 | 7.78 | 79.67 | 0.69 | 225616 | 1755292.48 | 52476.1 | 1702816.38 | 1504 | 1.Unit#01 was normally shut down due to low hydrology at 16:50hrs.Unit#01 start and synchronized to the system at 14:44hrs. 2.Both units shut down due to punch list issue. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-12 | 2025 | 12 | 12 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11.4 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remain shut down due to box channel repair work as requested by the EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-12 | 2025 | 12 | 12 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 16 | 2 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | No data submitted for this date | engr.atifwazir@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-12-12 | 2025 | 12 | 12 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 20.52 | 0 | 0 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 0 | 5565088.8 | 0 | As the Irrigation Department diverted water from the auxiliary tunnel because of a shortage in the main canal. Consequently the units have been placed on standby. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-12 | 2025 | 12 | 12 | Pehur HPS | 18 | 9.04 | 8.93 | 214200 | 209000 | 12.5 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 787303 | 840041 | 5200 | Plant remained operational throughout 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-12 | 2025 | 12 | 12 | Reshun HPS | 4.2 | 3.16 | 1.76 | 39000 | 38399 | 2 | 2.39 | 79.57 | 13.48 | 66.67 | 45 | 67200 | 905856 | 517618.52 | 388237.48 | 601 | 1. outgoing feeder breaker remained Off for 3.30hours due to less hydrology and Mastuj section also remained Off for from 9:30am to 12:30pm. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-13 | 2025 | 12 | 13 | Daral Khwar HPS | 36.6 | 3.5 | 3 | 71800 | 68600 | 1.62 | 1.15 | 38.33 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 567205.38 | 3354746.97 | 3200 | Unit No 01 was on bar delivering an average load equal to 3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-13 | 2025 | 12 | 13 | Jabori HPS | 10.2 | 2.1 | 2 | 46379 | 44499 | 4.59 | 1.52 | 50.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 254053.69 | 1143558.47 | 1880 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-13 | 2025 | 12 | 13 | Karora HPS | 11.8 | 0 | 0 | 0 | 0 | 2.39 | 0 | 0 | 7.78 | 79.67 | 0.69 | 225616 | 1755292.48 | 0 | 1755292.48 | 0 | Both units , unit #01 and 02 shut down mode due to an RPM over shoot issue,governor issue and SCADA communication OS2 sytem. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-13 | 2025 | 12 | 13 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11.4 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The Plant remain shutdown due to box channel repairing work as requested by the EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-13 | 2025 | 12 | 13 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 16 | 2 | 66.67 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0608Hrs on 09-12-2025 due to low hydrological inflow, as canal water was diverted by the Irrigation Department in accordance with the weekly canal closure schedule. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-13 | 2025 | 12 | 13 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 20.52 | 0 | 0 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 0 | 5565088.8 | 0 | As the Irrigation Department diverted water from the auxiliary tunnel because of a shortage in the main canal. Consequently the units have been placed on standby. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-13 | 2025 | 12 | 13 | Pehur HPS | 18 | 9 | 8.92 | 214000 | 208000 | 11 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 783536 | 843808 | 6000 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-13 | 2025 | 12 | 13 | Reshun HPS | 4.2 | 2.7 | 1.6 | 38500 | 37902 | 2 | 2.36 | 38.19 | 13.48 | 66.67 | 45 | 67200 | 905856 | 510918.96 | 394937.04 | 598 | No data submitted for this date | zafar.src@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-12-14 | 2025 | 12 | 14 | Daral Khwar HPS | 36.6 | 3.6 | 3 | 72390 | 69590 | 1.62 | 1.16 | 38.67 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 575391 | 3346561.35 | 2800 | Unit No 01 was on bar delivering an average load equal to 3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-14 | 2025 | 12 | 14 | Jabori HPS | 10.2 | 2.1 | 2 | 44428 | 42560 | 4.59 | 1.45 | 48.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 242983.55 | 1154628.61 | 1868 | Plant was shutdown from 1145 Hrs to 1300 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-14 | 2025 | 12 | 14 | Karora HPS | 11.8 | 2.8 | 0.23 | 7916 | 6311 | 2.39 | 0.17 | 5.6 | 7.78 | 79.67 | 0.69 | 225616 | 1755292.48 | 49099.58 | 1706192.9 | 1605 | Unit#01 remain shutdown due to Governor over speed issue While Unit#02 was started at 23:49Hrs to check it Governor speed status. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-14 | 2025 | 12 | 14 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11.4 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remained shut down due to Box Channel repair by EPC Contractor | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-14 | 2025 | 12 | 14 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 16 | 2 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | No data submitted for this date | engr.atifwazir@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-12-14 | 2025 | 12 | 14 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 20.52 | 0 | 0 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 0 | 5565088.8 | 0 | As the Irrigation Department diverted water from the auxiliary tunnel because of a shortage in the main canal. Consequently the units have been placed on standby. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-14 | 2025 | 12 | 14 | Pehur HPS | 18 | 9.01 | 8.71 | 209000 | 203000 | 11 | 17 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 764701 | 862643 | 6000 | The plant remained operational throughout 24 hours as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-14 | 2025 | 12 | 14 | Reshun HPS | 4.2 | 3.11 | 1.65 | 38000 | 37406 | 2 | 2.33 | 77.53 | 13.48 | 66.67 | 45 | 67200 | 905856 | 504232.88 | 401623.12 | 594 | outgoing feeder breaker remained Off 5.25 hrs due to less hydrology. Mastuj Section remained Off from Booni for 4.30hrs. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-15 | 2025 | 12 | 15 | Daral Khwar HPS | 36.6 | 3.2 | 2 | 47580 | 45580 | 1.62 | 0.76 | 25.33 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 376869.11 | 3545083.24 | 2000 | 1. Unit No.01 was on bar delivering an average load equal to 2.0 MW according to the available hydrology. 2. The plant was shut down and 132 KV line tripped at 1058 hours due to a PESCO shutdown for annual maintenance of the 132 KV transmission line. The line was restored at 1639 hours. 3. Unit No.01 was synchronized with the national grid at 1840 Hrs. | daralkhwarhpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-15 | 2025 | 12 | 15 | Jabori HPS | 10.2 | 2.1 | 2 | 45123 | 43340 | 4.59 | 1.47 | 49 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 247436.73 | 1150175.43 | 1783 | Plant was shutdown from 1815 Hrs to 1930 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-15 | 2025 | 12 | 15 | Karora HPS | 11.8 | 2.8 | 0.24 | 9735 | 8137 | 2.39 | 0.17 | 5.6 | 7.78 | 79.67 | 0.69 | 225616 | 1755292.48 | 63305.86 | 1691986.62 | 1598 | complex remain shutdown due to Governor over speed issue and unit#02 was running multiples times to check governor speed status. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-15 | 2025 | 12 | 15 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11.4 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remained shut down due to Box Channel repair by EPC contractor | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-15 | 2025 | 12 | 15 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 16 | 2 | 66.67 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0608Hrs on 09-12-2025 due to low hydrological inflow, as canal water was diverted by the Irrigation Department in accordance with the weekly canal closure schedule. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-15 | 2025 | 12 | 15 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 20.52 | 0 | 0 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 0 | 5565088.8 | 0 | As the Irrigation Department diverted water from the auxiliary tunnel because of a shortage in the main canal. Consequently the units have been placed on standby. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-15 | 2025 | 12 | 15 | Pehur HPS | 18 | 8.47 | 8.35 | 200600 | 195000 | 11 | 17 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 734565 | 892779 | 5600 | Plant remained operational throughout 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-15 | 2025 | 12 | 15 | Reshun HPS | 4.2 | 2.45 | 1.57 | 38000 | 37400 | 2 | 2.33 | 77.53 | 13.48 | 66.67 | 45 | 67200 | 905856 | 504152 | 401704 | 600 | 1. Outgoing Feeder Breaker remained Off 3times for 2.45hours due to less hydrology. 2. Mastuj Section remained Off from Booni for 4.10 hours. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-16 | 2025 | 12 | 16 | Daral Khwar HPS | 36.6 | 3.5 | 2.9 | 68700 | 65500 | 1.62 | 1.1 | 36.67 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 541573.65 | 3380378.7 | 3200 | 1. Unit No 01 was on bar delivering an average load equal to 2.9 MW according to available hydrology. 2. Unit No 01 tripped at 0400 hrs due to grid over frequency and synchronized 0409 Hrs. 3. Unit No 01 tripped again at 0509 Hrs due to grid over frequency and synchronized at 0514 Hrs. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-16 | 2025 | 12 | 16 | Jabori HPS | 10.2 | 2.1 | 2 | 45474 | 43680 | 4.59 | 1.49 | 49.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 249377.86 | 1148234.3 | 1794 | Plant was shutdown from 1855 Hrs to 2005 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-16 | 2025 | 12 | 16 | Karora HPS | 11.8 | 2.8 | 0.94 | 20140 | 18545 | 2.39 | 0.7 | 23.33 | 7.78 | 79.67 | 0.69 | 225616 | 1755292.48 | 144280.1 | 1611012.38 | 1595 | the plant was operational on average load of 0.94MW and maximum load of 2.8MW as per available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-16 | 2025 | 12 | 16 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11.4 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remained shut down due to Box Channel Leakage repair by EPC contractor | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-16 | 2025 | 12 | 16 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 16 | 2 | 66.67 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 0608Hrs on 09-12-2025 due to low hydrological inflow, as canal water was diverted by the Irrigation Department in accordance with the weekly canal closure schedule. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-16 | 2025 | 12 | 16 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 20.52 | 0 | 0 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 0 | 5565088.8 | 0 | As the Irrigation Department diverted water from the auxiliary tunnel because of a shortage in the main canal. Consequently the units have been placed on standby. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-16 | 2025 | 12 | 16 | Pehur HPS | 18 | 8.51 | 7.72 | 185200 | 181000 | 11 | 17 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 681827 | 945517 | 4200 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-16 | 2025 | 12 | 16 | Reshun HPS | 4.2 | 3.13 | 1.75 | 37000 | 36404 | 2 | 2.26 | 75.5 | 13.48 | 66.67 | 45 | 67200 | 905856 | 490725.92 | 415130.08 | 596 | 1. outgoing feeder breaker remained Off 01hours for storage of water. 2. Booni and Mastuj section connected with Feeder No. II. 3. outgoing feeder breaker tripped 4times due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-17 | 2025 | 12 | 17 | Daral Khwar HPS | 36.6 | 3.5 | 2.8 | 67510 | 64710 | 1.62 | 1.08 | 36 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 535041.69 | 3386910.66 | 2800 | Unit No 01 was on bar delivering an average load equal to 2.8 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-17 | 2025 | 12 | 17 | Jabori HPS | 10.2 | 2.1 | 2 | 44946 | 43090 | 4.59 | 1.47 | 49 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 246009.43 | 1151602.73 | 1856 | Plant was shutdown from 1541 Hrs to 1717 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-17 | 2025 | 12 | 17 | Karora HPS | 11.8 | 2.9 | 1.06 | 32547 | 30695 | 2.39 | 1.15 | 38.33 | 7.78 | 79.67 | 0.69 | 225616 | 1755292.48 | 238807.1 | 1516485.38 | 1852 | the plant was operational on average load of 1.06mw and maximum load of 2.9mw as per available hydrology | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-17 | 2025 | 12 | 17 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11.4 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remained shut down due to Box Channel leakage repair by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-17 | 2025 | 12 | 17 | Machai HPS | 2.6 | 0.5 | 0.05 | 1312 | 1232 | 16 | 13 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 5754.67 | 285715.73 | 80 | 1.The Unit, after completion of all preliminary checks, was started at 1520Hrs on 17-12-2025 following restoration of the rated head due to increased canal discharge, as per Irrigation Department notification (C.W No. 984-7,Supply Turn of Swabi Irrigation Division. The Unit was initially maintained at Full Speed No Load (FSNL) for observation. After confirming all parameters were normal, it was synchronized with the system at 1548Hrs and load was gradually increased in accordance with available inflow and prevailing system conditions. 2.The unit, while on bar delivering power to the National Grid as per available water inflow and system conditions, was frequently taken on precautionary shutdown to rebuild the water head at 1700Hrs & 1920Hrs on 17-12-2025 due to continuous drops in the headrace level. The recorded inflow was up to 13cumecs, whereas the minimum required inflow for safe and smooth unit operation is 16 cumecs. The unit was subsequently synchronized with the system after restoration of rated head at 1820Hrs, 2215Hrs respectively. 3.The unit has remained on standby since 2239 Hrs on 17-12-2025 due to low hydrological inflow, following a significant drop in the headrace water level caused by decreased canal discharge. The recorded inflow was up to 13 cumecs, whereas the minimum required inflow for safe and smooth unit operation is 16 cumecs | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-17 | 2025 | 12 | 17 | Malakand-3 HPS | 81 | 20 | 10.09 | 242232 | 238410 | 20.52 | 8.31 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 682496.31 | 4882592.49 | 3822 | Unit #02 was synchronized with the system at 10:41 hrs on 17-12-2025 after diversion of water to the Malakand-III channel by the Irrigation Department. As per the available hydrology from the Irrigation Department, one unit is currently on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-17 | 2025 | 12 | 17 | Pehur HPS | 18 | 7.75 | 7.52 | 180600 | 175000 | 11 | 16 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 659225 | 968119 | 5600 | The plant remained operational throughout 24 hours as per available hydrology, and the irrigation valve is open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-17 | 2025 | 12 | 17 | Reshun HPS | 4.2 | 2.38 | 1.42 | 34000 | 33409 | 2 | 2.08 | 33.73 | 13.48 | 66.67 | 45 | 67200 | 905856 | 450353.32 | 455502.68 | 591 | No data submitted for this date | zafar.src@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-12-18 | 2025 | 12 | 18 | Daral Khwar HPS | 36.6 | 3 | 2.8 | 68390 | 65590 | 1.62 | 1.1 | 36.67 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 542317.8 | 3379634.55 | 2800 | 1. Unit No 01 was on bar delivering an average load equal to 2.8 MW according to available hydrology. 2. Unit No 01 tripped due to the failure of 132KV transmission line at 1753 hrs. The line restored at 1820 hrs. 3. Unit No 01 synchronized with the national grid at 1835 Hrs. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-18 | 2025 | 12 | 18 | Jabori HPS | 10.2 | 2.1 | 2 | 44673 | 42740 | 4.59 | 1.46 | 48.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 244011.21 | 1153600.95 | 1933 | Plant was shutdown from 1555 Hrs to 1725 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-18 | 2025 | 12 | 18 | Karora HPS | 11.8 | 2.8 | 1.06 | 32525 | 30715 | 2.39 | 1.15 | 38.33 | 7.78 | 79.67 | 0.69 | 225616 | 1755292.48 | 238962.7 | 1516329.78 | 1810 | the plant was operational on average load of 1.06mw and miximum load of 2.8mw as per available hydrology | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-18 | 2025 | 12 | 18 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11.4 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remained shut down due to Box Channel leakage repair by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-18 | 2025 | 12 | 18 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 16 | 13 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 2239 Hrs on 17-12-2025 due to low hydrological inflow, following a significant drop in the headrace water level caused by decreased canal discharge. The recorded inflow was up to 13cumecs, whereas the minimum required inflow for safe and smooth unit operation is 15cumecs. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-18 | 2025 | 12 | 18 | Malakand-3 HPS | 81 | 20 | 18.98 | 455634 | 6284 | 20.52 | 12.1 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 17989.21 | 5547099.59 | 449350 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-18 | 2025 | 12 | 18 | Pehur HPS | 18 | 7.5 | 7.39 | 177400 | 172000 | 11 | 16 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 647924 | 979420 | 5400 | The plant remained operational throughout 24 hours as per available hydrology, and the irrigation valve is open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-18 | 2025 | 12 | 18 | Reshun HPS | 4.2 | 3.08 | 1.37 | 31000 | 30414 | 2 | 1.9 | 63.23 | 13.48 | 66.67 | 45 | 67200 | 905856 | 409980.72 | 495875.28 | 586 | 1. outgoing feeder breaker remained Off in times for 5.50hrs for storage of water. 2. Booni and Mastuj Section connected with Feeder No.II. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-19 | 2025 | 12 | 19 | Daral Khwar HPS | 36.6 | 3 | 2.7 | 65640 | 62840 | 1.62 | 1.05 | 35 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 519579.97 | 3402372.38 | 2800 | Unit No 01 was on bar delivering an average load equal to 2.7 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-19 | 2025 | 12 | 19 | Jabori HPS | 10.2 | 2.1 | 2 | 44499 | 42660 | 4.59 | 1.45 | 48.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 243554.47 | 1154057.69 | 1839 | Plant was shutdown from 1533 Hrs to 1707 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-19 | 2025 | 12 | 19 | Karora HPS | 11.8 | 2.9 | 0.83 | 30834 | 28937 | 2.39 | 0.98 | 32.67 | 7.78 | 79.67 | 0.69 | 225616 | 1755292.48 | 225129.86 | 1530162.62 | 1897 | the plant was operational on average load 0.98MW and a Maximum Load 2.9MW as per available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-19 | 2025 | 12 | 19 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11.4 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant is shut down due to the repair work in box channel. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-19 | 2025 | 12 | 19 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 16 | 12.75 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | No data submitted for this date | engr.atifwazir@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-12-19 | 2025 | 12 | 19 | Malakand-3 HPS | 81 | 20 | 18.87 | 452935 | 446450 | 20.52 | 12.06 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1278052.42 | 4287036.38 | 6485 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-19 | 2025 | 12 | 19 | Pehur HPS | 18 | 8.36 | 7.68 | 184300 | 180000 | 11 | 16.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 678060 | 949284 | 4300 | Plant remained operational throughout 24 Hrs as per available hydrology + irrigation valve open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-19 | 2025 | 12 | 19 | Reshun HPS | 4.2 | 3.08 | 1.51 | 35000 | 34400 | 2.14 | 2.23 | 100 | 13.48 | 71.4 | 45 | 71971.2 | 970171.78 | 463712 | 506459.78 | 600 | 1. Outgoing feeder breaker remained Off for 6.10hours for storage of water in variouse times. 2. Mastuj Section remained Off from Booni for 5.40hour. | zafar.src@gmail.com | Original | Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2025-12-20 | 2025 | 12 | 20 | Daral Khwar HPS | 36.6 | 3.5 | 2.9 | 70150 | 68550 | 1.62 | 1.15 | 38.33 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 566791.96 | 3355160.38 | 1600 | 1. Unit No 01 was on bar delivering an average load equal to 2.9 MW according to available hydrology. 2. Unit No 01 desynchronized due to over frequency of the national grid. 3. Unit No 01 resynchronized with the national grid at 0732 Hrs after frequency of the national grid stabilized. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-20 | 2025 | 12 | 20 | Jabori HPS | 10.2 | 2.1 | 2 | 44933 | 43050 | 4.59 | 1.47 | 49 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 245781.06 | 1151831.1 | 1883 | Plant was shutdown from 1410 Hrs to 1525 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-20 | 2025 | 12 | 20 | Karora HPS | 11.8 | 2.9 | 0.83 | 33336 | 32162 | 2.39 | 0.97 | 32.33 | 7.78 | 79.67 | 0.69 | 225616 | 1755292.48 | 250220.36 | 1505072.12 | 1174 | the plant was operational on average load 0.83MW and maximum load 2.9MW as per available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-20 | 2025 | 12 | 20 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11.4 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | the plant was shut down due to box channel repairing works in progress. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-20 | 2025 | 12 | 20 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 16 | 12.5 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 2239 Hrs on 17-12-2025 due to low hydrological inflow, following a significant drop in the headrace water level caused by decreased canal discharge. The recorded inflow was up to 13cumecs, whereas the minimum required inflow for safe and smooth unit operation is 15cumecs. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-12-20 | 2025 | 12 | 20 | Malakand-3 HPS | 81 | 20 | 19.04 | 456857 | 450860 | 20.52 | 12.13 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1290676.92 | 4274411.88 | 5997 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-20 | 2025 | 12 | 20 | Pehur HPS | 18 | 8.6 | 8.41 | 201900 | 196000 | 11 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 738332 | 889012 | 5900 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-20 | 2025 | 12 | 20 | Reshun HPS | 4.2 | 2.96 | 1.56 | 36000 | 35406 | 2 | 2.57 | 85.67 | 13.48 | 66.67 | 45 | 67200 | 905856 | 477272.88 | 428583.12 | 594 | 1. Outgoing feeder breaker remained Off for 1.30hour for storage of water in in the reservoir. 2. Booni and Mastuj Section connected with Feeder NO.II from 09:25am to 12:50pm. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-21 | 2025 | 12 | 21 | Daral Khwar HPS | 36.6 | 4 | 3.4 | 82120 | 78120 | 1.62 | 1.31 | 43.67 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 645919.6 | 3276032.75 | 4000 | 1. Unit No 01 was on bar delivering an average load equal to 3.4 MW according to available hydrology. 2. Unit No 01 desynchronized at 0707 hrs due to grid over frequency and then again at 2133 hrs. 3. Unit No 01 synchronized with the national grid at 0717 hrs and 2133 hrs respectively. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-21 | 2025 | 12 | 21 | Jabori HPS | 10.2 | 4 | 3 | 72974 | 71010 | 4.73 | 2.38 | 79.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 405410.29 | 992201.87 | 1964 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-21 | 2025 | 12 | 21 | Karora HPS | 11.8 | 2.9 | 1.17 | 35379 | 34277 | 1.78 | 0.97 | 32.33 | 7.78 | 59.33 | 0.69 | 168032 | 1307288.96 | 266675.06 | 1040613.9 | 1102 | the plant was operational on average load 1.17MW and maximum load 2.9MW as per available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-21 | 2025 | 12 | 21 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11.4 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant was remained shut down due to EPC contractor work on the leakage of box channel. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-21 | 2025 | 12 | 21 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 16 | 13 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Not reported | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-21 | 2025 | 12 | 21 | Malakand-3 HPS | 81 | 24 | 21.49 | 515742 | 509880 | 20.52 | 13.76 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1459633.48 | 4105455.32 | 5862 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-21 | 2025 | 12 | 21 | Pehur HPS | 18 | 8.58 | 8.53 | 204700 | 199000 | 11 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 749633 | 877711 | 5700 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-21 | 2025 | 12 | 21 | Reshun HPS | 4.2 | 2.73 | 1.64 | 37000 | 36400 | 2 | 2.26 | 75.5 | 13.48 | 66.67 | 45 | 67200 | 905856 | 490672 | 415184 | 600 | 1. Outgoing feede breaker remained Off for 4.00hours for storage of water in the reservoir. 2. Mastuj Section remained Off for 5.00hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-22 | 2025 | 12 | 22 | Daral Khwar HPS | 36.6 | 4.5 | 3.6 | 85870 | 83070 | 1.62 | 1.39 | 46.33 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 686847.68 | 3235104.67 | 2800 | 1. Unit No 01 was on bar delivering an average load equal to 3.6 MW according to available hydrology. 2. Unit No 01 desyed due to fluctuations in frequency of the national grid at 0340 hrs. 3. Unit No 01 synchronized with the national grid at 0411 hrs. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-22 | 2025 | 12 | 22 | Jabori HPS | 10.2 | 4.5 | 3 | 61432 | 59780 | 4.73 | 2.01 | 67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 341295.98 | 1056316.18 | 1652 | Unit 01 tripped at 0647 Hrs due to tripping of 132 KV transmission line. Line restored at 0753 Hrs and unit 01 was synchronized with national grid at 0845 Hrs. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-22 | 2025 | 12 | 22 | Karora HPS | 11.8 | 4 | 2.35 | 53056 | 51480 | 1.78 | 1.65 | 55 | 7.78 | 59.33 | 0.69 | 168032 | 1307288.96 | 400514.4 | 906774.56 | 1576 | the plant was operational on average load 2.35MW and maximum load 4.0MW as per available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-22 | 2025 | 12 | 22 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11.4 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant was remained shut down due to EPC contractor working on the repairing of box channel. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-22 | 2025 | 12 | 22 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 16 | 12.2 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 2239 Hrs on 17-12-2025 due to low hydrological inflow, following a significant drop in the headrace water level caused by decreased canal discharge. The recorded inflow was up to 13cumecs, whereas the minimum required inflow for safe and smooth unit operation is 15cumecs. | engr.atifwazir@gmail.com | Original | Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-12-22 | 2025 | 12 | 22 | Malakand-3 HPS | 81 | 25 | 23.93 | 574264 | 567900 | 20.52 | 15.91 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1625727.33 | 3939361.47 | 6364 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-22 | 2025 | 12 | 22 | Pehur HPS | 18 | 8.66 | 7 | 186000 | 181000 | 11 | 17 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 681827 | 945517 | 5000 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-22 | 2025 | 12 | 22 | Reshun HPS | 4.2 | 1.51 | 1.51 | 34000 | 33410 | 2 | 2.08 | 69.37 | 13.48 | 66.67 | 45 | 67200 | 905856 | 450366.8 | 455489.2 | 590 | 1. outgoing feeder breaker remained Off for 2hours for storage of water in the reservoir. 2. Mastuj and Booni Section connected with feeder No. II from 9:20am to 12:20pm. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-23 | 2025 | 12 | 23 | Daral Khwar HPS | 36.6 | 3.8 | 3.3 | 79370 | 76170 | 1.62 | 1.27 | 42.33 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 629796.41 | 3292155.94 | 3200 | Unit No 01 was on bar delivering an average load equal to 3.3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-23 | 2025 | 12 | 23 | Jabori HPS | 10.2 | 3.5 | 3 | 67040 | 65060 | 4.73 | 2.19 | 73 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 371440.55 | 1026171.61 | 1980 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-23 | 2025 | 12 | 23 | Karora HPS | 11.8 | 2.9 | 2.13 | 50480 | 49222 | 1.78 | 1.51 | 50.33 | 7.78 | 59.33 | 0.69 | 168032 | 1307288.96 | 382947.16 | 924341.8 | 1258 | The plant was operational on average load 2.13MW and Maximum load 2.9MW as per hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-23 | 2025 | 12 | 23 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11.4 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | All units are standby due to repair work in Box Channel | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-23 | 2025 | 12 | 23 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 16 | 12.5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 2239 Hrs on 17-12-2025 due to low hydrological inflow, following a significant drop in the headrace water level caused by decreased canal discharge. The recorded inflow was up to 12.5cumecs, whereas the minimum required inflow for safe and smooth unit operation is 15cumecs. | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-23 | 2025 | 12 | 23 | Malakand-3 HPS | 81 | 25 | 24.12 | 578780 | 572210 | 20.52 | 15.48 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1638065.57 | 3927023.23 | 6570 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-23 | 2025 | 12 | 23 | Pehur HPS | 18 | 8.17 | 7.18 | 172200 | 167000 | 11 | 15.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 629089 | 998255 | 5200 | Plant remained operational throughout 24 hours as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-23 | 2025 | 12 | 23 | Reshun HPS | 4.2 | 2.99 | 1.6 | 36000 | 35405 | 2 | 2.2 | 73.43 | 13.48 | 66.67 | 45 | 67200 | 905856 | 477259.4 | 428596.6 | 595 | 1. outgoing feeder breaker remaind Off 5time for storage of water in the reservoir. 2. Mastuj section remained Off from 8.00 am to 01:00pm. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-24 | 2025 | 12 | 24 | Daral Khwar HPS | 36.6 | 4 | 3 | 72110 | 69310 | 1.62 | 1.16 | 38.67 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 573075.87 | 3348876.48 | 2800 | Unit No 01 was on bar delivering an average load equal to 3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-24 | 2025 | 12 | 24 | Jabori HPS | 10.2 | 2.5 | 2.3 | 55290 | 53350 | 4.73 | 1.81 | 60.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 304585.82 | 1093026.34 | 1940 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-24 | 2025 | 12 | 24 | Karora HPS | 11.8 | 2.9 | 2.01 | 39028 | 37003 | 2.39 | 1.33 | 44.33 | 7.78 | 79.67 | 0.69 | 225616 | 1755292.48 | 287883.34 | 1467409.14 | 2025 | The plant was operational on average load of 2.01mw and maximum load of 2.9mw as per available hydrology | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-24 | 2025 | 12 | 24 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11.4 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The units are standby due to repair work in Box Channel. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-24 | 2025 | 12 | 24 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 16 | 10 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | The unit has remained on standby since 2239 Hrs on 17-12-2025 due to low hydrological inflow, following a significant drop in the headrace water level caused by decreased canal discharge. The recorded inflow was up to 13 cumecs, whereas the minimum required inflow for safe and smooth unit operation is 15 cumecs | machai.12333@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-12-24 | 2025 | 12 | 24 | Malakand-3 HPS | 81 | 24 | 20.61 | 494623 | 488200 | 20.52 | 13.35 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1397570.14 | 4167518.66 | 6423 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-24 | 2025 | 12 | 24 | Pehur HPS | 18 | 8.29 | 8.16 | 195900 | 191000 | 11 | 17 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 719497 | 907847 | 4900 | Plant remained operational throughout 24 hours as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-24 | 2025 | 12 | 24 | Reshun HPS | 4.2 | 3.1 | 1.49 | 37000 | 36400 | 2.26 | 2 | 66.67 | 13.48 | 75.5 | 45 | 76104 | 1025881.92 | 490672 | 535209.92 | 600 | 1. outgoing Feeder Breaker remained Off 2.55hour for 4times due to less hydrology. 2. Booni Section connected with Feeder No. II from 9:30am to 01:00pm. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-25 | 2025 | 12 | 25 | Daral Khwar HPS | 36.6 | 4 | 3 | 70880 | 68080 | 1.62 | 1.14 | 38 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 562905.86 | 3359046.48 | 2800 | Unit No 01 was on bar delivering an average load equal to 3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-25 | 2025 | 12 | 25 | Jabori HPS | 10.2 | 2.4 | 2.2 | 51870 | 49920 | 4.73 | 1.7 | 56.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 285003.26 | 1112608.9 | 1950 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-25 | 2025 | 12 | 25 | Karora HPS | 11.8 | 2 | 1.55 | 37310 | 35586 | 2.39 | 1.35 | 13.17 | 7.78 | 79.67 | 0.69 | 225616 | 1755292.48 | 276859.08 | 1478433.4 | 1724 | No data submitted for this date | rekarorahps2000@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-12-25 | 2025 | 12 | 25 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.24 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | All three units shutdown due to repairing of box channel | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-25 | 2025 | 12 | 25 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 16 | 5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | weekly canal closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-25 | 2025 | 12 | 25 | Malakand-3 HPS | 81 | 21 | 14.95 | 358824 | 352770 | 20.52 | 10.07 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1009874.68 | 4555214.12 | 6054 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-25 | 2025 | 12 | 25 | Pehur HPS | 18 | 8.5 | 8.34 | 200200 | 195000 | 11 | 17 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 734565 | 892779 | 5200 | The plant remained operational throughout 24 hours as per available hydrology, and the irrigation valve is closed. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-25 | 2025 | 12 | 25 | Reshun HPS | 4.2 | 3.01 | 1.48 | 36000 | 35400 | 2 | 2.2 | 73.43 | 13.48 | 66.67 | 45 | 67200 | 905856 | 477192 | 428664 | 600 | 1. Outgooing feeder remained Off 3.30hours for storage of Water in ther reservoir. 2. Mastuj Section remained Off for 7.00hours. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-26 | 2025 | 12 | 26 | Daral Khwar HPS | 36.6 | 4.5 | 3.2 | 76520 | 73320 | 1.62 | 1.23 | 41 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 606231.76 | 3315720.59 | 3200 | Unit No 01 was on bar delivering an average load equal to 3.2 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-26 | 2025 | 12 | 26 | Jabori HPS | 10.2 | 2.5 | 2 | 48747 | 46800 | 4.73 | 1.59 | 53 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 267190.56 | 1130421.6 | 1947 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-26 | 2025 | 12 | 26 | Karora HPS | 11.8 | 2.9 | 1.66 | 35592 | 34170 | 2.39 | 1.37 | 45.67 | 7.78 | 79.67 | 0.69 | 225616 | 1755292.48 | 265842.6 | 1489449.88 | 1422 | The plant was operational on average load of 1.66mw and maximum load of 2.9mw as per available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-26 | 2025 | 12 | 26 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.24 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | The plant is shut down to facilitate Box Channel repair. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-26 | 2025 | 12 | 26 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 16 | 5 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Weekly Canal Closure | machai.12333@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2025-12-26 | 2025 | 12 | 26 | Malakand-3 HPS | 81 | 14 | 12.54 | 301024 | 294670 | 20.52 | 9.61 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 843551.81 | 4721536.99 | 6354 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-26 | 2025 | 12 | 26 | Pehur HPS | 18 | 8.56 | 8.5 | 202900 | 197000 | 11 | 17 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 742099 | 885245 | 5900 | plant remained operational throughout 24 hours as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-26 | 2025 | 12 | 26 | Reshun HPS | 4.2 | 3.31 | 1.54 | 35000 | 34400 | 2 | 2.14 | 71.4 | 13.48 | 66.67 | 45 | 67200 | 905856 | 463712 | 442144 | 600 | 1. Outgoing feeder breaker remained Off 4times for 4.35hours for storage of water. 2. Mastuj and Booni Section connected with Feeder No.II for 4.15hours. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-27 | 2025 | 12 | 27 | Daral Khwar HPS | 36.6 | 4.4 | 2.9 | 70080 | 67280 | 1.62 | 1.13 | 37.67 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 556291.22 | 3365661.12 | 2800 | Unit No 01 was on bar delivering an average load equal to 2.9 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-27 | 2025 | 12 | 27 | Jabori HPS | 10.2 | 2.3 | 2.1 | 49530 | 47520 | 4.73 | 1.62 | 54 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 271301.18 | 1126310.98 | 2010 | Plant was shutdown from 1642 Hrs to 1700 Hrs for clearing/refreshing the cache memory of unit 01 governor PLC. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-27 | 2025 | 12 | 27 | Karora HPS | 11.8 | 2.87 | 1.65 | 33794 | 32381 | 1.78 | 1.36 | 45.33 | 7.78 | 59.33 | 0.69 | 168032 | 1307288.96 | 251924.18 | 1055364.78 | 1413 | The plant was operational on average load 1.65MW and maximum load of 2.87MW as per available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-27 | 2025 | 12 | 27 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.24 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | The plant remained shut down to facilitate Box Channel repair. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-27 | 2025 | 12 | 27 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 16 | 4 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | weekly irrigation canal closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-27 | 2025 | 12 | 27 | Malakand-3 HPS | 81 | 13 | 12.02 | 288490 | 282080 | 20.52 | 9.26 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 807510.42 | 4757578.38 | 6410 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-27 | 2025 | 12 | 27 | Pehur HPS | 18 | 8.75 | 8.5 | 204000 | 199000 | 11 | 17 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 749633 | 877711 | 5000 | Plant remained operational throughout 24 Hrs as per available hydrology + irrigation valve open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-27 | 2025 | 12 | 27 | Reshun HPS | 4.2 | 3.15 | 1.42 | 35000 | 34424 | 2 | 2.14 | 71.4 | 13.48 | 66.67 | 45 | 67200 | 905856 | 464035.52 | 441820.48 | 576 | 1. Outgoing feeder breaker remained Off 4times for 7.10 hours for storage of water in the Reservoir. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-28 | 2025 | 12 | 28 | Daral Khwar HPS | 36.6 | 4 | 3.1 | 73420 | 70620 | 1.62 | 1.18 | 39.33 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 583907.35 | 3338045 | 2800 | Unit No 01 was on bar delivering an average load equal to 3.1 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-28 | 2025 | 12 | 28 | Jabori HPS | 10.2 | 2.9 | 2.1 | 48519 | 46560 | 4.73 | 1.59 | 53 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 265820.35 | 1131791.81 | 1959 | Plant was shutdown from 1406 Hrs to 1523 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-28 | 2025 | 12 | 28 | Karora HPS | 11.8 | 3 | 1.32 | 32605 | 31398 | 1.78 | 0.2 | 6.57 | 7.78 | 59.33 | 0.69 | 168032 | 1307288.96 | 244276.44 | 1063012.52 | 1207 | the plant was operational on average load 1.32MW and maximum load of 3.0MW as per available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-28 | 2025 | 12 | 28 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11.4 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remained shut down to facilitate Box Channel repair | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-28 | 2025 | 12 | 28 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 8 | 2 | 0 | 4.671 | 50 | 70 | 31200 | 145735.2 | 0 | 145735.2 | 0 | No data submitted for this date | engr.atifwazir@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2025-12-28 | 2025 | 12 | 28 | Malakand-3 HPS | 81 | 12 | 11.49 | 275756 | 269400 | 20.52 | 8.91 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 771211.38 | 4793877.42 | 6356 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-28 | 2025 | 12 | 28 | Pehur HPS | 18 | 8.61 | 7.99 | 191800 | 186000 | 11 | 16 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 700662 | 926682 | 5800 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-28 | 2025 | 12 | 28 | Reshun HPS | 4.2 | 3.09 | 1.48 | 36000 | 35430 | 2 | 2.2 | 73.43 | 13.48 | 66.67 | 45 | 67200 | 905856 | 477596.4 | 428259.6 | 570 | outgoing feeder breaker remained Off for 6.00hours for the storage of water in the reservoir. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-29 | 2025 | 12 | 29 | Daral Khwar HPS | 36.6 | 3.3 | 2 | 48820 | 46420 | 1.62 | 0.78 | 26 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 383814.49 | 3538137.86 | 2400 | 1. Unit No 01 was on bar delivering an average load equal to 2 MW according to available hydrology. 2. The plant shutdown at 0926 hrs and 132 KV line tripped at 0930 hrs due to a PESCO scheduled shutdown for the annual maintenance of the 132 KV transmission line. The line was restored at 1503 hrs. 3. Unit No 01 synchronized with the national grid at 1520 hrs. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-29 | 2025 | 12 | 29 | Jabori HPS | 10.2 | 2.7 | 2.1 | 47049 | 45120 | 4.73 | 1.54 | 51.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 257599.1 | 1140013.06 | 1929 | Plant was shutdown from 1430 Hrs to 1550 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-29 | 2025 | 12 | 29 | Karora HPS | 11.8 | 2.86 | 1.65 | 33673 | 32276 | 1.78 | 1.36 | 45.33 | 7.78 | 59.33 | 0.69 | 168032 | 1307288.96 | 251107.28 | 1056181.68 | 1397 | the plant was operational delivering power max load 2.86MW min load0MW | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-29 | 2025 | 12 | 29 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11.4 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remained shutdown due to Box Channel repair. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-29 | 2025 | 12 | 29 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Weekly Closure. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-29 | 2025 | 12 | 29 | Malakand-3 HPS | 81 | 12 | 4.01 | 96168 | 94060 | 20.52 | 4.7 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 269265.56 | 5295823.24 | 2108 | As per the Irrigation Department letter C.W. No. 1023-3 dated 29-12-2025, water was diverted from the auxiliary tunnel due to a shortage in the main canal. As a result of low hydrology, the unit # 02 was desynchronized from the system at 08:28 hrs on 29-12-2025 and subsequently placed on standby. Unit # 01 & 03 were already standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-29 | 2025 | 12 | 29 | Pehur HPS | 18 | 8.19 | 7.6 | 182300 | 178000 | 11 | 15.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 670526 | 956818 | 4300 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-29 | 2025 | 12 | 29 | Reshun HPS | 4.2 | 2.96 | 1.46 | 33000 | 32419 | 2 | 2.02 | 67.33 | 13.48 | 66.67 | 45 | 67200 | 905856 | 437008.12 | 468847.88 | 581 | Outgoing feeder breaker remained Off 3.40hours for the storage of water in Reservoir. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-30 | 2025 | 12 | 30 | Daral Khwar HPS | 36.6 | 3 | 2.8 | 66420 | 63220 | 1.62 | 1.06 | 35.33 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 522721.93 | 3399230.42 | 3200 | Unit No 01 was on bar delivering an average load equal to 2.8 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-30 | 2025 | 12 | 30 | Jabori HPS | 10.2 | 3.4 | 2.1 | 45092 | 43200 | 4.73 | 1.47 | 49 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 246637.44 | 1150974.72 | 1892 | Plant was shutdown from 0800 Hrs to 0930 Hrs and from 2200 Hrs to 2313 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-30 | 2025 | 12 | 30 | Karora HPS | 11.8 | 2.99 | 1.67 | 37179 | 35741 | 1.78 | 1.37 | 45.67 | 7.78 | 59.33 | 0.69 | 168032 | 1307288.96 | 278064.98 | 1029223.98 | 1438 | the plant was operational delivering power max load 2.99MW average load 1.67MW average flow 1.37cumecs | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-30 | 2025 | 12 | 30 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11.4 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remained shutdown due to Box Channel repair. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-30 | 2025 | 12 | 30 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | weekly closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-30 | 2025 | 12 | 30 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 20.52 | 0 | 0 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 0 | 5565088.8 | 0 | As per the Irrigation Department letter C.W. No. 1023-3 dated 29-12-2025, water was diverted from the auxiliary tunnel due to a shortage in the main canal. As a result of low hydrology, the unit # 02 was desynchronized from the system at 08:28 hrs on 29-12-2025 and subsequently placed on standby. Unit # 01 & 03 were already standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-30 | 2025 | 12 | 30 | Pehur HPS | 18 | 8.44 | 8.17 | 196000 | 191000 | 11 | 17 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 719497 | 907847 | 5000 | The plant remained operational throughout 24 hours as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-30 | 2025 | 12 | 30 | Reshun HPS | 4.2 | 3.1 | 1.44 | 34000 | 33417 | 2 | 2.08 | 69.37 | 13.48 | 66.67 | 45 | 67200 | 905856 | 450461.16 | 455394.84 | 583 | Outgoing feeder breaker remained Off 4.55hours for storage of water in reservoir. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-31 | 2025 | 12 | 31 | Daral Khwar HPS | 36.6 | 3 | 2.8 | 67410 | 64210 | 1.62 | 1.07 | 35.67 | 8.2683 | 54 | 48 | 474336 | 3921952.35 | 530907.54 | 3391044.81 | 3200 | Unit No 01 was on bar delivering an average load equal to 2.8 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-31 | 2025 | 12 | 31 | Jabori HPS | 10.2 | 2.1 | 2.2 | 52631 | 50660 | 4.73 | 1.72 | 57.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 289228.07 | 1108384.09 | 1971 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-31 | 2025 | 12 | 31 | Karora HPS | 11.8 | 2.95 | 2.01 | 40969 | 39436 | 1.78 | 1.67 | 55.67 | 7.78 | 59.33 | 0.69 | 168032 | 1307288.96 | 306812.08 | 1000476.88 | 1533 | the plant was operational delivering power max load 2.95MW average load 2.01MW average flow Cumecs 1.67 | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-31 | 2025 | 12 | 31 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11.4 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The Plant is shut down due to Box channel repair work. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-31 | 2025 | 12 | 31 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Weekly closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-31 | 2025 | 12 | 31 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 20.52 | 0 | 0 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 0 | 5565088.8 | 0 | As per the Irrigation Department letter C.W. No. 1023-3 dated 29-12-2025, water was diverted from the auxiliary tunnel due to a shortage in the main canal. As a result of low hydrology, the unit # 02 was desynchronized from the system at 08:28 hrs on 29-12-2025 and subsequently placed on standby. Unit # 01 & 03 were already standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-31 | 2025 | 12 | 31 | Pehur HPS | 18 | 8.48 | 8.43 | 202300 | 197000 | 11 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 742099 | 885245 | 5300 | Plant remained operational throughout 24 Hrs as per available hydrology + low irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2025-12-31 | 2025 | 12 | 31 | Reshun HPS | 4.2 | 3.02 | 1.47 | 34000 | 33416 | 2 | 2.02 | 67.37 | 13.48 | 66.67 | 45 | 67200 | 905856 | 450447.68 | 455408.32 | 584 | outgoing feeder breaker remained Off 4times for 3.05hours for the storage of water in Reservoir. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-01 | 2026 | 1 | 1 | Daral Khwar HPS | 36.6 | 3 | 3.1 | 73280 | 69680 | 1.5 | 1.17 | 39 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 576135.14 | 3055302.22 | 3600 | Unit No 01 was on bar delivering an average load equal to 3.1 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-01 | 2026 | 1 | 1 | Jabori HPS | 10.2 | 3.2 | 2.5 | 61114 | 59090 | 4.73 | 2 | 66.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 337356.63 | 1060255.53 | 2024 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-01 | 2026 | 1 | 1 | Karora HPS | 11.8 | 2.98 | 2.25 | 50062 | 48077 | 2.01 | 1.85 | 61.67 | 7.78 | 67 | 0.69 | 189744 | 1476208.32 | 374039.06 | 1102169.26 | 1985 | the plant was operational delivering power max load 2.98MW average laoad2.25MW | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-01 | 2026 | 1 | 1 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant was shut down due to Box channel repair work in progress. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-01 | 2026 | 1 | 1 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Weekly Closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-01 | 2026 | 1 | 1 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 30.23 | 0 | 0 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 0 | 5565088.8 | 0 | As per the Irrigation Department letter C.W. No. 1023-3 dated 29-12-2025, water was diverted from the auxiliary tunnel due to a shortage in the main canal. As a result of low hydrology, the unit # 02 was desynchronized from the system at 08:28 hrs on 29-12-2025 and subsequently placed on standby. Unit # 01 & 03 were already standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-01 | 2026 | 1 | 1 | Pehur HPS | 18 | 8.67 | 8.56 | 205600 | 200000 | 10.02 | 17 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 753400 | 873944 | 5600 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-01 | 2026 | 1 | 1 | Reshun HPS | 4.2 | 2.84 | 1.53 | 34000 | 33412 | 2 | 2.08 | 69.37 | 13.48 | 66.67 | 45 | 67200 | 905856 | 450393.76 | 455462.24 | 588 | Outgoing feeder breaker remained Off 5.27hours for storage of water in Reservoir. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-02 | 2026 | 1 | 2 | Daral Khwar HPS | 36.6 | 4 | 3.3 | 80040 | 76840 | 1.5 | 1.29 | 43 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 635336.17 | 2996101.19 | 3200 | Unit No 01 was on bar delivering an average load equal to 3.3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-02 | 2026 | 1 | 2 | Jabori HPS | 10.2 | 2.7 | 2 | 40218 | 38620 | 4.73 | 1.31 | 43.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 220489.3 | 1177122.86 | 1598 | Plant was shutdown from 0900 Hrs to 1411 Hrs due to permit on 132KV Transmission line Oghi as per NGC letter No. 683DM/AM(N)/NGC Mansehra | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-02 | 2026 | 1 | 2 | Karora HPS | 11.8 | 3.45 | 2.08 | 53870 | 51889 | 2.01 | 1.59 | 53 | 7.78 | 67 | 0.69 | 189744 | 1476208.32 | 403696.42 | 1072511.9 | 1981 | the plant was operational delivering power max load 3.45MW average load 2.08MW average flow 1.59Cumecs | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-02 | 2026 | 1 | 2 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant was shut down due to box channel repair work in progress form EPC contractor side. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-02 | 2026 | 1 | 2 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Weekly Closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-02 | 2026 | 1 | 2 | Malakand-3 HPS | 81 | 26 | 14.12 | 337352 | 332550 | 30.23 | 9.96 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 951990.88 | 4613097.92 | 4802 | Unit # 02 synchronized with the system at 07:50hrs dated 02-01-2026 after diversion of water to Malakand-III channel by irrigation department. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-02 | 2026 | 1 | 2 | Pehur HPS | 18 | 9.03 | 8.77 | 210400 | 205000 | 10.02 | 17 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 772235 | 855109 | 5400 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-02 | 2026 | 1 | 2 | Reshun HPS | 4.2 | 2.91 | 1.57 | 35000 | 34420 | 2 | 2.14 | 71.4 | 13.48 | 66.67 | 45 | 67200 | 905856 | 463981.6 | 441874.4 | 580 | Outgoing feeder remain Off 5times for 2.27hours for the storage of water in reservoir. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-03 | 2026 | 1 | 3 | Daral Khwar HPS | 36.6 | 3.5 | 3.5 | 82960 | 79760 | 1.5 | 1.33 | 44.33 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 659479.61 | 2971957.75 | 3200 | Unit No 01 was on bar delivering an average load equal to 3.5 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-03 | 2026 | 1 | 3 | Jabori HPS | 10.2 | 2.5 | 2 | 45606 | 43680 | 4.73 | 1.49 | 49.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 249377.86 | 1148234.3 | 1926 | Plant was shutdown from 1230 Hrs to 1355 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-03 | 2026 | 1 | 3 | Karora HPS | 11.8 | 2.9 | 1.78 | 39872 | 38359 | 2.01 | 2.25 | 75 | 7.78 | 67 | 0.69 | 189744 | 1476208.32 | 298433.02 | 1177775.3 | 1513 | The plant was operational on average load of 1.78MW and maximum load of 2.90MW as per available Hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-03 | 2026 | 1 | 3 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant was shut down due to box channel repair work in progress from EPC contractor side. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-03 | 2026 | 1 | 3 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | weekly closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-03 | 2026 | 1 | 3 | Malakand-3 HPS | 81 | 21 | 18.65 | 447647 | 441540 | 30.23 | 12.53 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1263996.56 | 4301092.24 | 6107 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-03 | 2026 | 1 | 3 | Pehur HPS | 18 | 9.03 | 9 | 215000 | 209000 | 10.02 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 787303 | 840041 | 6000 | Plant remained operational throughout 24 Hrs as per available hydrology . | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-03 | 2026 | 1 | 3 | Reshun HPS | 4.2 | 2.69 | 1.4 | 3300 | 32421 | 2 | 2.02 | 67.37 | 13.48 | 66.67 | 45 | 67200 | 905856 | 437035.08 | 468820.92 | 29121 | Outgoing feeder breaker remained Off 3times for 3.30hours for storage of water in Reservoir. | zafar.src@gmail.com | Original | CHECK: Net > Units (source me verify karein) | Link_Generation_Data_Summary.xlsx
2026-01-04 | 2026 | 1 | 4 | Daral Khwar HPS | 36.6 | 3.5 | 3.1 | 74140 | 70940 | 1.5 | 1.19 | 39.67 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 586553.2 | 3044884.16 | 3200 | Unit No 01 was on bar delivering an average load equal to 3.1 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-04 | 2026 | 1 | 4 | Jabori HPS | 10.2 | 2.1 | 2 | 49087 | 47010 | 4.73 | 1.6 | 53.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 268389.49 | 1129222.67 | 2077 | Plant was operational as per available hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-04 | 2026 | 1 | 4 | Karora HPS | 11.8 | 2.92 | 1.31 | 32410 | 31194 | 2.01 | 1.07 | 35.67 | 7.78 | 67 | 0.69 | 189744 | 1476208.32 | 242689.32 | 1233519 | 1216 | the plant was operational on average load 1.31MW and maximum load 2.92MW as per available hydrology. Both units are remain shutdown due to low hydrology from 19:56 hrs. 04-01-2026. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-04 | 2026 | 1 | 4 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | All units are standby due to box channel repair work. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-04 | 2026 | 1 | 4 | Machai HPS | 2.6 | 0.53 | 0.24 | 5944 | 5500 | 16 | 16 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 25690.5 | 265779.9 | 444 | Unit after all preliminary checks was started at 1208 hrs on 03-01-2026 following restoration of rated head due to increase inflow in canal. Initially Unit was maintained at FSNL and then synchronized with system at 1244 hrs. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-04 | 2026 | 1 | 4 | Malakand-3 HPS | 81 | 18 | 16.69 | 400536 | 394800 | 30.23 | 11.48 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1130193.96 | 4434894.84 | 5736 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-04 | 2026 | 1 | 4 | Pehur HPS | 18 | 9.09 | 9.01 | 216300 | 211000 | 10.02 | 19 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 794837 | 832507 | 5300 | Plant remained operational throughout 24 Hrs as per available hydrology . | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-04 | 2026 | 1 | 4 | Reshun HPS | 4.2 | 2.68 | 1.45 | 33000 | 32422 | 2 | 2.02 | 67.33 | 13.48 | 66.67 | 45 | 67200 | 905856 | 437048.56 | 468807.44 | 578 | outgoing feeder breaker remained Off 3times for 4.32hours for storage of water in Reservoir. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-05 | 2026 | 1 | 5 | Daral Khwar HPS | 36.6 | 3.2 | 3 | 71020 | 67420 | 1.5 | 1.13 | 37.67 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 557448.79 | 3073988.57 | 3600 | Unit No 01 was on bar delivering an average load equal to 3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-05 | 2026 | 1 | 5 | Jabori HPS | 10.2 | 2.1 | 2 | 47354 | 45270 | 4.73 | 1.55 | 51.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 258455.48 | 1139156.68 | 2084 | Plant was shutdown from 1540 Hrs to 1610 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-05 | 2026 | 1 | 5 | Karora HPS | 11.8 | 2.87 | 0.48 | 11967 | 11483 | 2.01 | 0.39 | 13 | 7.78 | 67 | 0.69 | 189744 | 1476208.32 | 89337.74 | 1386870.58 | 484 | the plant was operational on average load 0.48MW and maximum load 2.87MW as per available hydrology. Both units are remain shutdown due to low hydrology from 20.00 hrs .05-01-2026 | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-05 | 2026 | 1 | 5 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | All units are standby due to repair work in Box Channel | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-05 | 2026 | 1 | 5 | Machai HPS | 2.6 | 0.65 | 0.41 | 9220 | 8568 | 15 | 1 | 33.33 | 4.671 | 100 | 70 | 62400 | 291470.4 | 40021.13 | 251449.27 | 652 | The unit, while on bar and delivering power to the National Grid as per available water inflow and prevailing system conditions | engr.atifwazir@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-05 | 2026 | 1 | 5 | Malakand-3 HPS | 81 | 18 | 17.25 | 414112 | 408170 | 30.12 | 11.83 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1168468.26 | 4396620.54 | 5942 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-05 | 2026 | 1 | 5 | Pehur HPS | 18 | 9.16 | 9.05 | 217200 | 211000 | 10.02 | 19 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 794837 | 832507 | 6200 | Plant remained operational throughout 24 Hrs as per available hydrology . | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-05 | 2026 | 1 | 5 | Reshun HPS | 4.2 | 2.8 | 1.44 | 34000 | 33431 | 2 | 2.08 | 69.37 | 13.48 | 66.67 | 45 | 67200 | 905856 | 450649.88 | 455206.12 | 569 | outgoing feeder breaker remained Off 4times for 5.10hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-06 | 2026 | 1 | 6 | Daral Khwar HPS | 36.6 | 3.5 | 2.8 | 67120 | 63920 | 1.5 | 1.07 | 35.67 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 528509.74 | 3102927.62 | 3200 | Unit No 01 was on bar delivering an average load equal to 2.8 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-06 | 2026 | 1 | 6 | Jabori HPS | 10.2 | 2.1 | 2 | 44982 | 42900 | 4.73 | 1.47 | 49 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 244924.68 | 1152687.48 | 2082 | Plant was shutdown from 1410 Hrs to 1520 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-06 | 2026 | 1 | 6 | Karora HPS | 11.8 | 2.88 | 0.48 | 11203 | 10777 | 2.01 | 0.39 | 13 | 7.78 | 67 | 0.69 | 189744 | 1476208.32 | 83845.06 | 1392363.26 | 426 | the plant was operational on average load 0.48MW and maximum load 2.88MW as per available hydrology. both units are remain shutdown due to low hydrology from 20:00 hrs 06-01-2026 | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-06 | 2026 | 1 | 6 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remain shutdown down due to box channel repair work as requested by the EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-06 | 2026 | 1 | 6 | Machai HPS | 2.6 | 0.56 | 0.26 | 7008 | 6392 | 1 | 14.5 | 100 | 4.671 | 33.33 | 70 | 20800 | 97156.8 | 29857.03 | 67299.77 | 616 | The unit, while on bar and delivering power to the National Grid as per available water inflow and prevailing system conditions, tripped at 0105Hrs on 06.01.2026 due to reverse power resulting from high system voltage i-e 11.9KV Vs 11KV. Subsequently, the unit remained shut down/standby and could not be synchronized with the system due to persistently high system voltage. The unit was finally synchronized with the system at 0616Hr, once the voltage stabilized. Unit tripped at 0924 & 1131 hrs due to earth fault, 11KV line restored at 0928 & 1143 hrs , Unit synchronised at 0932 & 1149 hrs respectively. Unit tripped at 1444, 1557, 1936 hrs due to reverse power while synchronised at 1505, 1837, 2107 hrs respectively. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-06 | 2026 | 1 | 6 | Malakand-3 HPS | 81 | 18 | 16.62 | 398821 | 392130 | 11.58 | 20.52 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1122550.55 | 4442538.25 | 6691 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-06 | 2026 | 1 | 6 | Pehur HPS | 18 | 9.19 | 9.07 | 217700 | 212000 | 10.02 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 798604 | 828740 | 5700 | The plant remained operational throughout 24 hours as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-06 | 2026 | 1 | 6 | Reshun HPS | 4.2 | 2.6 | 1.26 | 26000 | 25490 | 2 | 1.59 | 53.03 | 13.48 | 66.67 | 45 | 67200 | 905856 | 343605.2 | 562250.8 | 510 | 1. Outgoing Feeder Breaker remained Off 4times for 6.00hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-07 | 2026 | 1 | 7 | Daral Khwar HPS | 36.6 | 3.5 | 2.7 | 64370 | 60770 | 1.5 | 1.02 | 34 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 502464.59 | 3128972.77 | 3600 | Unit No 01 was on bar delivering an average load equal to 2.7 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-07 | 2026 | 1 | 7 | Jabori HPS | 10.2 | 2 | 2 | 43714 | 41620 | 4.73 | 1.43 | 47.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 237616.9 | 1159995.26 | 2094 | Plant was shutdown from 1230 Hrs to 1345 Hrs due to low hydrology | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-07 | 2026 | 1 | 7 | Karora HPS | 11.8 | 2.84 | 0.35 | 10637 | 10218 | 2.01 | 0.29 | 9.67 | 7.78 | 67 | 0.69 | 189744 | 1476208.32 | 79496.04 | 1396712.28 | 419 | the plant was operational on average load 0.35 MW and maximum load 2.84 MW as per available hydrology. Both units are remain shutdown due to low hydrology from 19:51hrs 07-01-2026. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-07 | 2026 | 1 | 7 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The Plant remain shutdown due to box channel repair work as requested by the EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-07 | 2026 | 1 | 7 | Machai HPS | 2.6 | 0.53 | 0.27 | 6500 | 6028 | 1 | 14 | 100 | 4.671 | 33.33 | 70 | 20800 | 97156.8 | 28156.79 | 69000.01 | 472 | The unit, while on bar and delivering power to the National Grid as per available water inflow and prevailing system conditions, stopped at 0026Hrs on 06.01.2026 due to less head race level. Subsequently, the unit remained shut down/standby and could not be synchronized with the system due to persistently high system voltage. The unit was finally synchronized with the system at 0653Hr, once the voltage stabilized. Unit tripped at 0750, 0949, 1141 hrs due to 132KV tripping, 11KV line restored at 0844, 1032, 1203 hrs. Unit synchronised at 0854, 1041, 1213 hrs respectively. Unit normally stopped at 1720 hrs due to low headrace level and Synchronised at 1838 hrs. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-07 | 2026 | 1 | 7 | Malakand-3 HPS | 81 | 18 | 15.9 | 381577 | 375140 | 30.23 | 11.48 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1073913.28 | 4491175.52 | 6437 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-07 | 2026 | 1 | 7 | Pehur HPS | 18 | 9.23 | 7.88 | 189200 | 184000 | 10.02 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 693128 | 934216 | 5200 | The plant remained operational throughout 24 hours as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-07 | 2026 | 1 | 7 | Reshun HPS | 4.2 | 2.52 | 1.26 | 29000 | 28460 | 2 | 1.77 | 59 | 13.48 | 66.67 | 45 | 67200 | 905856 | 383640.8 | 522215.2 | 540 | outgoing Feeder Breaker remained Off 4times fir 6.25 for storage of water in reservoir. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-08 | 2026 | 1 | 8 | Daral Khwar HPS | 36.6 | 3.5 | 2.6 | 62720 | 59520 | 1.5 | 1 | 33.33 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 492129.22 | 3139308.14 | 3200 | Unit No 01 was on bar delivering an average load equal to 2.6 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-08 | 2026 | 1 | 8 | Jabori HPS | 10.2 | 2 | 2 | 43125 | 41120 | 4.73 | 1.41 | 47 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 234762.3 | 1162849.86 | 2005 | Plant was shutdown from 1255 Hrs to 1435 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-08 | 2026 | 1 | 8 | Karora HPS | 11.8 | 2.85 | 0.35 | 10277 | 9858 | 2.01 | 0.3 | 10 | 7.78 | 67 | 0.69 | 189744 | 1476208.32 | 76695.24 | 1399513.08 | 419 | the plant was operational on average load 0.35 MW and maximum load 2.85 MW as per available hydrology. Both units are remain shutdown due to low hydrology from 19:51hrs 08-01-2026 | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-08 | 2026 | 1 | 8 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remain shutdown due to box channel repair work as requested by the EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-08 | 2026 | 1 | 8 | Machai HPS | 2.6 | 0.52 | 0.1 | 2320 | 2156 | 16 | 13.9 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 10070.68 | 281399.72 | 164 | 1*unit tripped at 0102,0655,1150hrs due to revers power, while unit synch with the system at 0627,0710,1256hrs 2* unit tripped at 0729,1026,1415hrs due to 132kv line tripped, 11kv line restored at 0920,1032,1427hrs, while unit synch with the system at 0951,1043hrs | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-08 | 2026 | 1 | 8 | Malakand-3 HPS | 81 | 16 | 13.32 | 319742 | 312970 | 30.23 | 9.68 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 895939.22 | 4669149.58 | 6772 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-08 | 2026 | 1 | 8 | Pehur HPS | 18 | 8.96 | 5.5 | 131200 | 127000 | 10.02 | 12 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 478409 | 1148935 | 4200 | Generation is less due to low irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-08 | 2026 | 1 | 8 | Reshun HPS | 4.2 | 3.28 | 1.23 | 28000 | 27445 | 1.5 | 1.71 | 57.13 | 13.48 | 50 | 45 | 50400 | 679392 | 369958.6 | 309433.4 | 555 | Outgoing Feeder Breaker remained Off 5times for 8.20hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-09 | 2026 | 1 | 9 | Daral Khwar HPS | 36.6 | 3 | 2.6 | 63300 | 59700 | 1.5 | 1 | 33.33 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 493617.51 | 3137819.85 | 3600 | Unit No 01 was on bar delivering an average load equal to 2.6 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-09 | 2026 | 1 | 9 | Jabori HPS | 10.2 | 2 | 2 | 43407 | 41400 | 4.73 | 1.42 | 47.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 236360.88 | 1161251.28 | 2007 | Plant was shutdown from 1000 Hrs to 1145 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-09 | 2026 | 1 | 9 | Karora HPS | 11.8 | 2.87 | 0.47 | 10097 | 9687 | 2.56 | 0.39 | 13 | 7.78 | 85.33 | 0.69 | 241664 | 1880145.92 | 75364.86 | 1804781.06 | 410 | the plant was operationl on average load of 0.47 mw and maximum load of 2.87 mw as per available hydrology | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-09 | 2026 | 1 | 9 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remain shutdown due to box channel repair work as requested by the EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-09 | 2026 | 1 | 9 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 14 | 8 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Annual closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-09 | 2026 | 1 | 9 | Malakand-3 HPS | 81 | 14 | 11.58 | 277990 | 270870 | 30.23 | 9.08 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 775419.55 | 4789669.25 | 7120 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-09 | 2026 | 1 | 9 | Pehur HPS | 18 | 8.95 | 6.92 | 166000 | 161000 | 10.02 | 14.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 606487 | 1020857 | 5000 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-09 | 2026 | 1 | 9 | Reshun HPS | 4.2 | 2.97 | 1.25 | 27000 | 26500 | 2 | 1.65 | 55.07 | 13.48 | 66.67 | 45 | 67200 | 905856 | 357220 | 548636 | 500 | outgoing feeder breaker remained Off 6times 7.53hours due less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-10 | 2026 | 1 | 10 | Daral Khwar HPS | 36.6 | 3 | 2.7 | 65650 | 62450 | 1.5 | 1.04 | 34.67 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 516355.34 | 3115082.02 | 3200 | Unit No 01 was on bar delivering an average load equal to 2.7 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-10 | 2026 | 1 | 10 | Jabori HPS | 10.2 | 2 | 2 | 42677 | 40700 | 4.73 | 1.39 | 46.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 232364.44 | 1165247.72 | 1977 | Plant was shutdown from 0900 Hrs to 1015 Hrs and from 2005 Hrs to 2105 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-10 | 2026 | 1 | 10 | Karora HPS | 11.8 | 2.85 | 0.47 | 10224 | 9825 | 2.01 | 0.38 | 12.67 | 7.78 | 67 | 0.69 | 189744 | 1476208.32 | 76438.5 | 1399769.82 | 399 | The plant was operational on average load of 0.47MW and maximum load of 2.85MW as per available Hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-10 | 2026 | 1 | 10 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | Plant is shutdown due to box channel repair work. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-10 | 2026 | 1 | 10 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 2 | 5 | 100 | 4.671 | 66.67 | 70 | 41600 | 194313.6 | 0 | 194313.6 | 0 | Annual closure. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-10 | 2026 | 1 | 10 | Malakand-3 HPS | 81 | 20 | 13.94 | 334477 | 328180 | 20.52 | 9.83 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 939480.89 | 4625607.91 | 6297 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-10 | 2026 | 1 | 10 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 10.02 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant remained shut down since 0000 hrs on date 10-01-2026, as per notification of irrigation department due to annual canal closure period 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-10 | 2026 | 1 | 10 | Reshun HPS | 4.2 | 3.03 | 1.41 | 31000 | 30520 | 2 | 1.9 | 63.23 | 13.48 | 66.67 | 45 | 67200 | 905856 | 411409.6 | 494446.4 | 480 | outgoing feeder breaker remained Off 4times for 6.26hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-11 | 2026 | 1 | 11 | Daral Khwar HPS | 36.6 | 3 | 2.8 | 66460 | 63260 | 1.5 | 1.06 | 35.33 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 523052.66 | 3108384.7 | 3200 | Unit No 01 was on bar delivering an average load equal to 2.8 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-11 | 2026 | 1 | 11 | Jabori HPS | 10.2 | 2.1 | 2 | 44169 | 42240 | 4.73 | 1.44 | 48 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 241156.61 | 1156455.55 | 1929 | Plant was shutdown from 1833 Hrs to 2011 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-11 | 2026 | 1 | 11 | Karora HPS | 11.8 | 2.88 | 0.24 | 10145 | 9727 | 2.93 | 0.2 | 6.53 | 7.78 | 97.67 | 0.69 | 276592 | 2151885.76 | 75676.06 | 2076209.7 | 418 | The Plant was operational on average load of 0.24MW and maximum load of 2.88MW as per available hydrology, | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-11 | 2026 | 1 | 11 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant is shutdown due to box channel repair work. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-11 | 2026 | 1 | 11 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 3 | 100 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual closure. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-11 | 2026 | 1 | 11 | Malakand-3 HPS | 81 | 19 | 17.82 | 427644 | 421590 | 30.23 | 11.97 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1206885.69 | 4358203.11 | 6054 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-11 | 2026 | 1 | 11 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 10.02 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 hrs on date 10-01-2026 as per the notification of the irrigation department for the annual canal closure period of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-11 | 2026 | 1 | 11 | Reshun HPS | 4.2 | 2.96 | 1.46 | 32000 | 31485 | 2 | 1.96 | 65.3 | 13.48 | 66.67 | 45 | 67200 | 905856 | 424417.8 | 481438.2 | 515 | outgoing feeder breaker remained Off 5times for 5.40hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-12 | 2026 | 1 | 12 | Daral Khwar HPS | 36.6 | 2.8 | 2.6 | 62380 | 58780 | 1.5 | 0.98 | 32.67 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 486010.67 | 3145426.69 | 3600 | Unit No 01 was on bar delivering an average load equal to 2.6 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-12 | 2026 | 1 | 12 | Jabori HPS | 10.2 | 2.7 | 2.1 | 44914 | 42960 | 4.73 | 1.47 | 49 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 245267.23 | 1152344.93 | 1954 | Plant was shutdown from 0632 Hrs to 0810 Hrs and from 1701 Hrs to 1912 Hrs due to low hydrology and PTW issued to contractor on cooling water system respectively. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-12 | 2026 | 1 | 12 | Karora HPS | 11.8 | 3.17 | 0.37 | 11602 | 11099 | 2.93 | 0.29 | 9.67 | 7.78 | 97.67 | 0.69 | 276592 | 2151885.76 | 86350.22 | 2065535.54 | 503 | The Plant was operational on average load of 0.37MW and maximum load of 3.17MW as per available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-12 | 2026 | 1 | 12 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remained shut down due to Box Channel repair as requested by the EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-12 | 2026 | 1 | 12 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual closure. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-12 | 2026 | 1 | 12 | Malakand-3 HPS | 81 | 20 | 18.45 | 442878 | 433100 | 30.23 | 12.35 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1239835.37 | 4325253.43 | 9778 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-12 | 2026 | 1 | 12 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 10.02 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 Hrs dated 10-01-2026 as per notification of the irrigation department for annual canal closure period of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-12 | 2026 | 1 | 12 | Reshun HPS | 4.2 | 3.04 | 1.39 | 30000 | 29470 | 2 | 1.86 | 62 | 13.48 | 66.67 | 45 | 67200 | 905856 | 397255.6 | 508600.4 | 530 | outgoing feeder breaker remained Off 5times for 5.30hours due less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-13 | 2026 | 1 | 13 | Daral Khwar HPS | 36.6 | 2.8 | 1.9 | 44440 | 42040 | 1.5 | 0.7 | 23.33 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 347599.33 | 3283838.03 | 2400 | 1. Unit No 01 was on bar delivering an average load equal to 1.9 MW according to available hydrology. 2. At 1023 hrs plant was shutdown under PESCO maintenance schedule NOC. 132 KV supply was cut off at 1025 hrs. 3. 132KV supply was restored at 1638 hrs and unit No 01 was synchronized with the national grid at 164h hrs. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-13 | 2026 | 1 | 13 | Jabori HPS | 10.2 | 2.3 | 1.8 | 30219 | 28610 | 4.73 | 0.99 | 33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 163340.21 | 1234271.95 | 1609 | 1- Plant was shutdown from 0231 Hrs to 0403 Hrs and from 2253 Hrs to 2400 Hrs due to low hydrology. 2- plant was shutdown from 1135 Hrs to 1708 Hrs due to NOC issued to SS & TL Division HAZECO for annual maintenance of Oghi-Battal Transmission line. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-13 | 2026 | 1 | 13 | Karora HPS | 11.8 | 3.17 | 0.61 | 9327 | 8927 | 2.93 | 0.49 | 16.27 | 7.78 | 97.67 | 0.69 | 276592 | 2151885.76 | 69452.06 | 2082433.7 | 400 | the plant was operational delivering power .Max load 3.17MW average load 0.61MW due to low hydrology | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-13 | 2026 | 1 | 13 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant was shut down due to Box channel repair work in progress from EPC contractor side. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-13 | 2026 | 1 | 13 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-13 | 2026 | 1 | 13 | Malakand-3 HPS | 81 | 19 | 17.71 | 425065 | 419990 | 30.23 | 12.17 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1202305.37 | 4362783.43 | 5075 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-13 | 2026 | 1 | 13 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 10.02 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-13 | 2026 | 1 | 13 | Reshun HPS | 4.2 | 3.11 | 1.5 | 32000 | 31464 | 2 | 1.96 | 65.3 | 13.48 | 66.67 | 45 | 67200 | 905856 | 424134.72 | 481721.28 | 536 | outgoing feeder breaker remained Off 5times for 5.26hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-14 | 2026 | 1 | 14 | Daral Khwar HPS | 36.6 | 2.8 | 2.6 | 62710 | 59110 | 1.5 | 0.99 | 33 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 488739.21 | 3142698.15 | 3600 | Unit No 01 was on bar delivering an average load equal to 2.6 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-14 | 2026 | 1 | 14 | Jabori HPS | 10.2 | 2.5 | 2 | 40680 | 38700 | 4.73 | 1.33 | 44.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 220946.04 | 1176666.12 | 1980 | Plant was shutdown from 1159 Hrs to 1334 Hrs and from 2232 Hrs to 2400 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-14 | 2026 | 1 | 14 | Karora HPS | 11.8 | 2.85 | 0.47 | 9052 | 8683 | 2.93 | 0.39 | 13 | 7.78 | 97.67 | 0.69 | 276592 | 2151885.76 | 67553.74 | 2084332.02 | 369 | the plant was operational delivering power max load 2.85MW min load 0MW average load 0.47MW due to low hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-14 | 2026 | 1 | 14 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant was shut down due to box channel repair work in progress from EPC contractor side. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-14 | 2026 | 1 | 14 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Annual Closure | machai.12333@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load; Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2026-01-14 | 2026 | 1 | 14 | Malakand-3 HPS | 81 | 22 | 12.77 | 303913 | 298630 | 30.23 | 13.39 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 854888.1 | 4710200.7 | 5283 | Unit desynchronized from the system at 13:03Hrs to adjust the inlet valve seal of Unit # 03 and cleaning of wicket gates due to debris in the guide vanes of units. Unit synchronized with system at 21:06hrs. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-14 | 2026 | 1 | 14 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 10.02 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-14 | 2026 | 1 | 14 | Reshun HPS | 4.2 | 3.1 | 1.41 | 30000 | 29485 | 2 | 1.86 | 62 | 13.48 | 66.67 | 45 | 67200 | 905856 | 397457.8 | 508398.2 | 515 | Outgoing Feeder Breaker remaind Off 5time for 5.30hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-15 | 2026 | 1 | 15 | Daral Khwar HPS | 36.6 | 2.5 | 2.5 | 59550 | 56350 | 1.5 | 0.94 | 31.33 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 465918.7 | 3165518.66 | 3200 | Unit No 01 was on bar delivering an average load equal to 2.5 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-15 | 2026 | 1 | 15 | Jabori HPS | 10.2 | 2.2 | 2.1 | 43210 | 41280 | 4.73 | 1.41 | 47 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 235675.78 | 1161936.38 | 1930 | Plant was shutdown from 0930 Hrs to 1058 Hrs and from 2003 Hrs to 2133 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-15 | 2026 | 1 | 15 | Karora HPS | 11.8 | 2.84 | 0.35 | 8999 | 8647 | 2.93 | 0.29 | 9.67 | 7.78 | 97.67 | 0.69 | 276592 | 2151885.76 | 67273.66 | 2084612.1 | 352 | the plant was operational on maximum load 2.84MW average load 0.35MW as per available hydrology | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-15 | 2026 | 1 | 15 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant was shut down due to box channel repair work in progress from EPC contractor side. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-15 | 2026 | 1 | 15 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Unit Standby due to Annual canal closure. | machai.12333@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2026-01-15 | 2026 | 1 | 15 | Malakand-3 HPS | 81 | 25 | 23.24 | 557798 | 550620 | 30.23 | 14.88 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1576259.87 | 3988828.93 | 7178 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-15 | 2026 | 1 | 15 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 10.02 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 Hrs dated 10-01-2026 as per the notification of the irrigation department for the annual canal closure period of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-15 | 2026 | 1 | 15 | Reshun HPS | 4.2 | 3.07 | 1.42 | 31000 | 30458 | 2 | 1.9 | 63.23 | 13.48 | 66.67 | 45 | 67200 | 905856 | 410573.84 | 495282.16 | 542 | Outgoing feeder breaker remained Off 5times for 6.15hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-16 | 2026 | 1 | 16 | Daral Khwar HPS | 36.6 | 2.5 | 2.5 | 59820 | 57020 | 1.5 | 0.95 | 31.67 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 471458.47 | 3159978.89 | 2800 | Unit No 01 was on bar delivering an average load equal to 2.5 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-16 | 2026 | 1 | 16 | Jabori HPS | 10.2 | 2.2 | 2 | 43525 | 41550 | 4.73 | 1.42 | 47.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 237217.26 | 1160394.9 | 1975 | Plant was shutdown from 0308 Hrs to 0356 Hrs and from 1303 Hrs to 1424 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-16 | 2026 | 1 | 16 | Karora HPS | 11.8 | 2.86 | 0.47 | 9157 | 8800 | 2.93 | 0.39 | 13 | 7.78 | 97.67 | 0.69 | 276592 | 2151885.76 | 68464 | 2083421.76 | 357 | the plant was operational delivering power maximum load 2.86MW minimum load 0MW average load 0.47MW as per available hydrology | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-16 | 2026 | 1 | 16 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | All units are standby due to repair work in Box Channel. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-16 | 2026 | 1 | 16 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Unit standby due to annual canal closure | machai.12333@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load; Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2026-01-16 | 2026 | 1 | 16 | Malakand-3 HPS | 81 | 25 | 20.44 | 490484 | 483300 | 30.23 | 12.95 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1383542.91 | 4181545.89 | 7184 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-16 | 2026 | 1 | 16 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 10.02 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 Hrs dated 10-01-2026 as per notification of the irrigation department for annual canal closure period of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-16 | 2026 | 1 | 16 | Reshun HPS | 4.2 | 2.84 | 1.45 | 31000 | 30400 | 2 | 1.9 | 63.23 | 13.48 | 66.67 | 45 | 67200 | 905856 | 409792 | 496064 | 600 | Outgoing feeder breaker remained Off 3times for 3.50hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-17 | 2026 | 1 | 17 | Daral Khwar HPS | 36.6 | 2.5 | 2.5 | 60400 | 57200 | 1.5 | 0.96 | 32 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 472946.76 | 3158490.6 | 3200 | Unit No 01 was on bar delivering an average load equal to 2.5 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-17 | 2026 | 1 | 17 | Jabori HPS | 10.2 | 2.2 | 2 | 41239 | 39200 | 4.73 | 1.35 | 45 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 223800.64 | 1173811.52 | 2039 | Plant was shutdown from 0127 Hrs to 0228 Hrs, 1153 Hrs to 1315 Hrs and from 2102 Hrs to 2223 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-17 | 2026 | 1 | 17 | Karora HPS | 11.8 | 2.86 | 0.35 | 8984 | 8629 | 2.93 | 0.29 | 9.67 | 7.78 | 97.67 | 0.69 | 276592 | 2151885.76 | 67133.62 | 2084752.14 | 355 | the was operational delivering power maximum load 2.86MW minimum load 0MW average load 0.35MW as per available hydrology during day. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-17 | 2026 | 1 | 17 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | All units are standby due to repair work in Box Channel. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-17 | 2026 | 1 | 17 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Unit standby due to annual canal closure. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-17 | 2026 | 1 | 17 | Malakand-3 HPS | 81 | 25 | 24.17 | 580182 | 573930 | 30.23 | 15.44 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1642989.41 | 3922099.39 | 6252 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-17 | 2026 | 1 | 17 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 10.02 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 Hrs dated 10-01-2026 as per notification of the irrigation department for annual canal closure period of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-17 | 2026 | 1 | 17 | Reshun HPS | 4.2 | 2.73 | 1.34 | 30000 | 29410 | 2 | 1.86 | 62 | 13.48 | 66.67 | 45 | 67200 | 905856 | 396446.8 | 509409.2 | 590 | outgoing feeder breaker remaind 3times for 4.30hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-18 | 2026 | 1 | 18 | Daral Khwar HPS | 36.6 | 2.5 | 2.3 | 56370 | 53570 | 1.5 | 0.9 | 30 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 442932.83 | 3188504.53 | 2800 | Unit No 01 was on bar delivering an average load equal to 2.3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-18 | 2026 | 1 | 18 | Jabori HPS | 10.2 | 2 | 2 | 42001 | 40160 | 4.73 | 1.37 | 45.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 229281.47 | 1168330.69 | 1841 | Plant was shutdown from 0749 Hrs to 0917 Hrs and from 1830 Hrs to 2008 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-18 | 2026 | 1 | 18 | Karora HPS | 11.8 | 2.86 | 0.35 | 8984 | 8629 | 2.93 | 0.3 | 10 | 7.78 | 97.67 | 0.69 | 276592 | 2151885.76 | 67133.62 | 2084752.14 | 355 | The Unit02 started twice a day till improvement of hydrology on the recommendation of Consultant. Unit 01 is unavailable due to Punch list remaining work | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-18 | 2026 | 1 | 18 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | Plant remain shutdown due to box channel repair works as requested by the EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-18 | 2026 | 1 | 18 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | annual closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-18 | 2026 | 1 | 18 | Malakand-3 HPS | 81 | 25 | 24.61 | 590597 | 584920 | 30.23 | 15.52 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1674450.48 | 3890638.32 | 5677 | As per available hydrology from Irrigation department one Unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-18 | 2026 | 1 | 18 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 10.02 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 Hrs dated 10-01-2026 as per the notification of the irrigation department for the annual canal closure period of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-18 | 2026 | 1 | 18 | Reshun HPS | 4.2 | 2.63 | 1.32 | 31000 | 30404 | 2 | 1.9 | 63.23 | 13.48 | 66.67 | 45 | 67200 | 905856 | 409845.92 | 496010.08 | 596 | outgoing feeder breaker remaind Off 3times for 4.55hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-19 | 2026 | 1 | 19 | Daral Khwar HPS | 36.6 | 2.8 | 2.3 | 26250 | 53050 | 1.5 | 0.89 | 29.67 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 438633.32 | 3192804.04 | 26800 | Unit No 01 was on bar delivering an average load equal to 2.3 MW according to available hydrology. | passion.to.programe@gmail.com | Original | CHECK: Net > Units (source me verify karein) | Link_Generation_Data_Summary.xlsx
2026-01-19 | 2026 | 1 | 19 | Jabori HPS | 10.2 | 2.3 | 1.9 | 42230 | 40320 | 4.73 | 1.38 | 46 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 230194.94 | 1167417.22 | 1910 | Plant was shutdown from 0317 Hrs to 0420 Hrs and from 1410 Hrs to 1550 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-19 | 2026 | 1 | 19 | Karora HPS | 11.8 | 2.92 | 0.48 | 8772 | 8437 | 2.93 | 0.4 | 13.33 | 7.78 | 97.67 | 0.69 | 276592 | 2151885.76 | 65639.86 | 2086245.9 | 335 | Unit#02 was shut down due to low hydrology at 10:34hrs and 19:31hrs and synchronized to the system at 8:59hrs and 17:56hrs respectively. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-19 | 2026 | 1 | 19 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remained shut down due to Box Channel repair as requested by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-19 | 2026 | 1 | 19 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-19 | 2026 | 1 | 19 | Malakand-3 HPS | 81 | 30 | 25.48 | 611631 | 604590 | 30.23 | 17.12 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1730759.79 | 3834329.01 | 7041 | As per available hydrology from Irrigation department one Unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-19 | 2026 | 1 | 19 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 10.02 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 Hrs dated 10-01-2026 as per notification of the irrigation department for annual canal closure period of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-19 | 2026 | 1 | 19 | Reshun HPS | 4.2 | 2.84 | 1.17 | 28000 | 27420 | 2 | 1.71 | 57 | 13.48 | 66.67 | 45 | 67200 | 905856 | 369621.6 | 536234.4 | 580 | outgoing feeder breaker remained off 3times for 3.50house due to less hydrology. | zafar.src@gmail.com | Original | Avg load = Units / 24h | Link_Generation_Data_Summary.xlsx
2026-01-20 | 2026 | 1 | 20 | Daral Khwar HPS | 36.6 | 2.5 | 2.5 | 59630 | 56430 | 1.5 | 0.94 | 31.33 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 466580.17 | 3164857.19 | 3200 | Unit No 01 was on bar delivering an average load equal to 2.5 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-20 | 2026 | 1 | 20 | Jabori HPS | 10.2 | 2.4 | 2 | 40706 | 38800 | 4.73 | 1.33 | 44.33 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 221516.96 | 1176095.2 | 1906 | Plant was shutdown from 0202 Hrs to 0404 Hrs and from 1830 Hrs to 2015 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-20 | 2026 | 1 | 20 | Karora HPS | 11.8 | 2.86 | 0.47 | 11016 | 10563 | 2.93 | 0.39 | 13 | 7.78 | 97.67 | 0.69 | 276592 | 2151885.76 | 82180.14 | 2069705.62 | 453 | unit#01 shutdown state as per EPC contractor instructions. And unit#02 was shutdown due to low hydrology at 10:42Hrs and 19:46Hrs and synchronized to the system at 08:33Hrs and 17:57Hrs respectively. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-20 | 2026 | 1 | 20 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | Plant remain shutdown down due to box channel repair works as requested by the EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-20 | 2026 | 1 | 20 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-20 | 2026 | 1 | 20 | Malakand-3 HPS | 81 | 25 | 8.49 | 203801 | 201560 | 30.23 | 6.88 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 577005.81 | 4988082.99 | 2241 | Water has been diverted by irrigation department as per letter CW No. 02. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-20 | 2026 | 1 | 20 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 10.02 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 Hrs dated 10-01-2026 as per notification of the irrigation department for annual canal closure period of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-20 | 2026 | 1 | 20 | Reshun HPS | 4.2 | 2.99 | 1.4 | 31000 | 30400 | 2 | 1.9 | 63.23 | 13.48 | 66.67 | 45 | 67200 | 905856 | 409792 | 496064 | 600 | outgoing feeder breaker remained Off 3times for 4.55hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-21 | 2026 | 1 | 21 | Daral Khwar HPS | 36.6 | 2.5 | 2.3 | 54010 | 50810 | 1.5 | 0.85 | 28.33 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 420112.32 | 3211325.04 | 3200 | 1. Unit No 01 was on bar delivering an average load equal to 2.3 MW according to available hydrology. 2. Unit No 01 tripped at 0507 Hrs due to high thrust bearing pad No.02 temperature and was synchronized at 0540Hrs. The unit tripped again at 0602 Hrs and was resynchronized at 0753 Hrs. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-21 | 2026 | 1 | 21 | Jabori HPS | 10.2 | 2.2 | 2 | 39473 | 37530 | 4.73 | 1.29 | 43 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 214266.28 | 1183345.88 | 1943 | Plant was shutdown from 0301Hrs to 0415Hrs, 1355 Hrs to 1550 Hrs and from 2200 to 2245 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-21 | 2026 | 1 | 21 | Karora HPS | 11.8 | 2.87 | 0.47 | 9423 | 9033 | 3.33 | 0.39 | 13 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 70276.74 | 2133019.26 | 390 | unit#01 shutdown state as per PEC contractor instructions. And unit#02 was shutdown due to low hydrology at 10:15Hrs and 19:37Hrs and synchronized to the system at 08:30Hrs and 17:59Hrs respectively. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-21 | 2026 | 1 | 21 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | Plant remain shutdown due to Box Channel repairs works as requested by the EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-21 | 2026 | 1 | 21 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Canal Closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-21 | 2026 | 1 | 21 | Malakand-3 HPS | 81 | 27 | 10.07 | 241560 | 238750 | 30.23 | 6.59 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 683469.62 | 4881619.18 | 2810 | Unit # 01 synchronized with the system at 14:46Hrs dated 21-01-2026. As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-21 | 2026 | 1 | 21 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 10.02 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-21 | 2026 | 1 | 21 | Reshun HPS | 4.2 | 2.94 | 1.38 | 28000 | 27430 | 2 | 1.71 | 57 | 13.48 | 66.67 | 45 | 67200 | 905856 | 369756.4 | 536099.6 | 570 | Outgoing Feeder Breaker remaind Off 3times for 5.10hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-22 | 2026 | 1 | 22 | Daral Khwar HPS | 36.6 | 2.5 | 2.4 | 57380 | 54180 | 1.5 | 0.91 | 30.33 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 447976.49 | 3183460.87 | 3200 | Unit No 01 was on bar delivering an average load equal to 2.4 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-22 | 2026 | 1 | 22 | Jabori HPS | 10.2 | 2.2 | 1.8 | 40139 | 38150 | 4.73 | 1.31 | 43.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 217805.98 | 1179806.18 | 1989 | Plant was shutdown from 0815 Hrs to 0955 Hrs and from 1905 Hrs to 2030 Hrs due to low hydrology. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-22 | 2026 | 1 | 22 | Karora HPS | 11.8 | 2.89 | 0.48 | 8976 | 8551 | 3.33 | 0.4 | 13.33 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 66526.78 | 2136769.22 | 425 | unit#01 remain in ashutdown state after updating governor setting and it has not yet been properly tested.The EPC contractor representative instructed that unit#01 shall not be started till further order. Unit#02 was shutdown due to low hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-22 | 2026 | 1 | 22 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remained shutdown due to Box Channel repair works, as requested by the EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-22 | 2026 | 1 | 22 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-22 | 2026 | 1 | 22 | Malakand-3 HPS | 81 | 27 | 26.08 | 625875 | 618410 | 30.23 | 16.32 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1770322.31 | 3794766.49 | 7465 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-22 | 2026 | 1 | 22 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 10.02 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 dated 10/01/2026 due to the annual canal closure period. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-22 | 2026 | 1 | 22 | Reshun HPS | 4.2 | 2.9 | 1.29 | 31000 | 30400 | 2 | 1.9 | 63.23 | 13.48 | 66.67 | 45 | 67200 | 905856 | 409792 | 496064 | 600 | outgoing feeder breaker remaind 3times for 5.10hours due to less hydrology. | zafar.src@gmail.com | Original | Avg load = Units / 24h | Link_Generation_Data_Summary.xlsx
2026-01-23 | 2026 | 1 | 23 | Daral Khwar HPS | 36.6 | 2.5 | 1.4 | 33410 | 30210 | 1.5 | 0.51 | 17 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 249785.34 | 3381652.02 | 3200 | Unit No 01 was on bar delivering an average load equal to 1.4 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-23 | 2026 | 1 | 23 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7092 | 0 | 79.57 | 0 | 0 | 0 | 0 | 0 | The power house is shut down as an evacuation of power is not possible following the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-23 | 2026 | 1 | 23 | Karora HPS | 11.8 | 3.01 | 0.96 | 24432 | 23377 | 3.33 | 0.79 | 26.33 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 181873.06 | 2021422.94 | 1055 | the plant was operational on average load 0.96MW and a max load 3.01MW as per hydrology and unit#01 shutdown state on the instruction of EPC contractor. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-23 | 2026 | 1 | 23 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remained shut down due to Box Channel repair works, as requested by the EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-23 | 2026 | 1 | 23 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-23 | 2026 | 1 | 23 | Malakand-3 HPS | 81 | 42 | 32.11 | 770709 | 762140 | 30.23 | 21.67 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2181778.18 | 3383310.62 | 8569 | Unit #02 was synchronized with the system at 11:36 hrs on 23-01-2026 due to an increase in hydrology. As per the available hydrology reported by the Irrigation Department, two units are currently on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-23 | 2026 | 1 | 23 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 10.02 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-23 | 2026 | 1 | 23 | Reshun HPS | 4.2 | 1.6 | 0.43 | 10000 | 9470 | 2 | 0.61 | 20.4 | 13.48 | 66.67 | 45 | 67200 | 905856 | 127655.6 | 778200.4 | 530 | the outgoing feeder breaker remained Off due to heavy snowfall. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-24 | 2026 | 1 | 24 | Daral Khwar HPS | 36.6 | 3.5 | 2.2 | 53240 | 50040 | 1.5 | 0.84 | 28 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 413745.73 | 3217691.63 | 3200 | Unit No 01 was on bar delivering an average load equal to 2.2 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-24 | 2026 | 1 | 24 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is shut down as an evacuation of power is not possible following the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2026-01-24 | 2026 | 1 | 24 | Karora HPS | 11.8 | 3.01 | 0.96 | 24432 | 23377 | 3.33 | 0.78 | 26 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 181873.06 | 2021422.94 | 1055 | unit#2 was started twice at 05:28 hrs and 15:35 hrs to system and shutdown at 09:59 and 19:16 due to low hydrology | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-24 | 2026 | 1 | 24 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remained shut down due to Box Channel repair works, as requested by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-24 | 2026 | 1 | 24 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual closure. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-24 | 2026 | 1 | 24 | Malakand-3 HPS | 81 | 50 | 38.24 | 917732 | 909660 | 30.23 | 28.71 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2604083.68 | 2961005.12 | 8072 | Unit #01 and Unit 02: 05:56 hrs tripped on 132 kV supply failure; Unit #01 and Unit #02 synchronized with the system at 07:29 hrs and 07:23 hrs; 16:39 hrs tripped on voltage and frequency fluctuation; Unit #01 and Unit #02 synchronized with the system at 17:12 hrs and 17:11 hrs ,As per available hydrology from the Irrigation Department two unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-24 | 2026 | 1 | 24 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 10.02 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-24 | 2026 | 1 | 24 | Reshun HPS | 4.2 | 2.2 | 1.35 | 30000 | 29410 | 2 | 2.86 | 95.33 | 13.48 | 66.67 | 45 | 67200 | 905856 | 396446.8 | 509409.2 | 590 | outgoing feeder breaker remained Off due to Snowfall and less less hydrology for 2.10hours. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-25 | 2026 | 1 | 25 | Daral Khwar HPS | 36.6 | 4.3 | 3.7 | 87980 | 84780 | 1.5 | 1.42 | 47.33 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 700986.47 | 2930450.89 | 3200 | Unit No 01 was on bar delivering an average load equal to 3.7 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-25 | 2026 | 1 | 25 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7092 | 0 | 79.57 | 0 | 0 | 0 | 0 | 0 | The power house is still shut down due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-25 | 2026 | 1 | 25 | Karora HPS | 11.8 | 2.87 | 0.59 | 16301 | 15564 | 3.33 | 0.49 | 16.4 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 121087.92 | 2082208.08 | 737 | the plant was operational on average load 0.59MW and maximum load 2.87MW as per hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-25 | 2026 | 1 | 25 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant was shut down due to box channel repair work in progress from EPC contractor side. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-25 | 2026 | 1 | 25 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual closure. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-25 | 2026 | 1 | 25 | Malakand-3 HPS | 81 | 47 | 37.94 | 910580 | 902750 | 30.23 | 29.42 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2584302.42 | 2980786.38 | 7830 | Unit # 01 & 02 tripped at 06:04, 19:55, 20:39, & 23:09Hrs due to unstable system frequency and voltage, which were continuously fluctuating up and down, informed RCC. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-25 | 2026 | 1 | 25 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 10.02 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 Hrs dated 10-01-2026 as per notification of the irrigation department for annual canal closure period of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-25 | 2026 | 1 | 25 | Reshun HPS | 4.2 | 2.62 | 1.41 | 29000 | 28420 | 2 | 1.77 | 59 | 13.48 | 66.67 | 45 | 67200 | 905856 | 383101.6 | 522754.4 | 580 | outgoing feeder breaker remained Off 4times for 8.25hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-26 | 2026 | 1 | 26 | Daral Khwar HPS | 36.6 | 4 | 3.5 | 83440 | 79840 | 1.5 | 1.34 | 44.67 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 660141.07 | 2971296.29 | 3600 | Unit No 01 was on bar delivering an average load equal to 3.5 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-26 | 2026 | 1 | 26 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7092 | 0 | 79.57 | 0 | 0 | 0 | 0 | 0 | The power house is still shut down due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-26 | 2026 | 1 | 26 | Karora HPS | 11.8 | 2.92 | 0.71 | 15181 | 14517 | 3.33 | 0.58 | 19.33 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 112942.26 | 2090353.74 | 664 | The plant was operational on average load 0.71 MW and maximum load 2.92MW as per available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-26 | 2026 | 1 | 26 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | the plant was shutdown due to box channel repair work in progress from EPC contractor | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-26 | 2026 | 1 | 26 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual closure. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-26 | 2026 | 1 | 26 | Malakand-3 HPS | 81 | 46 | 38.8 | 931186 | 922590 | 30.23 | 28.77 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2641098.39 | 2923990.41 | 8596 | Unit # 01 & 02 tripped at 06:18Hrs, 07:27Hrs, 10:16Hrs, 20:48Hrs, & 21:12Hrs due to unstable system frequency and voltage, which were continuously fluctuating up and down, informed RCC. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-26 | 2026 | 1 | 26 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 10.02 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 Hrs dated 10-01-2026 as per notification of the irrigation department for annual canal closure period of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-26 | 2026 | 1 | 26 | Reshun HPS | 4.2 | 3.15 | 1.5 | 29000 | 28423 | 2 | 1.77 | 59 | 13.48 | 66.67 | 45 | 67200 | 905856 | 383142.04 | 522713.96 | 577 | outgoing feeder breaker remained Off 6times for 8.12hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-27 | 2026 | 1 | 27 | Daral Khwar HPS | 36.6 | 3.5 | 3.2 | 76220 | 73020 | 1.5 | 1.22 | 40.67 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 603751.27 | 3027686.09 | 3200 | Unit No 01 was on bar delivering an average load equal to 3.2 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-27 | 2026 | 1 | 27 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7092 | 0 | 79.57 | 0 | 0 | 0 | 0 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026 | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-27 | 2026 | 1 | 27 | Karora HPS | 11.8 | 3.01 | 1.55 | 34989 | 33484 | 3.33 | 1.27 | 42.33 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 260505.52 | 1942790.48 | 1505 | The plant was operational on average load 1.55mw and maximum load 3.01mw as per available hydrology. Both unit are remain shutdown due to low hydrology from 21:13Hrs 27-01-2026 | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-27 | 2026 | 1 | 27 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant was shut down due to Box channel repair work in progress from EPC contractor side. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-27 | 2026 | 1 | 27 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual closure. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-27 | 2026 | 1 | 27 | Malakand-3 HPS | 81 | 45 | 37.36 | 896558 | 887650 | 30.23 | 26.32 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2541075.65 | 3024013.14 | 8908 | Unit # 01 & 02 tripped at 10:42Hrs, 21:05Hrs & 21:39Hrs due to unstable system frequency and voltage, which were continuously fluctuating up and down, informed RCC. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-27 | 2026 | 1 | 27 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 10.02 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 Hrs dated 10-01-2026 as per notification of the irrigation department for annual canal closure period of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-27 | 2026 | 1 | 27 | Reshun HPS | 4.2 | 3.06 | 1.33 | 29000 | 28431 | 2 | 1.77 | 59 | 13.48 | 66.67 | 45 | 67200 | 905856 | 383249.88 | 522606.12 | 569 | outgoing feeder breaker remained Off 6times for 10.10hours due less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-28 | 2026 | 1 | 28 | Daral Khwar HPS | 36.6 | 3 | 3 | 71840 | 68640 | 1.5 | 1.15 | 38.33 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 567536.11 | 3063901.25 | 3200 | Unit No 01 was on bar delivering an average load equal to 3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-28 | 2026 | 1 | 28 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7092 | 0 | 79.57 | 0 | 0 | 0 | 0 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-28 | 2026 | 1 | 28 | Karora HPS | 11.8 | 2.86 | 1.18 | 24272 | 23193 | 3.33 | 0.97 | 32.33 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 180441.54 | 2022854.46 | 1079 | The plant was operational on average load 1.18MW and maximum load 2.86MW as per available hydrology. Both unit are remain shutdown due to low hydrology from 22:02 hrs.28-01-2026 | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-28 | 2026 | 1 | 28 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | All units are standby due to repair work in Box Channel | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-28 | 2026 | 1 | 28 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-28 | 2026 | 1 | 28 | Malakand-3 HPS | 81 | 44 | 36.23 | 869605 | 861160 | 30.23 | 26.86 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2465242.73 | 3099846.07 | 8445 | As per available hydrology from the Irrigation Department Two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-28 | 2026 | 1 | 28 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 10.02 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 Hrs dated 10-01-2026 as per notification of the irrigation department for annual canal closure period of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-28 | 2026 | 1 | 28 | Reshun HPS | 4.2 | 3.08 | 1.26 | 30000 | 29428 | 2 | 1.86 | 62 | 13.48 | 66.67 | 45 | 67200 | 905856 | 396689.44 | 509166.56 | 572 | Outgoing feeder breaker remained off 4times for 5.10hours due less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-29 | 2026 | 1 | 29 | Daral Khwar HPS | 36.6 | 3 | 2.1 | 50780 | 48380 | 1.5 | 0.81 | 27 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 400020.35 | 3231417.01 | 2400 | 1. Unit No 01 was on bar delivering an average load equal to 2.1 MW according to available hydrology. 2. 132KV line tripped at 1238 hrs, during shutdown the broken shield wire of 132KV transmission line at Mina Sheikh Baba Madyan area was repaired and restored. 3. The work was initially suspended by the local land owner, however successfully executed after negotiation. 4. 132KV transmission line restored at 19:30 Hrs and Unit No 01 was synchronized with the national grid at 19:43 Hrs. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-29 | 2026 | 1 | 29 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7092 | 0 | 79.57 | 0 | 0 | 0 | 0 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-29 | 2026 | 1 | 29 | Karora HPS | 11.8 | 2.89 | 0.83 | 18909 | 17803 | 2.93 | 0.69 | 22.93 | 7.78 | 97.67 | 0.69 | 276592 | 2151885.76 | 138507.34 | 2013378.42 | 1106 | Plant was operational with Max load of 2.89MW and average load of 0.83MW as per available hydrology | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-29 | 2026 | 1 | 29 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | All units are standby due to repair work in Box Channel | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-29 | 2026 | 1 | 29 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | unit stand still due to annual canal closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-29 | 2026 | 1 | 29 | Malakand-3 HPS | 81 | 46 | 39.51 | 948331 | 939930 | 30.23 | 27.35 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2690737.61 | 2874351.19 | 8401 | As per available Hydrology from Irrigation department two Units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-29 | 2026 | 1 | 29 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 10.02 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 Hrs dated 10-01-2026 as per notification of the irrigation department for annual canal closure period of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-29 | 2026 | 1 | 29 | Reshun HPS | 4.2 | 3.09 | 1.17 | 29000 | 28420 | 2 | 1.77 | 59 | 13.48 | 66.67 | 45 | 67200 | 905856 | 383101.6 | 522754.4 | 580 | Outgoing feeder breaker remained off 5times for 6.50hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-30 | 2026 | 1 | 30 | Daral Khwar HPS | 36.6 | 3 | 2.9 | 70720 | 67920 | 1.5 | 1.14 | 38 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 561582.94 | 3069854.42 | 2800 | Unit No 01 was on bar delivering an average load equal to 2.9 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-30 | 2026 | 1 | 30 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7092 | 0 | 79.57 | 0 | 0 | 0 | 0 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-30 | 2026 | 1 | 30 | Karora HPS | 11.8 | 2 | 1.07 | 25530 | 24254 | 3.33 | 0.89 | 29.57 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 188696.12 | 2014599.88 | 1276 | Plant was operational with max and avg generation of 2.90MW and 1.07MW | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-30 | 2026 | 1 | 30 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | Plant remain shutdown due to box channel repair work as requested by the EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-30 | 2026 | 1 | 30 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | unit standstill due to annual canal closure | machai.12333@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load; Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2026-01-30 | 2026 | 1 | 30 | Malakand-3 HPS | 81 | 45 | 42.6 | 1022490 | 1013910 | 30.23 | 28.33 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2902520.16 | 2662568.64 | 8580 | As per available hydrology from the Irrigation Department Two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-30 | 2026 | 1 | 30 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 10.02 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained completely shut down due to the annual canal closure period of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-30 | 2026 | 1 | 30 | Reshun HPS | 4.2 | 3.05 | 1.18 | 29000 | 28430 | 2 | 1.77 | 59 | 13.48 | 66.67 | 45 | 67200 | 905856 | 383236.4 | 522619.6 | 570 | Outgoing feeder breaker remained off 6times for 5.35hours due less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-31 | 2026 | 1 | 31 | Daral Khwar HPS | 36.6 | 3 | 3 | 70940 | 68140 | 1.5 | 1.14 | 38 | 8.2683 | 50 | 48 | 439200 | 3631437.36 | 563401.96 | 3068035.4 | 2800 | Unit No 01 was on bar delivering an average load equal to 3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-31 | 2026 | 1 | 31 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7092 | 0 | 79.57 | 0 | 0 | 0 | 0 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-31 | 2026 | 1 | 31 | Karora HPS | 11.8 | 2.89 | 1.31 | 30135 | 28859 | 3.33 | 1.03 | 34.33 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 224523.02 | 1978772.98 | 1276 | the plant was operational on average load of 1.31mw and maximum load of 2.89mw is per available hydrology | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-31 | 2026 | 1 | 31 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remained shut down for Box Channel repair works by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-31 | 2026 | 1 | 31 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Unit stand still due to annual canal closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-31 | 2026 | 1 | 31 | Malakand-3 HPS | 81 | 44 | 41.6 | 998335 | 990120 | 25.72 | 27.89 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2834416.52 | 2730672.28 | 8215 | As per available hydrology from the Irrigation Department Two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-31 | 2026 | 1 | 31 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 10.02 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down due to the annual canal closure period. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-01-31 | 2026 | 1 | 31 | Reshun HPS | 4.2 | 2.94 | 1.22 | 28000 | 27419 | 2 | 1.71 | 57.13 | 13.48 | 66.67 | 45 | 67200 | 905856 | 369608.12 | 536247.88 | 581 | Outgoing feder breaker remained Off 5times for 5.20hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-01 | 2026 | 2 | 1 | Daral Khwar HPS | 36.6 | 3 | 3 | 71280 | 68080 | 1.85 | 1.14 | 38 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 562905.86 | 3915866.88 | 3200 | Unit No 01 was on bar delivering an average load equal to 3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-01 | 2026 | 2 | 1 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7092 | 0 | 79.57 | 0 | 0 | 0 | 0 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-01 | 2026 | 2 | 1 | Karora HPS | 11.8 | 2.91 | 1.32 | 33343 | 32098 | 4.23 | 6.87 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 249722.44 | 1953573.56 | 1245 | the plant was operational on average load of 1.32mw and maximum load of 2.91mw as per available hydrology | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-01 | 2026 | 2 | 1 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 14.6 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The Plant remained shut down due to Box Channel repair works by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-01 | 2026 | 2 | 1 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Unit stand still due to yearly canals closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-01 | 2026 | 2 | 1 | Malakand-3 HPS | 81 | 44 | 40.88 | 981213 | 973290 | 25.72 | 27.51 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2786237.28 | 2778851.52 | 7923 | As per available hydrology from irrigation department two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-01 | 2026 | 2 | 1 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 18.83 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 Hrs dated 10-01-2026 as per notification of the irrigation department for annual canal closure period of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-01 | 2026 | 2 | 1 | Reshun HPS | 4.2 | 2.98 | 1.22 | 29000 | 28433 | 1.99 | 1.77 | 59 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 383276.84 | 518049.88 | 567 | Outgoing feeder breaker remained off 4times fro5.55hours due less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-02 | 2026 | 2 | 2 | Daral Khwar HPS | 36.6 | 3 | 3 | 70900 | 68100 | 1.85 | 1.14 | 38 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 563071.23 | 3915701.51 | 2800 | Unit No 01 was on bar delivering an average load equal to 3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-02 | 2026 | 2 | 2 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7092 | 0 | 79.57 | 0 | 0 | 0 | 0 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-02 | 2026 | 2 | 2 | Karora HPS | 11.8 | 2.91 | 0.72 | 17312 | 16663 | 4.23 | 0.59 | 19.67 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 129638.14 | 2073657.86 | 649 | the plant was operational on average load of 0.72mw and maximum load of 2.91mw as per available hydrology | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-02 | 2026 | 2 | 2 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 14.6 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remained shut down due to Box Channel repair by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-02 | 2026 | 2 | 2 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-02 | 2026 | 2 | 2 | Malakand-3 HPS | 81 | 42 | 39.52 | 948587 | 940190 | 25.72 | 26.69 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2691481.91 | 2873606.89 | 8397 | As per available hydrology from irrigation department two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-02 | 2026 | 2 | 2 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 18.83 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 Hrs dated 10-01-2026 as per the notification of the irrigation department for the annual canal closure period of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-02 | 2026 | 2 | 2 | Reshun HPS | 4.2 | 3.16 | 1.17 | 29000 | 28437 | 1.99 | 1.77 | 59 | 13.48 | 66.37 | 45 | 66897.6 | 901779.65 | 383330.76 | 518448.89 | 563 | Outgoing feeder breaker remained Off 4times for 6.30hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-03 | 2026 | 2 | 3 | Daral Khwar HPS | 36.6 | 3 | 3 | 71290 | 68090 | 1.85 | 1.14 | 38 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 562988.55 | 3915784.2 | 3200 | Unit No 01 was on bar delivering an average load equal to 3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-03 | 2026 | 2 | 3 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7092 | 0 | 79.57 | 0 | 0 | 0 | 0 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-03 | 2026 | 2 | 3 | Karora HPS | 11.8 | 2.87 | 0.83 | 20033 | 19273 | 4.23 | 0.68 | 22.67 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 149943.94 | 2053352.06 | 760 | Unit#02 synchronized with the system at 10:17hrs and 16:17hrs , accordingly was shutdown at 2:03hrs and 19:41hrs . | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-03 | 2026 | 2 | 3 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 14.6 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remained shut down due to Box Channel repair by EPC Contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-03 | 2026 | 2 | 3 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-03 | 2026 | 2 | 3 | Malakand-3 HPS | 81 | 41 | 37.66 | 903830 | 895640 | 25.72 | 25.79 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2563948.63 | 3001140.17 | 8190 | As per available hydrology from the Irrigation Department Two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-03 | 2026 | 2 | 3 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 18.83 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 Hrs dated 10-01-2026 as per notification of the irrigation department for annual canal closure period of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-03 | 2026 | 2 | 3 | Reshun HPS | 4.2 | 3.23 | 1.27 | 26000 | 25438 | 1.99 | 1.59 | 53.03 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 342904.24 | 558422.48 | 562 | Outgoing feeder breaker remained off 6times for 7.55hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-04 | 2026 | 2 | 4 | Daral Khwar HPS | 36.6 | 3 | 2.8 | 68230 | 64630 | 1.85 | 1.08 | 36 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 534380.23 | 3944392.52 | 3600 | Unit No 01 was on bar delivering an average load equal to 2.8 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-04 | 2026 | 2 | 4 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7092 | 0 | 79.57 | 0 | 0 | 0 | 0 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-04 | 2026 | 2 | 4 | Karora HPS | 11.8 | 2.94 | 0.83 | 19441 | 18730 | 4.23 | 0.69 | 23 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 145719.4 | 2057576.6 | 711 | Unit#02 synchronized with the system at 11:58hrs and 17:33hrs, accordingly was shutdown at 15:34hrs and 20:52hrs. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-04 | 2026 | 2 | 4 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 14.6 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The Plant remained shut down due to Box Channel repair works by EPC Contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-04 | 2026 | 2 | 4 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-04 | 2026 | 2 | 4 | Malakand-3 HPS | 81 | 39 | 37.34 | 896206 | 888170 | 25.72 | 25.76 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2542564.26 | 3022524.54 | 8036 | As per available hydrology from the Irrigation Department Two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-04 | 2026 | 2 | 4 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 10.02 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 on 10-01-2026 due to the annual canal closure period. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-04 | 2026 | 2 | 4 | Reshun HPS | 4.2 | 3.11 | 1.2 | 27000 | 26430 | 1.99 | 1.77 | 59 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 356276.4 | 545050.32 | 570 | Outgoing feeder breaker remained Off 5times for 5.5o hours for the storage of Water in Reservoir. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-05 | 2026 | 2 | 5 | Daral Khwar HPS | 36.6 | 3 | 2.8 | 67160 | 64360 | 1.85 | 1.08 | 36 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 532147.79 | 3946624.96 | 2800 | Unit No 01 was on bar delivering an average load equal to 2.8 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-05 | 2026 | 2 | 5 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7092 | 0 | 79.57 | 0 | 0 | 0 | 0 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-05 | 2026 | 2 | 5 | Karora HPS | 11.8 | 2.86 | 0.94 | 19579 | 18730 | 4.23 | 0.78 | 26 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 145719.4 | 2057576.6 | 849 | Unit#02 synchronized with the grid at 09:07hrs and 15:49hrs, accordingly was shutdown at 13:47hrs and 19:39hrs. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-05 | 2026 | 2 | 5 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 14.46 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | All operating units are shutdown due to box channel repair from 10th Dec 2025 | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-05 | 2026 | 2 | 5 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-05 | 2026 | 2 | 5 | Malakand-3 HPS | 81 | 38 | 36.88 | 885003 | 877460 | 25.72 | 25.62 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2511904.74 | 3053184.06 | 7543 | As per available hydrology from the Irrigation Department Two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-05 | 2026 | 2 | 5 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 18.83 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 Hrs dated 10-01-2026 as per notification of the irrigation department for annual canal closure period of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-05 | 2026 | 2 | 5 | Reshun HPS | 4.2 | 2.95 | 1.18 | 27000 | 26445 | 1.99 | 1.59 | 53 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 356478.6 | 544848.12 | 555 | Outgoing feeder breaker remained Off 5times for 5.5hours due less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-06 | 2026 | 2 | 6 | Daral Khwar HPS | 36.6 | 3.4 | 2.9 | 70540 | 66940 | 1.85 | 1.12 | 37.33 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 553480 | 3925292.74 | 3600 | Unit No 01 was on bar delivering an average load equal to 2.9 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-06 | 2026 | 2 | 6 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7092 | 0 | 79.57 | 0 | 0 | 0 | 0 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-06 | 2026 | 2 | 6 | Karora HPS | 11.8 | 2.86 | 0.94 | 35149 | 33805 | 4.23 | 0.78 | 26 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 263002.9 | 1940293.1 | 1344 | Unit#02 synchronized with the system at 08:05hrs ,10:45hrs and 15:54hrs , accordingly was shutdown at 9:54hrs , 12:25hrs and 0:00hrs | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-06 | 2026 | 2 | 6 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant was shut down due to box channel repair work in progress from EPC contractor side. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-06 | 2026 | 2 | 6 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-06 | 2026 | 2 | 6 | Malakand-3 HPS | 81 | 39 | 36.82 | 883745 | 875810 | 25.72 | 25.52 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2507181.29 | 3057907.51 | 7935 | As per available hydrology from the Irrigation Department Two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-06 | 2026 | 2 | 6 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 18.83 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 Hrs dated 10-01-2026 as per notification of the irrigation department for annual canal closure period of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-06 | 2026 | 2 | 6 | Reshun HPS | 4.2 | 3.1 | 1.16 | 27000 | 26434 | 1.99 | 1.77 | 59 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 356330.32 | 544996.4 | 566 | Outgoing feeder breaker remained Off 6times for 7.20hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-07 | 2026 | 2 | 7 | Daral Khwar HPS | 36.6 | 3 | 2.9 | 69640 | 66840 | 1.85 | 1.12 | 37.33 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 552653.17 | 3926119.57 | 2800 | Unit No 01 was on bar delivering an average load equal to 2.9 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-07 | 2026 | 2 | 7 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7092 | 0 | 79.57 | 0 | 0 | 0 | 0 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-07 | 2026 | 2 | 7 | Karora HPS | 11.8 | 3.5 | 2.43 | 58974 | 56867 | 4.23 | 1.99 | 66.33 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 442425.26 | 1760870.74 | 2107 | The unit 02 was synchronized with the system at 11:17 hrs and 18:08 hrs,and shutdown at 10:00 hrs and 15:41 hrs, respectively. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-07 | 2026 | 2 | 7 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant was shut down due to box channel repair work in progress from EPC contractor side. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-07 | 2026 | 2 | 7 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Closure. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-07 | 2026 | 2 | 7 | Malakand-3 HPS | 81 | 44 | 40.19 | 964599 | 957300 | 25.72 | 27.47 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2740462.71 | 2824626.09 | 7299 | As per available hydrology from the Irrigation Department Two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-07 | 2026 | 2 | 7 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 18.83 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 Hrs dated 10-01-2026 as per notification of the irrigation department for annual canal closure period of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-07 | 2026 | 2 | 7 | Reshun HPS | 4.2 | 2.95 | 1.16 | 26000 | 25475 | 1.99 | 1.59 | 53 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 343403 | 557923.72 | 525 | Outgoing Feeder Breaker remained Off 6times for 5.40hours for load Shedding due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-08 | 2026 | 2 | 8 | Daral Khwar HPS | 36.6 | 3 | 2.9 | 70180 | 67380 | 1.85 | 1.13 | 37.67 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 557118.05 | 3921654.69 | 2800 | Unit No 01 was on bar delivering an average load equal to 2.9 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-08 | 2026 | 2 | 8 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7092 | 0 | 79.57 | 0 | 0 | 0 | 0 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Timeline for completion work has not been provided by PD/contractor. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-08 | 2026 | 2 | 8 | Karora HPS | 11.8 | 2.99 | 2.27 | 55967 | 53964 | 4.23 | 1.87 | 62.33 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 419839.92 | 1783456.08 | 2003 | Unit 02 synchronized with the system at 7:06hrs and 18:02hrs, accordingly was shutdown at 5:30hrs and 15:27hrs. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-08 | 2026 | 2 | 8 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant was shut down due to box channel repair work in progress from EPC contractor side. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-08 | 2026 | 2 | 8 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Closure till 10th February, 2026. (Extendable up to 20th Feb 2026) | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-08 | 2026 | 2 | 8 | Malakand-3 HPS | 81 | 43 | 39.14 | 939360 | 932020 | 25.72 | 26.87 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2668093.65 | 2896995.15 | 7340 | As per available hydrology from the Irrigation Department Two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-08 | 2026 | 2 | 8 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 18.83 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 Hrs dated 10-01-2026 as per notification of the irrigation department for annual canal closure period till 10th February, 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-08 | 2026 | 2 | 8 | Reshun HPS | 4.2 | 3 | 1.17 | 28000 | 27435 | 1.99 | 1.71 | 57 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 369823.8 | 531502.92 | 565 | Outgoing feeder breaker remained Off 6times for 5.05hours for loadshedding. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-09 | 2026 | 2 | 9 | Daral Khwar HPS | 36.6 | 3.3 | 3.1 | 73990 | 70790 | 1.85 | 1.18 | 39.33 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 585312.96 | 3893459.79 | 3200 | Unit No 01 was on bar delivering an average load equal to 3.1 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-09 | 2026 | 2 | 9 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2026-02-09 | 2026 | 2 | 9 | Karora HPS | 11.8 | 3 | 2.73 | 63716 | 61416 | 4.23 | 2.26 | 75.33 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 477816.48 | 1725479.52 | 2300 | unit 02 was synchronized with grid at 13:37hrs, accordingly was shutdown at 12:16hrs. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-09 | 2026 | 2 | 9 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 14.6 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | All units are standby due to repair work in Box Channel. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-09 | 2026 | 2 | 9 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Closure till 10th February, 2026. (Extendable up to 20th Feb 2026) | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-09 | 2026 | 2 | 9 | Malakand-3 HPS | 81 | 40 | 38.03 | 912824 | 905140 | 25.72 | 26.4 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2591144.28 | 2973944.52 | 7684 | As per available hydrology from the Irrigation Department Two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-09 | 2026 | 2 | 9 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 18.83 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 Hrs dated 10-01-2026 as per notification of the irrigation department for annual canal closure period of 2026.i.e. (10th February, 2026) | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-09 | 2026 | 2 | 9 | Reshun HPS | 4.2 | 2.88 | 1.13 | 24000 | 23490 | 1.99 | 1.57 | 52.3 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 316645.2 | 584681.52 | 510 | 1. Outgoing Feeder breaker remained Off 6times for 7.30hours for load Shedding. 2. due to fault occurred in Unit No. 3 the Mastuj section remained Off. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-10 | 2026 | 2 | 10 | Daral Khwar HPS | 36.6 | 3.3 | 3.2 | 76940 | 74140 | 1.85 | 1.24 | 41.33 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 613011.76 | 3865760.98 | 2800 | Unit No 01 was on bar delivering an average load equal to 3.2 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-10 | 2026 | 2 | 10 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2026-02-10 | 2026 | 2 | 10 | Karora HPS | 11.8 | 3.72 | 2.8 | 67797 | 65538 | 4.23 | 2.33 | 77.67 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 509885.64 | 1693410.36 | 2259 | Unit#02 synchronized with the system at 0:00hrs and 5:12hrs , accordingly was shutdown at 2:44hrs. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-10 | 2026 | 2 | 10 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 14.6 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remained shut down due to Box Channel repair works by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-10 | 2026 | 2 | 10 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual canal closure extended till Feb 20, 2026. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-10 | 2026 | 2 | 10 | Malakand-3 HPS | 81 | 41 | 39.42 | 946098 | 937790 | 25.72 | 27.21 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2684611.43 | 2880477.37 | 8308 | As per available hydrology from the Irrigation Department Two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-10 | 2026 | 2 | 10 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 18.83 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 Hrs dated 10-01-2026 as per notification of the irrigation department for annual canal closure period of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-10 | 2026 | 2 | 10 | Reshun HPS | 4.2 | 3.09 | 1.19 | 29000 | 28425 | 1.99 | 1.77 | 59 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 383169 | 518157.72 | 575 | Outgoing Feeder breaker remained Off 6times for 6.45hours for loadshedding. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-11 | 2026 | 2 | 11 | Daral Khwar HPS | 36.6 | 3.3 | 3 | 72140 | 68940 | 1.85 | 1.15 | 38.33 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 570016.6 | 3908756.14 | 3200 | Unit No 01 was on bar delivering an average load equal to 3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-11 | 2026 | 2 | 11 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2026-02-11 | 2026 | 2 | 11 | Karora HPS | 11.8 | 3.31 | 2.83 | 65533 | 63163 | 7.47 | 2.34 | 78 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 491408.14 | 1711887.86 | 2370 | The plant was operational on average load 2.83MW and A max Load 3.31MW as per available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-11 | 2026 | 2 | 11 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 14.6 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | Plant remain shutdown due to box channel repair work as requested by the EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-11 | 2026 | 2 | 11 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-11 | 2026 | 2 | 11 | Malakand-3 HPS | 81 | 44 | 39.87 | 956922 | 949280 | 25.72 | 27.8 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2717503.86 | 2847584.94 | 7642 | As per available hydrology from the Irrigation Department Two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-11 | 2026 | 2 | 11 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 18.83 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 hrs on date 10-01-2026 due to the annual canal closure of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-11 | 2026 | 2 | 11 | Reshun HPS | 4.2 | 2.94 | 1.14 | 25000 | 24465 | 1.99 | 1.53 | 51 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 329788.2 | 571538.52 | 535 | Outgoing feeder breaker remained off 6times for 6.30hours for loadshedding due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-12 | 2026 | 2 | 12 | Daral Khwar HPS | 36.6 | 3 | 2.9 | 69690 | 66890 | 1.85 | 1.12 | 37.33 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 553066.59 | 3925706.16 | 2800 | 1. Unit No 01 was on bar delivering an average load equal to 2.9 MW according to available hydrology. 2. Unit No 01 tripped at 23:25 hrs due to frequency fluctuation. The unit resynchronized with the national grid at 23:39 hrs. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-12 | 2026 | 2 | 12 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2026-02-12 | 2026 | 2 | 12 | Karora HPS | 11.8 | 3.48 | 2.66 | 61094 | 58914 | 7.47 | 2.19 | 73 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 458350.92 | 1744945.08 | 2180 | the plant was operational on average load of 2.66mw and maximum load of 3.48mw as per available hydrology | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-12 | 2026 | 2 | 12 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 14.6 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remain shut down due to Box Channel repair works as requested by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-12 | 2026 | 2 | 12 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-12 | 2026 | 2 | 12 | Malakand-3 HPS | 81 | 42 | 39.59 | 950067 | 942570 | 25.72 | 26.71 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2698295.14 | 2866793.66 | 7497 | As per available hydrology from the Irrigation Department Two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-12 | 2026 | 2 | 12 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 18.83 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 Hrs dated 10-01-2026 as per notification of the irrigation department for annual canal closure period of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-12 | 2026 | 2 | 12 | Reshun HPS | 4.2 | 3.01 | 1.18 | 25000 | 24438 | 1.99 | 1.53 | 51 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 329424.24 | 571902.48 | 562 | Outgoing feeder breaker remained Off 6times for7.25hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-13 | 2026 | 2 | 13 | Daral Khwar HPS | 36.6 | 4.3 | 3.4 | 82150 | 78950 | 1.85 | 1.32 | 44 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 652782.28 | 3825990.46 | 3200 | Unit No 01 was on bar delivering an average load equal to 3.4 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-13 | 2026 | 2 | 13 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2026-02-13 | 2026 | 2 | 13 | Karora HPS | 11.8 | 4.49 | 2.38 | 54565 | 52935 | 7.47 | 1.96 | 65.33 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 411834.3 | 1791461.7 | 1630 | the plant was operational on average load of 2.38mw and maximum load of 4.49mw as per available hydrology | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-13 | 2026 | 2 | 13 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 14.6 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remain shut down due to Box Channel repair works as requested by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-13 | 2026 | 2 | 13 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-13 | 2026 | 2 | 13 | Malakand-3 HPS | 81 | 41 | 37.98 | 911496 | 904150 | 25.72 | 26.25 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2588310.2 | 2976778.6 | 7346 | As per available hydrology from the Irrigation Department Two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-13 | 2026 | 2 | 13 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 18.83 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 Hrs dated 10-01-2026 as per notification of the irrigation department for annual canal closure period of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-13 | 2026 | 2 | 13 | Reshun HPS | 4.2 | 2.97 | 1 | 23000 | 22470 | 1.99 | 1.5 | 49.93 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 302895.6 | 598431.12 | 530 | Outgoing feeder breaker remained Off 6times for 4.42hours due to les hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-14 | 2026 | 2 | 14 | Daral Khwar HPS | 36.6 | 4.3 | 3.8 | 91470 | 88470 | 1.85 | 1.48 | 49.33 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 731496.5 | 3747276.24 | 3000 | Unit No 01 was on bar delivering an average load equal to 3.8 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-14 | 2026 | 2 | 14 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2026-02-14 | 2026 | 2 | 14 | Karora HPS | 11.8 | 4.72 | 3.6 | 82116 | 82116 | 7.47 | 2.96 | 98.67 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 638862.48 | 1564433.52 | 0 | the plant was operational on average load of 3.60mw and maximum load of 4.72mw as per available hydrology | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-14 | 2026 | 2 | 14 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant was shut down due to box channel repair work in progress from EPC contractor side | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-14 | 2026 | 2 | 14 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-14 | 2026 | 2 | 14 | Malakand-3 HPS | 81 | 42 | 40.08 | 961829 | 954690 | 25.72 | 26.98 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2732991.06 | 2832097.74 | 7139 | As per available hydrology from the Irrigation Department Two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-14 | 2026 | 2 | 14 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 18.83 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 Hrs dated 10-01-2026 as per the notification of the irrigation department for the annual canal closure period of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-14 | 2026 | 2 | 14 | Reshun HPS | 4.2 | 2.77 | 1.15 | 27000 | 26438 | 1.99 | 1.77 | 59 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 356384.24 | 544942.48 | 562 | outgoing feeder breaker remained off 6times for 5.26 hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-15 | 2026 | 2 | 15 | Daral Khwar HPS | 36.6 | 4 | 3.9 | 92500 | 89700 | 1.85 | 1.5 | 50 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 741666.51 | 3737106.23 | 2800 | Unit No 01 was on bar delivering an average load equal to 3.9 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-15 | 2026 | 2 | 15 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2026-02-15 | 2026 | 2 | 15 | Karora HPS | 11.8 | 4.47 | 3.96 | 94539 | 92361 | 7.47 | 3.29 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 718568.58 | 1484727.42 | 2178 | the plant was operational on average load of 3.96mw and maximum load of 4.47mw as per available hydrology | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-15 | 2026 | 2 | 15 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 14.6 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remain shut down due to Box Channel repair works as requested by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-15 | 2026 | 2 | 15 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-15 | 2026 | 2 | 15 | Malakand-3 HPS | 81 | 43 | 38.89 | 933387 | 926720 | 25.72 | 26.39 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2652921.34 | 2912167.46 | 6667 | As per available hydrology from the Irrigation Department Two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-15 | 2026 | 2 | 15 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 18.83 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 Hrs dated 10-01-2026 as per notification of the irrigation department for annual canal closure period of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-15 | 2026 | 2 | 15 | Reshun HPS | 4.2 | 2.8 | 1.1 | 25000 | 24410 | 1.99 | 1.53 | 51 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 329046.8 | 572279.92 | 590 | Outgoing feeder breaker remained Off 4times for 5.05hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-16 | 2026 | 2 | 16 | Daral Khwar HPS | 36.6 | 4.3 | 4.1 | 98280 | 95080 | 1.85 | 1.59 | 53 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 786149.96 | 3692622.78 | 3200 | Unit No 01 was on bar delivering an average load equal to 4.1 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-16 | 2026 | 2 | 16 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7092 | 0 | 79.57 | 0 | 0 | 0 | 0 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-16 | 2026 | 2 | 16 | Karora HPS | 11.8 | 5.79 | 4.6 | 108211 | 105990 | 7.47 | 3.78 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 824602.2 | 1378693.8 | 2221 | the plant was operational on average load of 4.60mw and maximum load of 5.79mw as per available hydrology | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-16 | 2026 | 2 | 16 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 14.6 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remain shut down due to Box Channel repairs works, as requested by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-16 | 2026 | 2 | 16 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-16 | 2026 | 2 | 16 | Malakand-3 HPS | 81 | 43 | 39.76 | 954210 | 947020 | 25.72 | 26.95 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2711034.15 | 2854054.65 | 7190 | As per available hydrology from the Irrigation Department Two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-16 | 2026 | 2 | 16 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 18.83 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 Hrs dated 10-01-2026 as per notification of the irrigation department for annual canal closure period of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-16 | 2026 | 2 | 16 | Reshun HPS | 4.2 | 2.96 | 1.04 | 28000 | 27402 | 1.99 | 1.71 | 57 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 369378.96 | 531947.76 | 598 | Outgoing feeder breaker remained off 3times for 5.30hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-17 | 2026 | 2 | 17 | Daral Khwar HPS | 36.6 | 4.3 | 3.3 | 79030 | 77430 | 1.85 | 1.29 | 43 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 640214.47 | 3838558.28 | 1600 | 1. Unit No 01 was on bar delivering an average load equal to 3.3 MW according to available hydrology. 2. Plant shutdown at 1301 hrs under NOC for PESCO emergency maintenance. 132 KV line tripped at 1305 hrs. 3. 132 KV line restored at 1710 hrs and unit No 01 synchronized at 1728 hrs. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-17 | 2026 | 2 | 17 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.12 | 0.04 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2026-02-17 | 2026 | 2 | 17 | Karora HPS | 11.8 | 4.48 | 4.03 | 94437 | 92169 | 7.39 | 3.31 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 717074.82 | 1486221.18 | 2268 | unit#02 is on bar delivering average load of 4.03MW to the system as per available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-17 | 2026 | 2 | 17 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant was shut down due to box channel repair work in progress from EPC contractor side. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-17 | 2026 | 2 | 17 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Closure | machai.12333@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2026-02-17 | 2026 | 2 | 17 | Malakand-3 HPS | 81 | 42 | 38.93 | 934395 | 927140 | 25.72 | 26.61 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2654123.68 | 2910965.12 | 7255 | As per available hydrology from the Irrigation Department Two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-17 | 2026 | 2 | 17 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 18.83 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 Hrs dated 10-01-2026 as per notification of the irrigation department for annual canal closure period of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-17 | 2026 | 2 | 17 | Reshun HPS | 4.2 | 2.85 | 1.11 | 25000 | 24404 | 1.99 | 1.53 | 51 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 328965.92 | 572360.8 | 596 | Outgoing feeder breaker remained off 2times for 4.20hours due to less hydrolgy. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-18 | 2026 | 2 | 18 | Daral Khwar HPS | 36.6 | 5.5 | 4.4 | 105520 | 102320 | 1.85 | 1.71 | 57 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 846012.46 | 3632760.29 | 3200 | Unit No 01 was on bar delivering an average load equal to 4.4 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-18 | 2026 | 2 | 18 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.23 | 0.07 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2026-02-18 | 2026 | 2 | 18 | Karora HPS | 11.8 | 4.98 | 4.07 | 95807 | 93610 | 7.47 | 3.36 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 728285.8 | 1475010.2 | 2197 | the plant was operational on average load 4.07MW and a maximum load 4.98MW as per hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-18 | 2026 | 2 | 18 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant was shut down due to box channel repair work in progress from EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-18 | 2026 | 2 | 18 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Closure | machai.12333@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Link_Generation_Data_Summary.xlsx
2026-02-18 | 2026 | 2 | 18 | Malakand-3 HPS | 81 | 40 | 36.38 | 873081 | 865760 | 25.72 | 25.12 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2478411.15 | 3086677.65 | 7321 | As per available hydrology from the Irrigation Department Two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-18 | 2026 | 2 | 18 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 18.83 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 Hrs dated 10-01-2026 as per notification of the irrigation department for annual canal closure period of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-18 | 2026 | 2 | 18 | Reshun HPS | 4.2 | 3.17 | 1.04 | 27000 | 26405 | 1.99 | 1.77 | 59 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 355939.4 | 545387.32 | 595 | outgoing feeder breaker remained Off 3times due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-19 | 2026 | 2 | 19 | Daral Khwar HPS | 36.6 | 5.5 | 5 | 120090 | 117690 | 1.85 | 1.97 | 65.67 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 973096.23 | 3505676.52 | 2400 | Unit No 01 was on bar delivering an average load equal to 5 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-19 | 2026 | 2 | 19 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.35 | 0.11 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. 30 days shut down permit obtained from Executive Engineer SS&TL HAZECO Abbottabad for rehabilitation of the collapsed Tower# 29 and stringing works. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2026-02-19 | 2026 | 2 | 19 | Karora HPS | 11.8 | 5.45 | 4.72 | 112487 | 110300 | 7.47 | 3.85 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 858134 | 1345162 | 2187 | The plant was operational on average load 4.72MW and Maximum 5.45MW as per hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-19 | 2026 | 2 | 19 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant was shut down due to box channel repair work in progress from EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-19 | 2026 | 2 | 19 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-19 | 2026 | 2 | 19 | Malakand-3 HPS | 81 | 39 | 31.42 | 754095 | 747130 | 25.72 | 21.76 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2138809.05 | 3426279.75 | 6965 | As per Irrigation Department letter C.W. No. 50-7 dated 19-02-2026, water was diverted from the auxiliary tunnel to Benton tunnel; consequently, the unit was desynchronized from the system at 07:44hrs due to less hydrology and placed on standby. Unit synchronized with the system at 14:55hrs as water has been diverted back from the Benton tunnel to auxiliary tunnel i.e. towards Malakand-III channel by Irrigation Department. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-19 | 2026 | 2 | 19 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 18.83 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 Hrs dated 10-01-2026 as per notification of the irrigation department for annual canal closure period of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-19 | 2026 | 2 | 19 | Reshun HPS | 4.2 | 2.9 | 1.17 | 26000 | 25420 | 1.99 | 1.59 | 53 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 342661.6 | 558665.12 | 580 | Outgoing feeder breaker remained Off 4times for 7.10hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-20 | 2026 | 2 | 20 | Daral Khwar HPS | 36.6 | 6 | 5.5 | 131410 | 128610 | 1.85 | 2.15 | 71.67 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 1063386.06 | 3415386.68 | 2800 | Unit No 01 was on bar delivering an average load equal to 5.5 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-20 | 2026 | 2 | 20 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.47 | 0.14 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. A 30-day shutdown permit has been obtained from the Executive Engineer, SS&TL, HAZECO Abbottabad, for the erection of collapsed Tower No. 29 and associated stringing works. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2026-02-20 | 2026 | 2 | 20 | Karora HPS | 11.8 | 5.8 | 5.03 | 114918 | 112985 | 7.47 | 4.14 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 879023.3 | 1324272.7 | 1933 | the plant was operational average load 5.03mw and maximum load 5.8mw as per available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-20 | 2026 | 2 | 20 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 14.6 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant was shut down due to box channel repair work by EPC contractor | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-20 | 2026 | 2 | 20 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-20 | 2026 | 2 | 20 | Malakand-3 HPS | 81 | 39 | 33.86 | 812741 | 805810 | 25.72 | 23.23 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2306792.29 | 3258296.51 | 6931 | Unit #01 desynchronized from the system at 18:40hrs as water has been diverted back from the auxiliary tunnel to Benton tunnel i.e. Malakand-III channel by Irrigation Department | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-20 | 2026 | 2 | 20 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 18.83 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant has remained shut down since 0000 Hrs dated 10-01-2026 as per the notification of the irrigation department for the annual canal closure period of 2026. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-20 | 2026 | 2 | 20 | Reshun HPS | 4.2 | 3.04 | 1.15 | 25000 | 24400 | 1.99 | 1.53 | 51 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 328912 | 572414.72 | 600 | Outgoing feeder breaker remained Off 3times for 4.40hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-21 | 2026 | 2 | 21 | Daral Khwar HPS | 36.6 | 6 | 5.9 | 141520 | 139120 | 1.85 | 2.33 | 77.67 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 1150285.9 | 3328486.85 | 2400 | Unit No 01 was on bar delivering an average load equal to 5.9 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-21 | 2026 | 2 | 21 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.58 | 0.18 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. A 30-day shutdown permit has been obtained from the Executive Engineer, SS&TL, HAZECO Abbottabad, for the erection of collapsed Tower No. 29 and associated stringing works. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2026-02-21 | 2026 | 2 | 21 | Karora HPS | 11.8 | 5.9 | 5.37 | 126824 | 125375 | 7.39 | 4.42 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 975417.5 | 1227878.5 | 1449 | The plant was operational on average load 5.37mw and maximum load 5.9mw as per hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-21 | 2026 | 2 | 21 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 14.6 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | Plant is shut down due to repair work in Box Channel | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-21 | 2026 | 2 | 21 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Annual Closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-21 | 2026 | 2 | 21 | Malakand-3 HPS | 81 | 25 | 19.67 | 472109 | 466820 | 25.72 | 13.2 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1336365.61 | 4228723.19 | 5289 | As per available Hydrology from Irrigation department one unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-21 | 2026 | 2 | 21 | Pehur HPS | 18 | 5.74 | 2.49 | 59800 | 56000 | 18.83 | 6 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 210952 | 1416392 | 3800 | Unit# 01 & 02 were taken on bar at 1327 & 1407 Hrs with total load 5.60 after receiving a message from irrigation department to release 10 cms flow in the canal. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-21 | 2026 | 2 | 21 | Reshun HPS | 4.2 | 2.89 | 1.14 | 27000 | 26402 | 1.99 | 1.77 | 59 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 355898.96 | 545427.76 | 598 | Outgoing feeder breaker remained off 3times for 5.35hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-22 | 2026 | 2 | 22 | Daral Khwar HPS | 36.6 | 6 | 6 | 143130 | 140330 | 1.85 | 2.35 | 78.33 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 1160290.54 | 3318482.2 | 2800 | Unit No 01 was on bar delivering an average load equal to 6 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-22 | 2026 | 2 | 22 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.7 | 0.21 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. A 30-day shutdown permit has been obtained from the Executive Engineer, SS&TL, HAZECO Abbottabad, for the erection of collapsed Tower No. 29 and associated stringing works. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2026-02-22 | 2026 | 2 | 22 | Karora HPS | 11.8 | 5.7 | 5.47 | 129993 | 128052 | 7.39 | 4.49 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 996244.56 | 1207051.44 | 1941 | Unit#02 is on bar delivering average load of 5.47 MW to National grid. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-22 | 2026 | 2 | 22 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 14.6 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | Plant is shut down due to repair work in Box Channel. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-22 | 2026 | 2 | 22 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 1 | 10 | 100 | 4.671 | 33.33 | 70 | 20800 | 97156.8 | 0 | 97156.8 | 0 | unit stand still due to low hydrology. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-22 | 2026 | 2 | 22 | Malakand-3 HPS | 81 | 20 | 18.44 | 442506 | 437170 | 25.72 | 12.59 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1251486.56 | 4313602.24 | 5336 | As per available Hydrology from Irrigation department one unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-22 | 2026 | 2 | 22 | Pehur HPS | 18 | 6.55 | 6.14 | 147300 | 144000 | 18.83 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 542448 | 1084896 | 3300 | Plant remained operational throughout 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-22 | 2026 | 2 | 22 | Reshun HPS | 4.2 | 3.12 | 1.13 | 25000 | 24415 | 1.99 | 1.53 | 51 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 329114.2 | 572212.52 | 585 | Outgoing feeder breaker remained off 3times for 6.00hours due to less hydrology | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-23 | 2026 | 2 | 23 | Daral Khwar HPS | 36.6 | 6.5 | 6 | 144160 | 141360 | 1.85 | 2.36 | 78.67 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 1168806.89 | 3309965.86 | 2800 | 1. Unit No 01 and 02 were on bar delivering an average load equal to 6 MW according to available hydrology. 2. Unit No 02 was synchronized at 1404 Hrs due to increased hydrology and Unit No 01 was desynchronized at 1406 Hrs. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-23 | 2026 | 2 | 23 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.81 | 0.25 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. A 30-day shutdown permit has been obtained from the Executive Engineer, SS&TL, HAZECO Abbottabad, for the erection of collapsed Tower No. 29 and associated stringing works. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2026-02-23 | 2026 | 2 | 23 | Karora HPS | 11.8 | 5.4 | 5.23 | 124107 | 122195 | 7.39 | 4.31 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 950677.1 | 1252618.9 | 1912 | Unit # 02 is on bar delivering load 5.23MW to the national Grid. Max Load: 5.4MW and Minimum Load: 4.5MW as per available Hydrology | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-23 | 2026 | 2 | 23 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 14.6 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | Not reported | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-23 | 2026 | 2 | 23 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 11 | 100 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Less inflow and mechanical bearing oil visibility issue. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-23 | 2026 | 2 | 23 | Malakand-3 HPS | 81 | 20 | 17.49 | 419848 | 414410 | 20.52 | 12.13 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1186331.51 | 4378757.29 | 5438 | As per available Hydrology from Irrigation department one Unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-23 | 2026 | 2 | 23 | Pehur HPS | 18 | 7.81 | 6.73 | 161700 | 157000 | 18.83 | 12 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 591419 | 1035925 | 4700 | The plant remained operational throughout 24 hours as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-23 | 2026 | 2 | 23 | Reshun HPS | 4.2 | 2.99 | 1.19 | 25000 | 24400 | 1.99 | 1.53 | 51 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 328912 | 572414.72 | 600 | Outgoing feeder breaker remained Off 3times for 6.10hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-24 | 2026 | 2 | 24 | Daral Khwar HPS | 36.6 | 7 | 6.3 | 151810 | 148610 | 1.85 | 2.49 | 83 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 1228752.06 | 3250020.68 | 3200 | Unit No 02 was on bar delivering an average load equal to 6.3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-24 | 2026 | 2 | 24 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. A 30-day shutdown permit has been obtained from the Executive Engineer, SS&TL, HAZECO Abbottabad, for the erection of collapsed Tower No. 29 and associated stringing works. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-02-24 | 2026 | 2 | 24 | Karora HPS | 11.8 | 5.2 | 5.13 | 121605 | 119625 | 7.39 | 4.22 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 930682.5 | 1272613.5 | 1980 | Unit # 02 is on bar delivering 5.13MW average load to the National Grid. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-24 | 2026 | 2 | 24 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 14.6 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remained shut down due to Box Channel repair works by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-24 | 2026 | 2 | 24 | Machai HPS | 2.6 | 0.48 | 0.09 | 2216 | 1936 | 17 | 12 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 9043.06 | 282427.34 | 280 | Unit stands still due to less inflow. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-24 | 2026 | 2 | 24 | Malakand-3 HPS | 81 | 18 | 15.94 | 382563 | 377280 | 25.72 | 11.13 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1080039.46 | 4485049.34 | 5283 | As per available Hydrology from Irrigation department one Unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-24 | 2026 | 2 | 24 | Pehur HPS | 18 | 7.87 | 6.96 | 167100 | 163000 | 18.83 | 16 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 614021 | 1013323 | 4100 | Plant remained operational throughout 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-24 | 2026 | 2 | 24 | Reshun HPS | 4.2 | 2.88 | 1.18 | 24000 | 23424 | 1.99 | 1.47 | 49 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 315755.52 | 585571.2 | 576 | Outgoing feeder breaker remained off 3times for 5.20hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-25 | 2026 | 2 | 25 | Daral Khwar HPS | 36.6 | 7 | 5.9 | 142460 | 139660 | 1.85 | 2.34 | 78 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 1154750.78 | 3324021.97 | 2800 | 1. Unit No 02 was on bar delivering an average load equal to 5.9 MW according to available hydrology. 2. Unit No 02 tripped at 20:31 Hrs due to frequency fluctuations. The Unit was synchronized with the national grid at 20:50 Hrs. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-25 | 2026 | 2 | 25 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. A 30-day shutdown permit has been obtained from the Executive Engineer, SS&TL, HAZECO Abbottabad, for the erection of collapsed Tower No. 29 and associated stringing works. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-02-25 | 2026 | 2 | 25 | Karora HPS | 11.8 | 5.2 | 4.77 | 115617 | 113713 | 7.39 | 3.95 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 884687.14 | 1318608.86 | 1904 | Unit#02 is on bar delivering average load of 4.77MW to the national grid. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-25 | 2026 | 2 | 25 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 14.6 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remain shut down due to Box Channel repair works by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-25 | 2026 | 2 | 25 | Machai HPS | 2.6 | 0.87 | 0.5 | 6904 | 6556 | 17 | 13 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 30623.08 | 260847.32 | 348 | Unit remained shut down due to inadequate inflow, for some hours. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-25 | 2026 | 2 | 25 | Malakand-3 HPS | 81 | 17 | 15.89 | 381255 | 375740 | 25.72 | 11.15 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1075630.9 | 4489457.9 | 5515 | As per available Hydrology from Irrigation department one Unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-25 | 2026 | 2 | 25 | Pehur HPS | 18 | 6.69 | 4.29 | 103000 | 100000 | 18.83 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 376700 | 1250644 | 3000 | At 0530 hours the plant was completely shut down upon instructions of the irrigation official due to a blockage in one of the canal outlets. At 1335 hours unit #01 and #02 started and synchronized normally | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-25 | 2026 | 2 | 25 | Reshun HPS | 4.2 | 1.72 | 1.02 | 24500 | 23926 | 1.99 | 1.5 | 24.31 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 322522.48 | 578804.24 | 574 | No data submitted for this date | zafar.src@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-02-26 | 2026 | 2 | 26 | Daral Khwar HPS | 36.6 | 6.4 | 5.6 | 134840 | 131640 | 1.85 | 2.2 | 73.33 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 1088439.01 | 3390333.73 | 3200 | Unit No 02 was on bar delivering an average load equal to 5.6 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-26 | 2026 | 2 | 26 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. A 30-day shutdown permit has been obtained from the Executive Engineer, SS&TL, HAZECO Abbottabad, for the erection of collapsed Tower No. 29 and associated stringing works. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-02-26 | 2026 | 2 | 26 | Karora HPS | 11.8 | 5 | 4.67 | 110373 | 108463 | 7.39 | 3.84 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 843842.14 | 1359453.86 | 1910 | Unit # 02 is on bar delivering 4.67MW to the national grid | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-26 | 2026 | 2 | 26 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 14.6 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remain shut down due to Box Channel repair works by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-26 | 2026 | 2 | 26 | Machai HPS | 2.6 | 0.68 | 0.38 | 9224 | 8800 | 15 | 13 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 41104.8 | 250365.6 | 424 | Unit stopped for some hours due to inadequate inflow; while tripped 2 times due to 11 KV line tripping. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-26 | 2026 | 2 | 26 | Malakand-3 HPS | 81 | 16 | 14.4 | 345482 | 340030 | 25.72 | 10.32 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 973403.88 | 4591684.92 | 5452 | As per available Hydrology from Irrigation department one Unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-26 | 2026 | 2 | 26 | Pehur HPS | 18 | 6.24 | 6 | 144000 | 140000 | 18.83 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 527380 | 1099964 | 4000 | low head + opening of irrigation valves. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-26 | 2026 | 2 | 26 | Reshun HPS | 4.2 | 2.64 | 1.1 | 25000 | 24428 | 1.99 | 1.53 | 51 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 329289.44 | 572037.28 | 572 | 1. Outgoing feeder breaker remained off 3times for 7.25hours. 2. Outgoing feeder breaker tripped due to line faults. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-27 | 2026 | 2 | 27 | Daral Khwar HPS | 36.6 | 6 | 5.4 | 128530 | 125730 | 1.85 | 2.1 | 70 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 1039573.36 | 3439199.38 | 2800 | Unit No 02 was on bar delivering an average load equal to 5.4 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-27 | 2026 | 2 | 27 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. A 30-day shutdown permit has been obtained from the Executive Engineer, SS&TL, HAZECO Abbottabad, for the erection of collapsed Tower No. 29 and associated stringing works. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-02-27 | 2026 | 2 | 27 | Karora HPS | 11.8 | 4.8 | 4.37 | 104314 | 102335 | 7.39 | 3.57 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 796166.3 | 1407129.7 | 1979 | Unit #02 is on bar delivering average load of 4.37 MW to National grid. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-27 | 2026 | 2 | 27 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 14.6 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remain shut down due to Box Channel repair works by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-27 | 2026 | 2 | 27 | Machai HPS | 2.6 | 0.5 | 0.4 | 11340 | 10736 | 1 | 13 | 100 | 4.671 | 33.33 | 70 | 20800 | 97156.8 | 50147.86 | 47008.94 | 604 | Unit tripped at 0343hrs due to 132kv line tripped, while restored at 0354hrs and unit synch at 0404hrs, Unit normally stopped at 2312hrs because of low hydrology, while unit synch at 2357hrs. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-27 | 2026 | 2 | 27 | Malakand-3 HPS | 81 | 15 | 13.91 | 333872 | 328280 | 25.72 | 10.06 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 939767.16 | 4625321.64 | 5592 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-27 | 2026 | 2 | 27 | Pehur HPS | 18 | 6.6 | 6.12 | 147000 | 142000 | 18.83 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 534914 | 1092430 | 5000 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-27 | 2026 | 2 | 27 | Reshun HPS | 4.2 | 2.77 | 1.03 | 240000 | 23435 | 1.99 | 1.47 | 49 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 315903.8 | 585422.92 | 216565 | 1.outgoing feeder breaker remained off 4times for 6.15hours due to less hydrology. 2. outgoing feeder tripped 3times. | zafar.src@gmail.com | Original | CHECK: units > installed capacity x 24h (source me verify karein) | Link_Generation_Data_Summary.xlsx
2026-02-28 | 2026 | 2 | 28 | Daral Khwar HPS | 36.6 | 5.5 | 5.1 | 122080 | 118480 | 1.85 | 1.98 | 66 | 8.2683 | 61.67 | 48 | 541680 | 4478772.74 | 979628.18 | 3499144.56 | 3600 | Unit No 02 was on bar delivering an average load equal to 5.1 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-28 | 2026 | 2 | 28 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. A 30-day shutdown permit has been obtained from the Executive Engineer, SS&TL, HAZECO Abbottabad, for the erection of collapsed Tower No. 29 and associated stringing works. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-02-28 | 2026 | 2 | 28 | Karora HPS | 11.8 | 4.5 | 4.03 | 96526 | 94617 | 7.39 | 3.33 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 736120.26 | 1467175.74 | 1909 | unit#02 is on bar delivering average load of 4.03MW to National grid. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-28 | 2026 | 2 | 28 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 14.6 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The Power Plant remain shut down due to Box Channel repair works by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-28 | 2026 | 2 | 28 | Machai HPS | 2.6 | 0.43 | 0.07 | 1646 | 1540 | 15 | 6 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 7193.34 | 284277.06 | 106 | Unit stopped at 0531 hrs due to low hydrology because of weekly canal closure. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-28 | 2026 | 2 | 28 | Malakand-3 HPS | 81 | 14 | 12.22 | 293248 | 287620 | 25.72 | 9.43 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 823369.77 | 4741719.03 | 5628 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-28 | 2026 | 2 | 28 | Pehur HPS | 18 | 6.44 | 5.9 | 141700 | 138000 | 18.89 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 519846 | 1107498 | 3700 | The plant remained operational throughout 24 hours as per available hydrology + irrigation valve is open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-02-28 | 2026 | 2 | 28 | Reshun HPS | 4.2 | 2.73 | 1.12 | 25000 | 24431 | 1.99 | 1.53 | 51 | 13.48 | 66.33 | 45 | 66864 | 901326.72 | 329329.88 | 571996.84 | 569 | Outgoing feeder breaker remained Off 4times for 6.55hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-01 | 2026 | 3 | 1 | Daral Khwar HPS | 36.6 | 5.5 | 5.3 | 126380 | 123580 | 4.76 | 2.07 | 69 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1021796.51 | 6241078.21 | 2800 | Unit No 02 was on bar delivering an average load equal to 5.3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-01 | 2026 | 3 | 1 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. A 30-day shutdown permit has been obtained from the Executive Engineer, SS&TL, HAZECO Abbottabad, for the erection of collapsed Tower No. 29 and associated stringing works. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-03-01 | 2026 | 3 | 1 | Karora HPS | 11.8 | 4.2 | 3.79 | 89299 | 87423 | 7.87 | 3.12 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 680150.94 | 1523145.06 | 1876 | unit#02 is on bar delivering average load of 3.79MW to national grid. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-01 | 2026 | 3 | 1 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 98.7 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remain shut down due to Box Channel repair works by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-01 | 2026 | 3 | 1 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Unit standstill due to low hydrology in canal because of Weekly closure from Irrigation side | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-01 | 2026 | 3 | 1 | Malakand-3 HPS | 81 | 13 | 10.07 | 241625 | 246580 | 47.34 | 8.84 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 705884.57 | 4859204.23 | 4955 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original | CHECK: Net > Units (source me verify karein) | Link_Generation_Data_Summary.xlsx
2026-03-01 | 2026 | 3 | 1 | Pehur HPS | 18 | 5.7 | 5.56 | 133300 | 129000 | 16.35 | 13.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 485943 | 1141401 | 4300 | Plant remained operational throughout 24 Hrs as per available hydrology & Irrigation valve open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-01 | 2026 | 3 | 1 | Reshun HPS | 4.2 | 2.79 | 1.23 | 25000 | 24435 | 1.41 | 1.77 | 59 | 13.48 | 47 | 45 | 47376 | 638628.48 | 329383.8 | 309244.68 | 565 | Outgoing feeder breaker remained off 5times for 7.55hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-02 | 2026 | 3 | 2 | Daral Khwar HPS | 36.6 | 5.5 | 5.3 | 128370 | 125570 | 4.76 | 2.1 | 70 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1038250.43 | 6224624.29 | 2800 | 1. Unit No 02 was on bar delivering an average load equal to 5.3 MW according to available hydrology. 2. 132 KV supply failed at 1052 Hrs and was restored at 1101 Hrs. 3. Unit No 02 was synchronized with the national grid at 1109 Hrs. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-02 | 2026 | 3 | 2 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. A 30-day shutdown permit has been obtained from the Executive Engineer, SS&TL, HAZECO Abbottabad, for the erection of collapsed Tower No. 29 and associated stringing works. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-03-02 | 2026 | 3 | 2 | Karora HPS | 11.8 | 4 | 3.45 | 82030 | 80127 | 7.87 | 2.88 | 96 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 623388.06 | 1579907.94 | 1903 | Unit#02 is on bar delivering average load 3.45MW to National grid. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-02 | 2026 | 3 | 2 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 14.6 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remain shut down due to box channel repair works by EPC contractor | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-02 | 2026 | 3 | 2 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Unit standstill due to weekly canal closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-02 | 2026 | 3 | 2 | Malakand-3 HPS | 81 | 12 | 5.74 | 0 | 132670 | 47.34 | 4.3 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 379794.41 | 5185294.39 | 132670 | As per irrigation department letter C.W No.82-5 dated 02-03-2026 water diverted from auxiliary tunnel to Benton tunnel due to extreme shortage at water in upper swat river, consequently the unit desynchronized from the system at 12:48Hrs due to less hydrology and place on standby. | malakand03hpc@gmail.com | Original | CHECK: Net > Units (source me verify karein) | Link_Generation_Data_Summary.xlsx
2026-03-02 | 2026 | 3 | 2 | Pehur HPS | 18 | 5.75 | 5.64 | 135300 | 131000 | 16.35 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 493477 | 1133867 | 4300 | Generation is less because of low head + opening of irrigation valves. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-02 | 2026 | 3 | 2 | Reshun HPS | 4.2 | 2.99 | 1.01 | 25000 | 24436 | 1.41 | 1.47 | 49 | 13.48 | 47 | 45 | 47376 | 638628.48 | 329397.28 | 309231.2 | 564 | Outgoing feeder breaker remained Off 5times for 7.25hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-03 | 2026 | 3 | 3 | Daral Khwar HPS | 36.6 | 6.7 | 5.8 | 138930 | 135730 | 4.76 | 2.27 | 75.67 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1122256.36 | 6140618.36 | 3200 | Unit No 02 was on bar delivering an average load equal to 5.8 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-03 | 2026 | 3 | 3 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. A 30-day shutdown permit has been obtained from the Executive Engineer, SS&TL, HAZECO Abbottabad, for the erection of collapsed Tower No. 29 and associated stringing works. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-03-03 | 2026 | 3 | 3 | Karora HPS | 11.8 | 4 | 3.71 | 89037 | 87169 | 7.87 | 3.1 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 678174.82 | 1525121.18 | 1868 | Unit#02 is on bar delivring average load of 3.71MW to grid. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-03 | 2026 | 3 | 3 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 14.6 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remain shut down due to box channel repair works by EPC contractor | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-03 | 2026 | 3 | 3 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Unit standstill due to Canal closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-03 | 2026 | 3 | 3 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 47.34 | 0 | 0 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 0 | 5565088.8 | 0 | As per irrigation department letter C.W No.82-5 dated 02-03-2026 water diverted from auxiliary tunnel to Benton tunnel due to extreme shortage at water in upper swat river, consequently the unit desynchronized from the system at 12:48Hrs due to less hydrology and place on standby. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-03 | 2026 | 3 | 3 | Pehur HPS | 18 | 5.73 | 5.57 | 133700 | 129000 | 16.35 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 485943 | 1141401 | 4700 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-03 | 2026 | 3 | 3 | Reshun HPS | 4.2 | 2.86 | 1.16 | 24000 | 23440 | 1.14 | 1.47 | 49 | 13.48 | 38.03 | 45 | 38337.6 | 516790.85 | 315971.2 | 200819.65 | 560 | Outgoing feeder breaker remained off 4times for 7.00hour due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-04 | 2026 | 3 | 4 | Daral Khwar HPS | 36.6 | 7.5 | 6.7 | 167400 | 164600 | 4.76 | 2.75 | 91.67 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1360962.18 | 5901912.54 | 2800 | Unit No 02 was on bar delivering an average load equal to 6.7 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-04 | 2026 | 3 | 4 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. A 30-day shutdown permit has been obtained from the Executive Engineer, SS&TL, HAZECO Abbottabad, for the erection of collapsed Tower No. 29 and associated stringing works. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-03-04 | 2026 | 3 | 4 | Karora HPS | 11.8 | 5.3 | 4.27 | 100812 | 98900 | 7.87 | 3.51 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 769442 | 1433854 | 1912 | The plant was operational on average load 4.27MW and maximum load 5.3MW as per hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-04 | 2026 | 3 | 4 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 98.7 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant was shut down due to Box channel repair work in progress from EPC contractor side. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-04 | 2026 | 3 | 4 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4.671 | 33.33 | 70 | 20800 | 97156.8 | 0 | 97156.8 | 0 | Unit stand still due to Weekly closure in irrigation canal | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-04 | 2026 | 3 | 4 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 47.34 | 0 | 0 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 0 | 5565088.8 | 0 | As per irrigation department letter C.W No.82-5 dated 02-03-2026 water diverted from auxiliary tunnel to Benton tunnel due to extreme shortage at water in upper swat river, consequently the unit desynchronized from the system at 12:48Hrs due to less hydrology and place on standby. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-04 | 2026 | 3 | 4 | Pehur HPS | 18 | 5.57 | 5.5 | 132300 | 128000 | 16.35 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 482176 | 1145168 | 4300 | Plant remained operational throughout 24 Hrs as per available hydrology & Irrigation valve open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-04 | 2026 | 3 | 4 | Reshun HPS | 4.2 | 2.72 | 1.22 | 26000 | 25438 | 1.41 | 1.59 | 53 | 13.48 | 47 | 45 | 47376 | 638628.48 | 342904.24 | 295724.24 | 562 | Outgoing feeder breaker remained Off 4times for 6.15hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-05 | 2026 | 3 | 5 | Daral Khwar HPS | 36.6 | 12 | 8.5 | 204450 | 201250 | 4.76 | 3.37 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 1663995.38 | 5598879.34 | 3200 | Unit No 02 was on bar delivering an average load equal to 8.5 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-05 | 2026 | 3 | 5 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. A 30-day shutdown permit has been obtained from the Executive Engineer, SS&TL, HAZECO Abbottabad, for the erection of collapsed Tower No. 29 and associated stringing works. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-03-05 | 2026 | 3 | 5 | Karora HPS | 11.8 | 5.1 | 4.48 | 106534 | 104670 | 7.87 | 3.71 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 814332.6 | 1388963.4 | 1864 | The plant was operational on average load 4.48MW and maximum load 5.1MW as per hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-05 | 2026 | 3 | 5 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 98.7 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remains shutdown due to box channel repair as requested by EPC Contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-05 | 2026 | 3 | 5 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 16.2 | 5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Weekly Closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-05 | 2026 | 3 | 5 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 47.34 | 0 | 0 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 0 | 5565088.8 | 0 | As per irrigation department letter C.W No.82-5 dated 02-03-2026 water diverted from auxiliary tunnel to Benton tunnel due to extreme shortage of water in upper swat river, consequently the unit desynchronized from the system due to less hydrology and place on standby. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-05 | 2026 | 3 | 5 | Pehur HPS | 18 | 5.52 | 5.44 | 130600 | 127000 | 16.35 | 13.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 478409 | 1148935 | 3600 | Plant remained operational throughout 24 Hrs as per available hydrology & Irrigation valve open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-05 | 2026 | 3 | 5 | Reshun HPS | 4.2 | 2.88 | 0.93 | 23000 | 22441 | 1.41 | 1.49 | 49.67 | 13.48 | 47 | 45 | 47376 | 638628.48 | 302504.68 | 336123.8 | 559 | Outgoing feeder breaker remained Off 3times for 5.50hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-06 | 2026 | 3 | 6 | Daral Khwar HPS | 36.6 | 11.5 | 10.6 | 253920 | 251120 | 4.76 | 4.2 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2076335.5 | 5186539.22 | 2800 | Unit No 02 was on bar delivering an average load equal to 10.6 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-06 | 2026 | 3 | 6 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. A 30-day shutdown permit has been obtained from the Executive Engineer, SS&TL, HAZECO Abbottabad, for the erection of collapsed Tower No. 29 and associated stringing works. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-03-06 | 2026 | 3 | 6 | Karora HPS | 11.8 | 5.4 | 5.19 | 123062 | 121230 | 7.87 | 4.28 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 943169.4 | 1260126.6 | 1832 | The plant was operational on average load 5.19MW and maximum load 5.4MW as per hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-06 | 2026 | 3 | 6 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 98.7 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remains shutdown due to box channel repair as requested by EPC Contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-06 | 2026 | 3 | 6 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 16.2 | 5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Weekly Closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-06 | 2026 | 3 | 6 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 47.34 | 0 | 0 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 0 | 5565088.8 | 0 | As per irrigation department letter C.W No.82-5 dated 02-03-2026 water diverted from auxiliary tunnel to Benton tunnel due to extreme shortage of water in upper swat river, consequently the unit desynchronized from the system at 12:48Hrs due to less hydrology and place on standby. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-06 | 2026 | 3 | 6 | Pehur HPS | 18 | 5.44 | 5.35 | 128400 | 124000 | 16.35 | 13.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 467108 | 1160236 | 4400 | Plant remained operational throughout 24 Hrs as per available hydrology & Irrigation valve open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-06 | 2026 | 3 | 6 | Reshun HPS | 4.2 | 2.93 | 0.48 | 14000 | 13443 | 1.41 | 0.86 | 28.67 | 13.48 | 47 | 45 | 47376 | 638628.48 | 181211.64 | 457416.84 | 557 | 1. Outging Feeder breaker tripped 3times due to line fault. 1. Breaker remained Off 6.35hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-07 | 2026 | 3 | 7 | Daral Khwar HPS | 36.6 | 13 | 12.5 | 299440 | 296640 | 4.76 | 4.96 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2452708.51 | 4810166.21 | 2800 | Unit No 02 was on bar delivering an average load equal to 12.5 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-07 | 2026 | 3 | 7 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. A 30-day shutdown permit has been obtained from the Executive Engineer, SS&TL, HAZECO Abbottabad, for the erection of collapsed Tower No. 29 and associated stringing works. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-03-07 | 2026 | 3 | 7 | Karora HPS | 11.8 | 5.4 | 5.09 | 120999 | 119255 | 7.87 | 4.19 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 927803.9 | 1275492.1 | 1744 | The plant was operational on average load 5.09MW and maximum load 5.4MW as per hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-07 | 2026 | 3 | 7 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 98.6 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | Not reported | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-07 | 2026 | 3 | 7 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 16.2 | 5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Weekly Closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-07 | 2026 | 3 | 7 | Malakand-3 HPS | 81 | 0 | 0 | 0 | 0 | 47.34 | 0 | 0 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 0 | 5565088.8 | 0 | As per irrigation department letter C.W No.82-5 dated 02-03-2026 water diverted from auxiliary tunnel to Benton tunnel due to extreme shortage of water in upper swat river, consequently the unit desynchronized from the system at 12:48Hrs due to less hydrology and place on standby. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-07 | 2026 | 3 | 7 | Pehur HPS | 18 | 6.82 | 4.9 | 117500 | 115000 | 16.35 | 11.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 433205 | 1194139 | 2500 | The plant remained shut down for 0300 hours upon the instructions of the irrigation SDO in search of a dead body in the canal, & the irrigation valve is open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-07 | 2026 | 3 | 7 | Reshun HPS | 4.2 | 2.68 | 0.8 | 16000 | 14467 | 1.41 | 0.97 | 32.33 | 13.48 | 47 | 45 | 47376 | 638628.48 | 195015.16 | 443613.32 | 1533 | Line faults and less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-08 | 2026 | 3 | 8 | Daral Khwar HPS | 36.6 | 13 | 10.8 | 258230 | 255430 | 4.76 | 4.27 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2111971.87 | 5150902.85 | 2800 | Unit No 02 was on bar delivering an average load equal to 10.8 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-08 | 2026 | 3 | 8 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. A 30-day shutdown permit has been obtained from the Executive Engineer, SS&TL, HAZECO Abbottabad, for the erection of collapsed Tower No. 29 and associated stringing works. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-03-08 | 2026 | 3 | 8 | Karora HPS | 11.8 | 5.1 | 4.87 | 114666 | 112930 | 7.87 | 3.99 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 878595.4 | 1324700.6 | 1736 | The plant was operational on average load 4.87MW and maximum load 5.1MW as per hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-08 | 2026 | 3 | 8 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 98.7 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant is shutdown due to box channel repair as requested by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-08 | 2026 | 3 | 8 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 16.2 | 5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Weekly Canal Closure | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-08 | 2026 | 3 | 8 | Malakand-3 HPS | 81 | 26 | 16.68 | 400364 | 395650 | 47.34 | 11.8 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1132627.25 | 4432461.54 | 4714 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-08 | 2026 | 3 | 8 | Pehur HPS | 18 | 6.69 | 5.73 | 137700 | 133000 | 16.35 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 501011 | 1126333 | 4700 | Plant remained operational throughout 24 Hrs as per available hydrology & Irrigation valve open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-08 | 2026 | 3 | 8 | Reshun HPS | 4.2 | 3.26 | 1.11 | 23000 | 22445 | 1.41 | 1.5 | 50 | 13.48 | 47 | 45 | 47376 | 638628.48 | 302558.6 | 336069.88 | 555 | Outgoing feeder breaker remained off 8.12hours for 5times due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-09 | 2026 | 3 | 9 | Daral Khwar HPS | 36.6 | 21.3 | 13.7 | 329240 | 326040 | 4.76 | 5.45 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2695796.53 | 4567078.19 | 3200 | 1. Unit No 01 and 02 were on bar delivering an average load equal to 13.7 MW according to available hydrology. 2. Unit No 01 synchronized with the national grid at 1740 Hrs due to increased hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-09 | 2026 | 3 | 9 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. A 30-day shutdown permit has been obtained from the Executive Engineer, SS&TL, HAZECO Abbottabad, for the erection of collapsed Tower No. 29 and associated stringing works. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-03-09 | 2026 | 3 | 9 | Karora HPS | 11.8 | 5.9 | 5.17 | 121422 | 119564 | 7.87 | 4.25 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 930207.92 | 1273088.08 | 1858 | the plant was operational on average load of 5.17mw and maximum load of 5.9mw as per available hydrology | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-09 | 2026 | 3 | 9 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 98.7 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remain shut down due to Box Channel repair works by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-09 | 2026 | 3 | 9 | Machai HPS | 2.6 | 0.7 | 0.45 | 8482 | 8008 | 1 | 17 | 100 | 4.671 | 33.33 | 70 | 20800 | 97156.8 | 37405.37 | 59751.43 | 474 | Unit synchronized with the system at 1041hrs. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-09 | 2026 | 3 | 9 | Malakand-3 HPS | 81 | 26 | 23.31 | 559467 | 553160 | 47.34 | 15.43 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1583531.13 | 3981557.67 | 6307 | As per available hydrology from the Irrigation Department one unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-09 | 2026 | 3 | 9 | Pehur HPS | 18 | 6.54 | 5.08 | 122100 | 119000 | 16.35 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 448273 | 1179071 | 3100 | Plant remained operational throughout 24 Hrs as per available hydrology & Irrigation valve open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-09 | 2026 | 3 | 9 | Reshun HPS | 4.2 | 2.88 | 1.12 | 25000 | 24438 | 1.41 | 1.47 | 49 | 13.48 | 47 | 45 | 47376 | 638628.48 | 329424.24 | 309204.24 | 562 | Outgoing feeder breaker remained off 4times for 6.10hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-10 | 2026 | 3 | 10 | Daral Khwar HPS | 36.6 | 36.6 | 26.8 | 642680 | 638280 | 4.76 | 10.67 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 5277490.52 | 1985384.2 | 4400 | 1. Unit No 01, 02 and 03 were on bar delivering an average load equal to 26.8 MW according to available hydrology. 2. Unit No 03 was synchronized with the national grid at 06:09 Hrs due to increased hydrology. 3. Unit No 01 desynchronized at 08:43 Hrs due to less hydrology. 4. Unit No 01 was again synchronized with the national grid at 06:30 Hrs due to increased hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-10 | 2026 | 3 | 10 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. A 30-day shutdown permit has been obtained from the Executive Engineer, SS&TL, HAZECO Abbottabad, for the erection of collapsed Tower No. 29 and associated stringing works. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-03-10 | 2026 | 3 | 10 | Karora HPS | 11.8 | 5.9 | 5.67 | 133555 | 132298 | 7.87 | 4.67 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1029278.44 | 1174017.56 | 1257 | The plant was operational on average load 5.67MW and maximum load 5.9MW as per hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-10 | 2026 | 3 | 10 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 98.7 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remain shut down due to Box Channel repair works by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-10 | 2026 | 3 | 10 | Machai HPS | 2.6 | 0.98 | 0.5 | 13004 | 12496 | 17 | 17 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 58368.82 | 233101.58 | 508 | Unit tripped 6 times due to governor fault. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-10 | 2026 | 3 | 10 | Malakand-3 HPS | 81 | 27 | 25.49 | 611830 | 605740 | 47.34 | 16.68 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 1734051.9 | 3831036.9 | 6090 | As per available hydrology from the Irrigation Department One unit is on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-10 | 2026 | 3 | 10 | Pehur HPS | 18 | 5.6 | 4.89 | 117200 | 113000 | 16.35 | 13 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 425671 | 1201673 | 4200 | low head + valve opening | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-10 | 2026 | 3 | 10 | Reshun HPS | 4.2 | 2.88 | 0.87 | 21000 | 20468 | 1.41 | 1.28 | 42.67 | 13.48 | 47 | 45 | 47376 | 638628.48 | 275908.64 | 362719.84 | 532 | Outgoing feeder breaker remained off for 4.3 hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-11 | 2026 | 3 | 11 | Daral Khwar HPS | 36.6 | 35.5 | 32.2 | 772640 | 767840 | 4.76 | 12.84 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6348731.47 | 914143.25 | 4800 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 32.2 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-11 | 2026 | 3 | 11 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. A 30-day shutdown permit has been obtained from the Executive Engineer, SS&TL, HAZECO Abbottabad, for the erection of collapsed Tower No. 29 and associated stringing works. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-03-11 | 2026 | 3 | 11 | Karora HPS | 11.8 | 5.9 | 3.28 | 80787 | 78475 | 7.35 | 2.79 | 93 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 610535.5 | 1592760.5 | 2312 | Plant on load with max load of 5.9MW | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-11 | 2026 | 3 | 11 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 98.7 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remain shut down due to Box Channel repair works by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-11 | 2026 | 3 | 11 | Machai HPS | 2.6 | 0.77 | 0.06 | 1364 | 1280 | 17.3 | 17 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 5978.88 | 285491.52 | 84 | Unit tripped 2 times due to governor system fault, while remain in operation for only 1.45 hour. Unit remain still for the rest of the hours due to governor system maintenance: as due to the lack of maintenance staff. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-11 | 2026 | 3 | 11 | Malakand-3 HPS | 81 | 46 | 30.69 | 736580 | 729880 | 47.34 | 20.18 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2089427.48 | 3475661.32 | 6700 | Unit #01 synchronized with the system at 14:07 hrs. on 11-03-2026. As per available hydrology from the Irrigation Department, two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-11 | 2026 | 3 | 11 | Pehur HPS | 18 | 4.71 | 4.6 | 110500 | 107000 | 16.35 | 13 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 403069 | 1224275 | 3500 | The plant remained operational throughout 24 hours as per available hydrology, and the irrigation valve is open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-11 | 2026 | 3 | 11 | Reshun HPS | 4.2 | 2.27 | 1.09 | 23000 | 22430 | 1.41 | 1.5 | 50 | 13.48 | 47 | 45 | 47376 | 638628.48 | 302356.4 | 336272.08 | 570 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-12 | 2026 | 3 | 12 | Daral Khwar HPS | 36.6 | 33.3 | 26 | 623990 | 619990 | 4.76 | 10.37 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 5126263.32 | 2136611.4 | 4000 | 1. Unit No 01, 02 and 03 were on bar delivering an average load equal to 26 MW according to available hydrology. 2. Unit No 02 and 03 tripped at 0739 Hrs due to grid over frequency and synchronized at 0757 Hrs and 0800 Hrs respectively. 3. Unit No 01 stopped at 0800 Hrs due to decrease in hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-12 | 2026 | 3 | 12 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. A 30-day shutdown permit has been obtained from the Executive Engineer, SS&TL, HAZECO Abbottabad, for the erection of collapsed Tower No. 29 and associated stringing works. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-03-12 | 2026 | 3 | 12 | Karora HPS | 11.8 | 5.9 | 4.33 | 99165 | 97094 | 7.35 | 3.63 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 755391.32 | 1447904.68 | 2071 | Plant on average load of 4.33MW | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-12 | 2026 | 3 | 12 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 98.7 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | No data submitted for this date | rekotohpc@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-03-12 | 2026 | 3 | 12 | Machai HPS | 2.6 | 1.5 | 0.39 | 8568 | 8400 | 16.3 | 17 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 39236.4 | 252234 | 168 | Unit remained still till 1733 hrs. due to governor maintenance. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-12 | 2026 | 3 | 12 | Malakand-3 HPS | 81 | 45 | 39.72 | 953251 | 945650 | 47.34 | 26.75 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2707112.26 | 2857976.54 | 7601 | Unit #03 desynchronized at 10:12 hrs. due to low hydrology and kept standby. Unit #02 synchronized at 11:05 hrs. as hydrology improved. Unit #03 synchronized at 13:07 hrs. as hydrology improved. Unit #01 desynchronized at 13:09 hrs. due to low hydrology and kept standby, As per available hydrology from the Irrigation Department, two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-12 | 2026 | 3 | 12 | Pehur HPS | 18 | 7.91 | 5.6 | 133900 | 130000 | 16.35 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 489710 | 1137634 | 3900 | The plant remained operational throughout 24 hours as per available hydrology & irrigation valve open. At 1230 hours unit #02 was taken off the bar due to low head restrictions, and unit #03 started and synchronized at 1455 hours. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-12 | 2026 | 3 | 12 | Reshun HPS | 4.2 | 2.28 | 0.97 | 23000 | 22425 | 1.41 | 1.5 | 50 | 13.48 | 47 | 45 | 47376 | 638628.48 | 302289 | 336339.48 | 575 | Outgoing feeder breaker tripped 2times due to lines faults and remained off 2times due to less hyddrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-13 | 2026 | 3 | 13 | Daral Khwar HPS | 36.6 | 19.1 | 16.8 | 403550 | 400750 | 4.76 | 6.7 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3313521.22 | 3949353.5 | 2800 | Unit No 02 and 03 were on bar delivering an average load equal to 16.8 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-13 | 2026 | 3 | 13 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. A 30-day shutdown permit has been obtained from the Executive Engineer, SS&TL, HAZECO Abbottabad, for the erection of collapsed Tower No. 29 and associated stringing works. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-03-13 | 2026 | 3 | 13 | Karora HPS | 11.8 | 5.9 | 5.9 | 139904 | 137884 | 7.35 | 4.85 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1072737.52 | 1130558.48 | 2020 | the plant was average load of 5.9 | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-13 | 2026 | 3 | 13 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 98.7 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant was shut down due to box channel repair work in progress from EPC contractor side. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-13 | 2026 | 3 | 13 | Machai HPS | 2.6 | 1.22 | 0.1 | 3476 | 3344 | 16 | 17 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 15619.82 | 275850.58 | 132 | Unit tripped twice, but remained still and under governor maintenance for the rest of the hours. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-13 | 2026 | 3 | 13 | Malakand-3 HPS | 81 | 44 | 40.83 | 979870 | 972600 | 47.34 | 27.06 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2784262.02 | 2780826.78 | 7270 | As per available hydrology from the Irrigation Department two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-13 | 2026 | 3 | 13 | Pehur HPS | 18 | 7.9 | 6.62 | 158800 | 156000 | 16.35 | 17.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 587652 | 1039692 | 2800 | Plant remained operational throughout 24 Hrs as per available hydrology & Irrigation valve open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-13 | 2026 | 3 | 13 | Reshun HPS | 4.2 | 1.65 | 0.98 | 23500 | 22912 | 1.41 | 1.48 | 23.31 | 13.48 | 47 | 45 | 47376 | 638628.48 | 308853.76 | 329774.72 | 588 | No data submitted for this date | zafar.src@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-03-14 | 2026 | 3 | 14 | Daral Khwar HPS | 36.6 | 15.6 | 13.1 | 315060 | 312260 | 4.76 | 5.22 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2581859.36 | 4681015.36 | 2800 | 1. Unit No 02 and 03 were on bar delivering an average load equal to 13.1 MW according to available hydrology. 2. Unit No 03 stopped at 2120 Hrs due to low hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-14 | 2026 | 3 | 14 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. A 30-day shutdown permit has been obtained from the Executive Engineer, SS&TL, HAZECO Abbottabad, for the erection of collapsed Tower No. 29 and associated stringing works. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-03-14 | 2026 | 3 | 14 | Karora HPS | 11.8 | 6.9 | 5.92 | 140607 | 138653 | 7.35 | 4.87 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1078720.34 | 1124575.66 | 1954 | unit#02 is on bar delivering 5.92MW to the system | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-14 | 2026 | 3 | 14 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 98.7 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remain shut down due to box channel repair work by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-14 | 2026 | 3 | 14 | Machai HPS | 2.6 | 1.43 | 0.71 | 11848 | 11572 | 1 | 22 | 100 | 4.671 | 33.33 | 70 | 20800 | 97156.8 | 54052.81 | 43103.99 | 276 | Unit synchronized with the system at 1503hrs unit tripped at 1643,2345hrs due to132kv line tripped , supply restored at 1701,2356hrs, while unit synchronized with system at 1711,0001hrs | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-14 | 2026 | 3 | 14 | Malakand-3 HPS | 81 | 45 | 40.85 | 980434 | 973390 | 47.34 | 27.09 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2786523.55 | 2778565.25 | 7044 | As per available hydrology from the Irrigation Department two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-14 | 2026 | 3 | 14 | Pehur HPS | 18 | 8 | 7.1 | 170500 | 166000 | 16.35 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 625322 | 1002022 | 4500 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-14 | 2026 | 3 | 14 | Reshun HPS | 4.2 | 2.25 | 1.04 | 24000 | 23400 | 1.41 | 1.47 | 49 | 13.48 | 47 | 45 | 47376 | 638628.48 | 315432 | 323196.48 | 600 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-15 | 2026 | 3 | 15 | Daral Khwar HPS | 36.6 | 13.8 | 12.9 | 312280 | 309480 | 4.76 | 5.18 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2558873.48 | 4704001.24 | 2800 | Unit No 02 was on bar delivering an average load equal to 13 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-15 | 2026 | 3 | 15 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. A 30-day shutdown permit has been obtained from the Executive Engineer, SS&TL, HAZECO Abbottabad, for the erection of collapsed Tower No. 29 and associated stringing works. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-03-15 | 2026 | 3 | 15 | Karora HPS | 11.8 | 6.9 | 5.92 | 140607 | 138653 | 7.35 | 4.87 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1078720.34 | 1124575.66 | 1954 | unit#02 is on bar delivering 5.92MW to national grid. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-15 | 2026 | 3 | 15 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 98.7 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant was shut down due to Box channel repair work in progress from EPC contractor side. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-15 | 2026 | 3 | 15 | Machai HPS | 2.6 | 1.4 | 1.26 | 31144 | 30316 | 17 | 22 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 141606.04 | 149864.36 | 828 | Unit tripped at 1645 due to 11 KV line tripping ant restored at 1654 while unit synched at 1701 | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-15 | 2026 | 3 | 15 | Malakand-3 HPS | 81 | 45 | 38.67 | 928120 | 920600 | 47.34 | 26.12 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2635401.62 | 2929687.18 | 7520 | As per available hydrology from the Irrigation Department Two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-15 | 2026 | 3 | 15 | Pehur HPS | 18 | 7.82 | 7.73 | 185400 | 182000 | 16.35 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 685594 | 941750 | 3400 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-15 | 2026 | 3 | 15 | Reshun HPS | 4.2 | 2.07 | 0.99 | 23000 | 22458 | 1.41 | 1.5 | 50 | 13.48 | 47 | 45 | 47376 | 638628.48 | 302733.84 | 335894.64 | 542 | Outgoing feeder breaker remained off 3times for 2.35hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-16 | 2026 | 3 | 16 | Daral Khwar HPS | 36.6 | 13.2 | 13.1 | 314210 | 311010 | 4.76 | 5.2 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2571523.98 | 4691350.74 | 3200 | Unit No 02 was on bar delivering an average load equal to 13.1 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-16 | 2026 | 3 | 16 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. A 30-day shutdown permit has been obtained from the Executive Engineer, SS&TL, HAZECO Abbottabad, for the erection of collapsed Tower No. 29 and associated stringing works. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-03-16 | 2026 | 3 | 16 | Karora HPS | 11.8 | 6.1 | 5.71 | 133309 | 131213 | 7.35 | 4.62 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1020837.14 | 1182458.86 | 2096 | unit#01 is unavailable for operation due to governor issues. unit#02 is on bar delivering average load 5.71 to the system. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-16 | 2026 | 3 | 16 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 98.7 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant was shut down due to box channel repair work in progress from EPC contractor side. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-16 | 2026 | 3 | 16 | Machai HPS | 2.6 | 1.45 | 1.24 | 30192 | 29480 | 19 | 19 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 137701.08 | 153769.32 | 712 | Normal Operation | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-16 | 2026 | 3 | 16 | Malakand-3 HPS | 81 | 45 | 42.21 | 1013122 | 1005440 | 47.34 | 27.86 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2878273.09 | 2686815.71 | 7682 | As per available hydrology from the Irrigation Department Two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-16 | 2026 | 3 | 16 | Pehur HPS | 18 | 7.78 | 7.65 | 183200 | 180000 | 16.35 | 19 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 678060 | 949284 | 3200 | Plant remained operational throughout 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-16 | 2026 | 3 | 16 | Reshun HPS | 4.2 | 2.31 | 0.94 | 23000 | 22438 | 1.41 | 1.5 | 50 | 13.48 | 47 | 45 | 47376 | 638628.48 | 302464.24 | 336164.24 | 562 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-17 | 2026 | 3 | 17 | Daral Khwar HPS | 36.6 | 12 | 11 | 263120 | 259920 | 4.76 | 4.35 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2149096.54 | 5113778.18 | 3200 | Unit No 02 was on bar delivering an average load equal to 11 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-17 | 2026 | 3 | 17 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. A 30-day shutdown permit has been obtained from the Executive Engineer, SS&TL, HAZECO Abbottabad, for the erection of collapsed Tower No. 29 and associated stringing works. The project authorities have yet to provide a restoration timeline for the damaged tower. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-03-17 | 2026 | 3 | 17 | Karora HPS | 11.8 | 6.5 | 5.88 | 139052 | 136946 | 7.35 | 4.52 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1065439.88 | 1137856.12 | 2106 | Unit #01 is on bar delivering an average load of 5.63MW as per the available hydrology over the last 11hours and Unit#02 on standby condition due to low hydrology. The total average station load for the last 24hours in 5.88MW. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-17 | 2026 | 3 | 17 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 98.7 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | Not reported | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-17 | 2026 | 3 | 17 | Machai HPS | 2.6 | 1.53 | 1.11 | 26304 | 25564 | 17 | 19 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 119409.44 | 172060.96 | 740 | Unit tripped twice at 0236 and 0604 due to tripping on 11 KV line while synced with system at 0327 and 0747 respectively. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-17 | 2026 | 3 | 17 | Malakand-3 HPS | 81 | 45 | 40.19 | 964613 | 956770 | 47.34 | 26.25 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2738945.48 | 2826143.32 | 7843 | Unit # 01 synchronized with the system at 10:17hrs & Unit # 03 desynchronized from the system at 10:18hrs due to less hydrology & kept standby & then Unit # 02 desynchronized from the system at 21:59hrs due to Rotor Ground Fault 64F & Unit # 03 synchronized with the system at 23:52Hrs now As per available hydrology from the Irrigation Department Two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-17 | 2026 | 3 | 17 | Pehur HPS | 18 | 7.73 | 7.67 | 184000 | 180000 | 16.35 | 19 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 678060 | 949284 | 4000 | Plant remained operational throughout 24 Hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-17 | 2026 | 3 | 17 | Reshun HPS | 4.2 | 2.4 | 0.95 | 22000 | 21420 | 1.41 | 1.34 | 44.67 | 13.48 | 47 | 45 | 47376 | 638628.48 | 288741.6 | 349886.88 | 580 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-18 | 2026 | 3 | 18 | Daral Khwar HPS | 36.6 | 11.5 | 11 | 264890 | 262090 | 4.76 | 4.38 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2167038.75 | 5095835.97 | 2800 | Unit No 02 was on bar delivering an average load equal to 11 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-18 | 2026 | 3 | 18 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 19.03.2026 to 07.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-03-18 | 2026 | 3 | 18 | Karora HPS | 11.8 | 5.9 | 5.73 | 135959 | 133772 | 7.35 | 4.32 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1040746.16 | 1162549.84 | 2187 | Unit#01 is on bar delivering an average load of 5.73 MW as per the available hydrology. Unit#02 on standby condition due to low hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-18 | 2026 | 3 | 18 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 98.7 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | Not reported | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-18 | 2026 | 3 | 18 | Machai HPS | 2.6 | 1.28 | 0.63 | 16080 | 15532 | 17 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 72549.97 | 218920.43 | 548 | Unit tripped at 0740 and 1308 hours due to 11 kv line tripping from Katlang Grid 11 KV line restored at 0901 and 1325 hours. Unit synchronized with system at 0951 and 1608 hours respectively Unit stop normally at 20:53 hours due to low hydrology in canal because of weekly canal closure started on 18th March 2026 | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-18 | 2026 | 3 | 18 | Malakand-3 HPS | 81 | 42 | 37.79 | 906898 | 899060 | 47.34 | 25.62 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2573739.06 | 2991349.74 | 7838 | As per available hydrology from the Irrigation Department two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-18 | 2026 | 3 | 18 | Pehur HPS | 18 | 7.77 | 7.26 | 174300 | 169000 | 16.35 | 19 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 636623 | 990721 | 5300 | Unit# 03 was taken off the bar at 2206 Hrs as per request of irrigation SDO to reduce the discharge up to 6 cms in the canal. Unit# 01 is on bar with 2.80 MW. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-18 | 2026 | 3 | 18 | Reshun HPS | 4.2 | 2.26 | 0.96 | 26000 | 25410 | 1.41 | 1.59 | 53 | 13.48 | 47 | 45 | 47376 | 638628.48 | 342526.8 | 296101.68 | 590 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-19 | 2026 | 3 | 19 | Daral Khwar HPS | 36.6 | 15.3 | 13.3 | 318790 | 316390 | 4.76 | 5.29 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2616007.44 | 4646867.28 | 2400 | Unit No 02 was on bar delivering an average load equal to 13.3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-19 | 2026 | 3 | 19 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 19.03.2026 to 07.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-03-19 | 2026 | 3 | 19 | Karora HPS | 11.8 | 11.7 | 6.47 | 153643 | 151456 | 7.35 | 4.96 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1178327.68 | 1024968.32 | 2187 | Unit#01 has been on bar since 13:43hrs on 17-03-2026,delivering an average load of 4.58MW; performance and issues are under strict observation. Both units on bar delivering a combined average load of 6.47MW. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-19 | 2026 | 3 | 19 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 98.8 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | Not reported | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-19 | 2026 | 3 | 19 | Machai HPS | 2.6 | 0.55 | 0.45 | 7156 | 6820 | 1 | 14 | 100 | 4.671 | 33.33 | 70 | 20800 | 97156.8 | 31856.22 | 65300.58 | 336 | Unit start and synchronized with the system at 1035hrs | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-19 | 2026 | 3 | 19 | Malakand-3 HPS | 81 | 46 | 41.72 | 1001271 | 993460 | 47.34 | 27.2 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2843977.94 | 2721110.86 | 7811 | As per available hydrology from the Irrigation Department two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-19 | 2026 | 3 | 19 | Pehur HPS | 18 | 3.39 | 3.07 | 73600 | 70000 | 16.35 | 7 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 263690 | 1363654 | 3600 | Plant remained throughout 24 hrs with restricted flow in the canal. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-19 | 2026 | 3 | 19 | Reshun HPS | 4.2 | 2.3 | 0.94 | 17000 | 16420 | 1.41 | 1.01 | 33.67 | 13.48 | 47 | 45 | 47376 | 638628.48 | 221341.6 | 417286.88 | 580 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-20 | 2026 | 3 | 20 | Daral Khwar HPS | 36.6 | 13.5 | 12.5 | 299430 | 296630 | 4.76 | 4.96 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2452625.83 | 4810248.89 | 2800 | Unit No 02 was on bar delivering an average load equal to 12.5 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-20 | 2026 | 3 | 20 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 19.03.2026 to 07.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-03-20 | 2026 | 3 | 20 | Karora HPS | 11.8 | 10.1 | 7.88 | 197458 | 195271 | 7.35 | 3.24 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1519208.38 | 684087.62 | 2187 | Units#01 has been on bar since 13:43hrs on 17-03-2026, delivering an average load of 3.79MW; performance and issues are under strict observation. Both units on bar delivering a combined average load of 7.88MW. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-20 | 2026 | 3 | 20 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 98.7 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remain shut down due to Box Channel repair works by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-20 | 2026 | 3 | 20 | Machai HPS | 2.6 | 0.55 | 0.51 | 12400 | 11836 | 16.2 | 14 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 55285.96 | 236184.44 | 564 | Unit on bar and delivering power to the National Grid accordance with available water inflow and prevailing system conditions. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-20 | 2026 | 3 | 20 | Malakand-3 HPS | 81 | 46 | 41.67 | 1000026 | 992550 | 47.34 | 27.68 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2841372.88 | 2723715.92 | 7476 | As per available hydrology from the Irrigation Department two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-20 | 2026 | 3 | 20 | Pehur HPS | 18 | 3.56 | 3.4 | 82100 | 79000 | 16.35 | 9 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 297593 | 1329751 | 3100 | Plant remained operational throughout 24 Hrs with restricted flow in the canal from irrigation department. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-20 | 2026 | 3 | 20 | Reshun HPS | 4.2 | 1.16 | 0.8 | 22000 | 21422 | 1.41 | 1.34 | 44.67 | 13.48 | 47 | 45 | 47376 | 638628.48 | 288768.56 | 349859.92 | 578 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-21 | 2026 | 3 | 21 | Daral Khwar HPS | 36.6 | 12 | 11.2 | 268810 | 266010 | 4.76 | 4.45 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2199450.48 | 5063424.24 | 2800 | 1. Unit No 02 was on bar delivering an average load equal to 11.2 MW according to available hydrology. 2. Unit No 02 tripped due to frequency fluctuation at 0740 Hrs and was synchronized with the national grid at 0759 Hrs. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-21 | 2026 | 3 | 21 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 0 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | No data submitted for this date | faizanbabar5@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-03-21 | 2026 | 3 | 21 | Karora HPS | 11.8 | 6.4 | 5.91 | 141934 | 139512 | 10 | 4.57 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1085403.36 | 1117892.64 | 2422 | Unit#01 has been on bar since 13:43 hrs on 17-03-2026, delivering an average load of 4.45MW; performance and issues are under strict observation. Both on bar delivering a combined average load of 5.91MW. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-21 | 2026 | 3 | 21 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 98.7 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The Plant remain shut down due to Box Channel repair works by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-21 | 2026 | 3 | 21 | Machai HPS | 2.6 | 0.63 | 0.48 | 11640 | 11000 | 16.2 | 14 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 51381 | 240089.4 | 640 | Unit tripped at 2004hrs due to 11KV Machai HPS line tripping from Katlang Grid by Earth-fault. 11 KV Machai HPS line restored at 2009hrs and Unit synchronised with the system at 2030hrs. Unit tripped due to MLDT fault at 2039hrs and synchronised at 2124hrs. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-21 | 2026 | 3 | 21 | Malakand-3 HPS | 81 | 43 | 41.37 | 992940 | 985790 | 47.34 | 27.89 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2822021.03 | 2743067.77 | 7150 | As per available hydrology from the Irrigation Department two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-21 | 2026 | 3 | 21 | Pehur HPS | 18 | 3.56 | 3.5 | 83900 | 80000 | 16.35 | 8 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 301360 | 1325984 | 3900 | The plant remained operational throughout 24 hrs as per irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-21 | 2026 | 3 | 21 | Reshun HPS | 4.2 | 1.65 | 0.86 | 1900 | 18400 | 1.41 | 1.19 | 39.67 | 13.48 | 47 | 45 | 47376 | 638628.48 | 248032 | 390596.48 | 16500 | Less Hydrology. | zafar.src@gmail.com | Original | CHECK: Net > Units (source me verify karein) | Link_Generation_Data_Summary.xlsx
2026-03-22 | 2026 | 3 | 22 | Daral Khwar HPS | 36.6 | 11.3 | 10.3 | 247940 | 245540 | 4.76 | 4.11 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2030198.38 | 5232676.34 | 2400 | Unit No 02 was on bar delivering an average load equal to 10.3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-22 | 2026 | 3 | 22 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 19.03.2026 to 07.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-03-22 | 2026 | 3 | 22 | Karora HPS | 11.8 | 5.9 | 5.85 | 137410 | 135680 | 7.35 | 4.39 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1055590.4 | 1147705.6 | 1730 | Unit#01 has been on bar since 13:43hrs on 17-03-2026, delivering an average load 5.85MW; performance and issues are under strict observation. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-22 | 2026 | 3 | 22 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 98.7 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The Plant remain shut down due to Box Channel repair works by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-22 | 2026 | 3 | 22 | Machai HPS | 2.6 | 0.67 | 0.57 | 14112 | 13596 | 16.2 | 14 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 63506.92 | 227963.48 | 516 | Unit tripped at 1818hrs due to 11KV Machai HPS line tripping from Katlang Grid by Earth-fault. 11 KV Machai HPS line restored at 1820hrs and Unit synchronised with the system at 1842hrs. Unit tripped due to MLDT fault at 1847hrs and synchronised at 1853hrs. Unit tripped due to Governor Tank pressure fail fault at 2157hrs and synchronised at 2208hrs. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-22 | 2026 | 3 | 22 | Malakand-3 HPS | 81 | 44 | 41.22 | 989296 | 982250 | 47.34 | 27.6 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2811887.08 | 2753201.72 | 7046 | As per available hydrology from the Irrigation Department two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-22 | 2026 | 3 | 22 | Pehur HPS | 18 | 3.91 | 3.65 | 87600 | 84000 | 16.35 | 8 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 316428 | 1310916 | 3600 | Plant operational 24 hrs with restriced flow of 8 cms due to low irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-22 | 2026 | 3 | 22 | Reshun HPS | 4.2 | 1.66 | 0.82 | 18000 | 17404 | 1.41 | 1.1 | 36.67 | 13.48 | 47 | 45 | 47376 | 638628.48 | 234605.92 | 404022.56 | 596 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-23 | 2026 | 3 | 23 | Daral Khwar HPS | 36.6 | 10.5 | 10.4 | 249920 | 247520 | 4.76 | 4.14 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2046569.62 | 5216305.1 | 2400 | Unit No 02 was on bar delivering an average load equal to 10.4 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-23 | 2026 | 3 | 23 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 19.03.2026 to 07.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-03-23 | 2026 | 3 | 23 | Karora HPS | 11.8 | 5.9 | 5.78 | 136542 | 134762 | 7.35 | 4.34 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1048448.36 | 1154847.64 | 1780 | Unit#01 has been on bar since 13:43hrs on 17-03-2026,delivering an average load of 5.78MW;performance and issues are under strict observation. Unit#02 is standby condition due to low hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-23 | 2026 | 3 | 23 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 98.7 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The Plant remain shut down due to Box Channel repair works by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-23 | 2026 | 3 | 23 | Machai HPS | 2.6 | 0.64 | 0.58 | 14312 | 13596 | 16.2 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 63506.92 | 227963.48 | 716 | Unit on bar and delivering power to the National Grid accordance with available water inflow and prevailing system conditions. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-23 | 2026 | 3 | 23 | Malakand-3 HPS | 81 | 44 | 40.66 | 975890 | 968950 | 47.34 | 27.25 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2773813.16 | 2791275.64 | 6940 | As per available hydrology from the Irrigation Department two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-23 | 2026 | 3 | 23 | Pehur HPS | 18 | 7.32 | 5.31 | 127500 | 124000 | 16.35 | 15 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 467108 | 1160236 | 3500 | Plant remained operational throughout 24 hrs as per available hydrology and irrigation valve is open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-23 | 2026 | 3 | 23 | Reshun HPS | 4.2 | 2.01 | 0.89 | 20000 | 19402 | 1.41 | 1.22 | 40.8 | 13.48 | 47 | 45 | 47376 | 638628.48 | 261538.96 | 377089.52 | 598 | Less hydrology, 1.4hours loadshedding has been observed. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-24 | 2026 | 3 | 24 | Daral Khwar HPS | 36.6 | 12.5 | 10.5 | 252890 | 250490 | 4.76 | 4.19 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2071126.47 | 5191748.25 | 2400 | Unit No 02 was on bar delivering an average load equal to 10.5 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-24 | 2026 | 3 | 24 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 19.03.2026 to 07.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-03-24 | 2026 | 3 | 24 | Karora HPS | 11.8 | 5.8 | 5.22 | 125369 | 123657 | 10 | 3.96 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 962051.46 | 1241244.54 | 1712 | the plant was operational on average load 5.22MW and maximum load 5.8MW as per hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-24 | 2026 | 3 | 24 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 98.7 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The Plant remain shut down due to Box Channel repair works by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-24 | 2026 | 3 | 24 | Machai HPS | 2.6 | 0.6 | 0.52 | 12000 | 11444 | 1 | 14 | 100 | 4.671 | 33.33 | 70 | 20800 | 97156.8 | 53454.92 | 43701.88 | 556 | unit stopped at 1111hrs due to low inflow and less water level, while back unit synch with the system at 1153hrs. unit tripped at 1209hrs due to revers power, unit synch with the system at 1237hrs. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-24 | 2026 | 3 | 24 | Malakand-3 HPS | 81 | 40 | 35.45 | 850837 | 843430 | 47.34 | 24.51 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2414487.06 | 3150601.74 | 7407 | As per available hydrology from the Irrigation Department two units are on bar. Load variation occurs due to variation in hydrology in swat river. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-24 | 2026 | 3 | 24 | Pehur HPS | 18 | 6.8 | 6.6 | 158900 | 156000 | 16.35 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 587652 | 1039692 | 2900 | Unit # 01 and 03 on bar along with irrigation valve open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-24 | 2026 | 3 | 24 | Reshun HPS | 4.2 | 2.25 | 0.83 | 20000 | 19406 | 1.41 | 1.22 | 40.67 | 13.48 | 47 | 45 | 47376 | 638628.48 | 261592.88 | 377035.6 | 594 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-25 | 2026 | 3 | 25 | Daral Khwar HPS | 36.6 | 13.5 | 11.9 | 284860 | 282060 | 4.76 | 4.72 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2332156.7 | 4930718.02 | 2800 | Unit No 02 was on bar delivering an average load equal to 11.9 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-25 | 2026 | 3 | 25 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 19.03.2026 to 07.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-03-25 | 2026 | 3 | 25 | Karora HPS | 11.8 | 5.12 | 4.84 | 113359 | 111732 | 10 | 3.62 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 869274.96 | 1334021.04 | 1627 | the plant was operational on average 4.84mw as per available hydrology | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-25 | 2026 | 3 | 25 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 98.7 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The Plant remain shut down due to Box Channel repair works by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-25 | 2026 | 3 | 25 | Machai HPS | 2.6 | 2.01 | 0.71 | 14112 | 13504 | 17 | 16 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 63077.18 | 228393.22 | 608 | Unit tripped thrice. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-25 | 2026 | 3 | 25 | Malakand-3 HPS | 81 | 35 | 32.68 | 784412 | 776840 | 47.34 | 22.9 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2223859.87 | 3341228.93 | 7572 | As per available hydrology from the Irrigation Department two units are on bar. Load variation occurs due to variation in hydrology in swat river. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-25 | 2026 | 3 | 25 | Pehur HPS | 18 | 7.7 | 6.99 | 167900 | 163000 | 16.35 | 18.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 614021 | 1013323 | 4900 | Plant remained operational throughout 24 Hrs as per available hydrology and irrigation valve open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-25 | 2026 | 3 | 25 | Reshun HPS | 4.2 | 2.18 | 0.84 | 19000 | 18435 | 1.41 | 1.16 | 38.67 | 13.48 | 47 | 45 | 47376 | 638628.48 | 248503.8 | 390124.68 | 565 | Outgoing feeder breaker remained off 2hours due to less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-26 | 2026 | 3 | 26 | Daral Khwar HPS | 36.6 | 14.5 | 13.4 | 322230 | 319830 | 4.76 | 5.35 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2644450.39 | 4618424.33 | 2400 | Unit No 02 was on bar delivering an average load equal to 13.4 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-26 | 2026 | 3 | 26 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 19.03.2026 to 07.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-03-26 | 2026 | 3 | 26 | Karora HPS | 11.8 | 10.9 | 4.8 | 116945 | 115021 | 10 | 3.92 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 894863.38 | 1308432.62 | 1924 | the plant average load of 4.80mw | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-26 | 2026 | 3 | 26 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 98.7 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remain shut down due to box channel repair work by EPC contractor | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-26 | 2026 | 3 | 26 | Machai HPS | 2.6 | 0.83 | 0.73 | 17736 | 17028 | 18 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 79537.79 | 211932.61 | 708 | Unit tripped once due to 11 KV line tripping. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-26 | 2026 | 3 | 26 | Malakand-3 HPS | 81 | 36 | 32.98 | 791562 | 784020 | 47.34 | 23.18 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2244414.05 | 3320674.75 | 7542 | As per available hydrology from the Irrigation Department two units are on bar.Load variation occurs due to variation in hydrology in swat river | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-26 | 2026 | 3 | 26 | Pehur HPS | 18 | 7.71 | 6.63 | 159100 | 156000 | 16.35 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 587652 | 1039692 | 3100 | Plant remained operational as per available hydrology and Unit# 01 & 03 Tripped twice , at 0654 Hrs and again at 1132 Hrs due to tripping of 132 KV line supply. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-26 | 2026 | 3 | 26 | Reshun HPS | 4.2 | 2.18 | 0.84 | 18000 | 17410 | 1.41 | 1.1 | 36.67 | 13.48 | 47 | 45 | 47376 | 638628.48 | 234686.8 | 403941.68 | 590 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-27 | 2026 | 3 | 27 | Daral Khwar HPS | 36.6 | 14.5 | 13.4 | 322230 | 319830 | 4.76 | 5.35 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2644450.39 | 4618424.33 | 2400 | Unit No 02 was on bar delivering an average load equal to 13.4 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-27 | 2026 | 3 | 27 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 19.03.2026 to 07.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-03-27 | 2026 | 3 | 27 | Karora HPS | 11.8 | 11.8 | 10.15 | 239913 | 237032 | 10 | 8 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1844108.96 | 359187.04 | 2881 | the plant was operational average load of 10.15me as per available hydrology | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-27 | 2026 | 3 | 27 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 98.7 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant reman shut down due to box channel repair work by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-27 | 2026 | 3 | 27 | Machai HPS | 2.6 | 1.22 | 0.74 | 16836 | 16192 | 22 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 75632.83 | 215837.57 | 644 | Unit tripped twice due to 11 KV line tripping. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-27 | 2026 | 3 | 27 | Malakand-3 HPS | 81 | 43 | 37.37 | 896767 | 889420 | 47.34 | 25.54 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2546142.63 | 3018946.17 | 7347 | As per available hydrology from the Irrigation Department Two units are on bar. Load variation occurs due to variation in hydrology in swat river. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-27 | 2026 | 3 | 27 | Pehur HPS | 18 | 7.11 | 6.68 | 160400 | 156500 | 16.35 | 17.5 | 37.13 | 3.767 | 100 | 41 | 432000 | 1627344 | 589535.5 | 1037808.5 | 3900 | No data submitted for this date | phpcmw18@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-03-27 | 2026 | 3 | 27 | Reshun HPS | 4.2 | 2.08 | 0.22 | 20000 | 19431 | 1.41 | 1.22 | 40.67 | 13.48 | 47 | 45 | 47376 | 638628.48 | 261929.88 | 376698.6 | 569 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-28 | 2026 | 3 | 28 | Daral Khwar HPS | 36.6 | 18.5 | 17 | 406830 | 403230 | 4.76 | 6.74 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3334026.61 | 3928848.11 | 3600 | Unit No 02 was on bar delivering an average load equal to 17 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-28 | 2026 | 3 | 28 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 19.03.2026 to 07.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-03-28 | 2026 | 3 | 28 | Karora HPS | 11.8 | 11.8 | 11.22 | 266555 | 263759 | 10 | 8.84 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 2052045.02 | 151250.98 | 2796 | Unit 01 & 02 on bar at average load s of 5.73MW & 5.49MW, respectively, as per available hydrology. Both units remain under close observation due to governor & protection system issues, with defects reported for rectification. The cooling water system issue remains unresolved. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-28 | 2026 | 3 | 28 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 98.7 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remain was shut down due to box channel repair works by EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-28 | 2026 | 3 | 28 | Machai HPS | 2.6 | 1.1 | 0.9 | 21272 | 20592 | 22 | 15 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 96185.23 | 195285.17 | 680 | Unit tripped 03 times, due to 11 KV line tripping. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-28 | 2026 | 3 | 28 | Malakand-3 HPS | 81 | 43 | 39.4 | 945596 | 938380 | 47.4 | 26.76 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2686300.43 | 2878788.37 | 7216 | As per available hydrology from the Irrigation Department Two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-28 | 2026 | 3 | 28 | Pehur HPS | 18 | 7.59 | 6.7 | 161700 | 157000 | 16.35 | 17 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 591419 | 1035925 | 4700 | Unit#03 is taken off the bar at 1935 Hrs dt. 28-03-26 due to low irrigation demand as per instruction of irrigation SDO. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-28 | 2026 | 3 | 28 | Reshun HPS | 4.2 | 2.05 | 0.8 | 19000 | 18436 | 1.41 | 1.16 | 38.67 | 13.48 | 47 | 45 | 47376 | 638628.48 | 248517.28 | 390111.2 | 564 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-29 | 2026 | 3 | 29 | Daral Khwar HPS | 36.6 | 27 | 22.9 | 549730 | 546530 | 4.76 | 9.14 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 4518874 | 2744000.72 | 3200 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 22.9 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-29 | 2026 | 3 | 29 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 19.03.2026 to 07.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-03-29 | 2026 | 3 | 29 | Karora HPS | 11.8 | 11.7 | 9.36 | 228566 | 225859 | 10 | 7.28 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1757183.02 | 446112.98 | 2707 | unit 01and unit 02on bar average load of 4.42mw and 4.94mw respectively as per available hydrology both units remain under close observation due to governor and protection system issues with defects reported for rectification the cooling water system issue remains unresolved | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-29 | 2026 | 3 | 29 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 98.6 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | Not reported | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-29 | 2026 | 3 | 29 | Machai HPS | 2.6 | 1.03 | 0.88 | 20964 | 20284 | 1 | 17 | 100 | 4.671 | 33.33 | 70 | 20800 | 97156.8 | 94746.56 | 2410.24 | 680 | Unit tripped at 1330hrs due to 11kv line tripped, and back restored at 1336hrs, while Unit synchronized with the system at 1353hrs. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-29 | 2026 | 3 | 29 | Malakand-3 HPS | 81 | 44 | 40.02 | 960502 | 953290 | 47.34 | 26.65 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2728983.28 | 2836105.52 | 7212 | As per available hydrology from the Irrigation Department Two units are on bar. Load variation occurs due to variation in hydrology in swat river. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-29 | 2026 | 3 | 29 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 16.35 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | Plant remained shutdown since 0000 Hrs dated 29-03-2026 due to nil irrigation demand (Heavy rainfall) as per instructions of irrigation SDO. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-29 | 2026 | 3 | 29 | Reshun HPS | 4.2 | 2.05 | 0.84 | 17000 | 16440 | 1.41 | 1.04 | 34.67 | 13.48 | 47 | 45 | 47376 | 638628.48 | 221611.2 | 417017.28 | 560 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-30 | 2026 | 3 | 30 | Daral Khwar HPS | 36.6 | 36.6 | 33.3 | 800020 | 796420 | 4.76 | 13.32 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6585039.49 | 677835.23 | 3600 | Unit No 02 was on bar delivering an average load equal to 33.3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-30 | 2026 | 3 | 30 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 19.03.2026 to 07.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-03-30 | 2026 | 3 | 30 | Karora HPS | 11.8 | 11.8 | 4.62 | 112192 | 110429 | 10 | 3.59 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 859137.62 | 1344158.38 | 1763 | 1) Unit#01and Unit#02 on bar average load of 2.50MW and 2.12MW respectively as per available hydrology ,both units on bar delivering a combined average load 4.62MW. 2) Both units remain under close observation due to governor and protection system issues with defects reported for rectification the cooling water system issue remains unresolved. 3) The complex was shut down at 11:02 hrs as a preventive measure due to severe weather conditions to avoid potential equipment damage and ensure the safety and operational integrity of the plant. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-30 | 2026 | 3 | 30 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 98.7 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remain shutdown due to repair work in Box Channel by EPC CONTRACTOR. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-30 | 2026 | 3 | 30 | Machai HPS | 2.6 | 0.95 | 0.45 | 11592 | 11088 | 17 | 17 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 51792.05 | 239678.35 | 504 | Unit was shutdown at 1452 hrs as a precautionary measure following a significant drop in headrace level due to decreased canal discharge by the Irrigation Department. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-30 | 2026 | 3 | 30 | Malakand-3 HPS | 81 | 45 | 39.88 | 957113 | 949720 | 47.34 | 27.85 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2718763.44 | 2846325.36 | 7393 | As per available hydrology from the Irrigation Department two units are on bar. Load variation occurs due to variation in the hydrology of River Swat. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-30 | 2026 | 3 | 30 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 16.35 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | Plant remained shutdown since 0000 Hrs dated 29-03-2026 due to nil irrigation demand (Heavy rainfall) as per instructions of irrigation SDO. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-30 | 2026 | 3 | 30 | Reshun HPS | 4.2 | 2.04 | 0.78 | 19000 | 18435 | 1.41 | 1.16 | 38.67 | 13.48 | 47 | 45 | 47376 | 638628.48 | 248503.8 | 390124.68 | 565 | Line faults and less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-31 | 2026 | 3 | 31 | Daral Khwar HPS | 36.6 | 36.6 | 35.2 | 845900 | 841900 | 4.76 | 14.08 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6961081.77 | 301792.95 | 4000 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 35.2 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-31 | 2026 | 3 | 31 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 6.7 | 4.12 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 19.03.2026 to 07.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with overall median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-03-31 | 2026 | 3 | 31 | Karora HPS | 11.8 | 11.8 | 4.65 | 101951 | 100648 | 10 | 3.67 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 783041.44 | 1420254.56 | 1303 | 1) Unit#01and Unit#02 on bar average load of 2.21MW and 2.44MW respectively as per available hydrology ,both units on bar delivering a combined average load 4.65MW. 2) Both units remain under close observation due to governor and protection system issues with defects reported for rectification the cooling water system issue remains unresolved. 3) Unit#02 and Unit#01 were synchronized with the grid at 14:32Hrs and 15:53Hrs respectively, after completing trash rack cleaning and sand trap flushing. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-31 | 2026 | 3 | 31 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 98.6 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | Not reported | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-31 | 2026 | 3 | 31 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.671 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | Unit standstill due to low hydrology in canal due to canal closure by irrigation at 30-03-2026 | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-31 | 2026 | 3 | 31 | Malakand-3 HPS | 81 | 43 | 37.85 | 908414 | 900980 | 47.34 | 26.41 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2579235.45 | 2985853.35 | 7434 | As per available hydrology from the Irrigation Department two units are on bar, Load variation occurs due to variation in the hydrology of River Swat. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-31 | 2026 | 3 | 31 | Pehur HPS | 18 | 3.39 | 1.69 | 40500 | 39000 | 16.35 | 4 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 146913 | 1480431 | 1500 | At 1112 Hrs, Unit # 01 synchronized with 3.30 MW load against restricted flow of 06 cms. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-03-31 | 2026 | 3 | 31 | Reshun HPS | 4.2 | 1.97 | 0.87 | 17000 | 16441 | 1.41 | 1.01 | 33.67 | 13.48 | 47 | 45 | 47376 | 638628.48 | 221624.68 | 417003.8 | 559 | Line faults and less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-01 | 2026 | 4 | 1 | Daral Khwar HPS | 36.6 | 30 | 26 | 623850 | 620250 | 14.17 | 10.37 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 5128413.08 | 2134461.64 | 3600 | 1. Unit No 01, 02 and 03 were on bar delivering an average load equal to 26 MW according to available hydrology. 2. Unit No 01 stopped at 11:25 Hrs due to low hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-01 | 2026 | 4 | 1 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 2.66 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 19.03.2026 to 07.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-04-01 | 2026 | 4 | 1 | Karora HPS | 11.8 | 11.8 | 11.8 | 281013 | 279165 | 10.11 | 9.3 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 2171903.7 | 31392.3 | 1848 | 1) UNIT#01 and Unit#02 are on bar, collectively delivering an average load of 11.8MW as per the available hydrology. 2) Rectification works mainly related to the SCADA system, Governor, Cooling water system and protection system as identified in the punch list, are still pending. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-01 | 2026 | 4 | 1 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 177.7 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant is shutdown due box channel repair | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-01 | 2026 | 4 | 1 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0.33 | 2 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Unit stand still due to canal closure from irrigation department on 30-03-2026 | machai.12333@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load; Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2026-04-01 | 2026 | 4 | 1 | Malakand-3 HPS | 81 | 44 | 38.52 | 924451 | 916900 | 51 | 26.27 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2624809.63 | 2940279.17 | 7551 | As per available hydrology from the Irrigation Department two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-01 | 2026 | 4 | 1 | Pehur HPS | 18 | 3.4 | 3.3 | 80700 | 77000 | 12.12 | 8 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 290059 | 1337285 | 3700 | Unit#01 is on the bar with 3.3 MW load with restricted flow. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-01 | 2026 | 4 | 1 | Reshun HPS | 4.2 | 2.02 | 0.82 | 19000 | 18433 | 1.21 | 1.16 | 38.67 | 13.48 | 40.33 | 45 | 40656 | 548042.88 | 248476.84 | 299566.04 | 567 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-02 | 2026 | 4 | 2 | Daral Khwar HPS | 36.6 | 25 | 21.5 | 515030 | 512230 | 14.17 | 8.57 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 4235271.31 | 3027603.41 | 2800 | Unit No 02 and 03 were on bar delivering an average load equal to 21.5 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-02 | 2026 | 4 | 2 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 2.66 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 19.03.2026 to 07.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-04-02 | 2026 | 4 | 2 | Karora HPS | 11.8 | 11.85 | 11.82 | 279926 | 278005 | 10.11 | 9.29 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 2162878.9 | 40417.1 | 1921 | 1) Unit#01 and Unit#02 are on bar, collectively delivering an average load of 11.8MW as per the available hydrology. 2) Rectification works mainly related to the SCADA system, Governor, Cooling water system and protection system as identified in the punch list, are still pending. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-02 | 2026 | 4 | 2 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 177.7 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | After completion of civil repair works of Box Channel, Unit No.3 started on Heat Run at 05:18 pm dated 02-04-2026. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-02 | 2026 | 4 | 2 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0.67 | 4 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Unit standstill due to low water inflow in canal due to canal closure by irrigation department on 30-03-2026 | machai.12333@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load; Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Link_Generation_Data_Summary.xlsx
2026-04-02 | 2026 | 4 | 2 | Malakand-3 HPS | 81 | 42 | 38.6 | 926302 | 918880 | 51 | 25.88 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2630477.78 | 2934611.02 | 7422 | As per available hydrology from the Irrigation Department two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-02 | 2026 | 4 | 2 | Pehur HPS | 18 | 3.5 | 3.4 | 81700 | 78000 | 12.12 | 8.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 293826 | 1333518 | 3700 | Unit#01 is on the bar with 3.5 MW load with restricted flow. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-02 | 2026 | 4 | 2 | Reshun HPS | 4.2 | 2.02 | 0.86 | 20000 | 19439 | 1.21 | 1.24 | 41.33 | 13.48 | 40.33 | 45 | 40656 | 548042.88 | 262037.72 | 286005.16 | 561 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-03 | 2026 | 4 | 3 | Daral Khwar HPS | 36.6 | 36.6 | 27.8 | 667330 | 663730 | 14.17 | 11.1 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 5487918.76 | 1774955.96 | 3600 | 1. Unit No 01, 02 and 03 were on bar delivering an average load equal to 27.8 MW according to available hydrology. 2. Unit No 01 was synchronized with the national grid at 12:04 Hrs due to increased hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-03 | 2026 | 4 | 3 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 2.66 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 19.03.2026 to 07.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-04-03 | 2026 | 4 | 3 | Karora HPS | 11.8 | 11.84 | 11.82 | 279549 | 277534 | 10.11 | 9.3 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 2159214.52 | 44081.48 | 2015 | 1) Unit#01 and Unit#02 are on bar, collectively delivering an average load of 11.8MW as per the available hydrology. 2) Rectification works mainly related to the SCADA system, Governor, Cooling water system and protection system as identified in the punch list, are still pending. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-03 | 2026 | 4 | 3 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 177.7 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | Due to flooding at the intake site, Sarwar Camp, and batching plant area, the situation is currently critical. The site team requested the opening of the undersluice gates for protection purposes. Following the opening of the undersluice gates, the available head became insufficient for unit operation. Accordingly, the EPC Contractor instructed the CCR to shut down the plant. All three generating units are shut down Under sluice gates are open Intake gates are closed. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-03 | 2026 | 4 | 3 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 1 | 6 | 100 | 4.671 | 33.33 | 70 | 20800 | 97156.8 | 0 | 97156.8 | 0 | Unit stand still due to low inflow and less water level in irrigation canal, because of stormy weather. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-03 | 2026 | 4 | 3 | Malakand-3 HPS | 81 | 43 | 35.84 | 860216 | 852430 | 51 | 24.2 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2440251.36 | 3124837.44 | 7786 | As per available hydrology from the Irrigation Department two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-03 | 2026 | 4 | 3 | Pehur HPS | 18 | 3.45 | 2.3 | 55400 | 53000 | 12.12 | 6 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 199651 | 1427693 | 2400 | Plant shut down at 1610 hrs due to nil demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-03 | 2026 | 4 | 3 | Reshun HPS | 4.2 | 2 | 0.84 | 19000 | 18445 | 1.21 | 1.16 | 38.67 | 13.48 | 40.33 | 45 | 40656 | 548042.88 | 248638.6 | 299404.28 | 555 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-04 | 2026 | 4 | 4 | Daral Khwar HPS | 36.6 | 32.3 | 30.5 | 732190 | 727790 | 14.17 | 12.17 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6017586.06 | 1245288.66 | 4400 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 30.5 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-04 | 2026 | 4 | 4 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 2.66 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 19.03.2026 to 07.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-04-04 | 2026 | 4 | 4 | Karora HPS | 11.8 | 11.82 | 9.27 | 219912 | 218072 | 10.11 | 7.3 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1696600.16 | 506695.84 | 1840 | 1: Unit # 01 and 02 are on bar, collectively delivering an average load of 9.27MW as per the available hydrology. 2: A complex shutdown was carried out from 17:19 hrs to 22:13 hrs due to severe weather condition to prevent equipment damage and ensure the safety and operational integrity of the plant. 3: Rectification works mainly related to the SCADA System, Governor, Cooling Water System and Protection System as identified in the punch list, are still pending | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-04 | 2026 | 4 | 4 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 177.7 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | Due to the recent flood surge and in accordance with the contractor’s directives, it is mandatory to conduct Insulation Resistance (IR) testing on all generators before they are put under load. Consequently, all units are currently offline. The Koto Hydropower Plant units will be synchronized and brought back onto the grid as soon as these tests are successfully completed. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-04 | 2026 | 4 | 4 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 23.8 | 6 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Unit standstill due to low water inflow in canal due to weekly canal closure by irrigation department | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-04 | 2026 | 4 | 4 | Malakand-3 HPS | 81 | 44 | 38.92 | 933964 | 926650 | 51 | 26.28 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2652720.96 | 2912367.84 | 7314 | As per available hydrology from the Irrigation Department two units are on bar. Load variation occurs due to variation in the hydrology of River Swat. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-04 | 2026 | 4 | 4 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 12.12 | 0 | 0 | 3.767 | 100 | 41 | 432000 | 1627344 | 0 | 1627344 | 0 | The plant remained shut down throughout 24 hrs due to nil irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-04 | 2026 | 4 | 4 | Reshun HPS | 4.2 | 2.14 | 0.81 | 16000 | 15447 | 1.21 | 0.97 | 32.33 | 13.48 | 40.33 | 45 | 40656 | 548042.88 | 208225.56 | 339817.32 | 553 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-05 | 2026 | 4 | 5 | Daral Khwar HPS | 36.6 | 28 | 24.2 | 580300 | 577100 | 14.17 | 9.65 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 4771635.93 | 2491238.79 | 3200 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 24.2 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-05 | 2026 | 4 | 5 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 2.66 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 19.03.2026 to 07.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-04-05 | 2026 | 4 | 5 | Karora HPS | 11.8 | 11.86 | 10.97 | 259301 | 257279 | 10.11 | 8.64 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 2001630.62 | 201665.38 | 2022 | Unit#01 and Unit#02 are on bar , collectivelly delivering an average load of 10.97 MW as per the available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-05 | 2026 | 4 | 5 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 177.7 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | The plant remain shut down since 10th December 2025 for Box Channel repair works by EPC contractor. Box Channel repair works has been completed. Pre-Loading mandatory tests of generators carried out, and power generation will be started very soon. Inshallah. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-05 | 2026 | 4 | 5 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 23.8 | 8 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Unit standstill due to low water inflow in canal due to weekly canal closure by irrigation department | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-05 | 2026 | 4 | 5 | Malakand-3 HPS | 81 | 46 | 32.79 | 787026 | 780860 | 51 | 25.38 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2235367.92 | 3329720.88 | 6166 | As per instructions of Mr. Mansingh (NPCC Islamabad), received via phone call (03169221986), Units #01 and #03 were shut down and station load was brought to zero for approximately 1 to 1.5 hours or as per their demand. Units #01 and #03 were desynchronized from the system at 11:11 hrs. Subsequently, upon instructions from Mr. Saqib (NPCC Islamabad), Unit #01 and Unit #03 were synchronized with the system at 13:27 hrs. and 13:28 hrs., respectively. Unit# 01 desynchronized from the system at 15:07hrs due to decreasing trend in hydrology & kept standby due to less hydrology.Unit#02 synchronized with the system at 18:55hrs as hydrology improved | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-05 | 2026 | 4 | 5 | Pehur HPS | 18 | 3.74 | 1.72 | 41200 | 40000 | 12.12 | 3.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 150680 | 1476664 | 1200 | Plant remained operational since 1230 hrs dated 05-04-2026 as per irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-05 | 2026 | 4 | 5 | Reshun HPS | 4.2 | 2.34 | 0.78 | 19000 | 18441 | 1.21 | 1.16 | 38.67 | 13.48 | 40.33 | 45 | 40656 | 548042.88 | 248584.68 | 299458.2 | 559 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-06 | 2026 | 4 | 6 | Daral Khwar HPS | 36.6 | 22 | 20.3 | 486950 | 483750 | 14.17 | 8.09 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3999790.12 | 3263084.6 | 3200 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 20.3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-06 | 2026 | 4 | 6 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 2.66 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 19.03.2026 to 07.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-04-06 | 2026 | 4 | 6 | Karora HPS | 11.8 | 11.83 | 11.78 | 276531 | 274499 | 10.11 | 9.26 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 2135602.22 | 67693.78 | 2032 | Both units are on bar, collectively delivering an average load of 11.78 MW as per the available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-06 | 2026 | 4 | 6 | Koto HPS | 40.8 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 8.24 | 100 | 58 | 979200 | 8068608 | 0 | 8068608 | 0 | Unit #1 and Unit #3 are started at Full Speed No Load (FSNL ) & excited to completely dry stator before connecting with grid. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-06 | 2026 | 4 | 6 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 23.8 | 8 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Unit standstill due to low water inflow in canal due to weekly canal closure by irrigation department | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-06 | 2026 | 4 | 6 | Malakand-3 HPS | 81 | 45 | 41.6 | 998483 | 991300 | 51 | 26.93 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2837794.51 | 2727294.29 | 7183 | As per available hydrology from the Irrigation Department two units are on bar. Load variation occurs due to variation in the hydrology of River Swat. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-06 | 2026 | 4 | 6 | Pehur HPS | 18 | 3.7 | 3.61 | 86700 | 83000 | 12.12 | 9 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 312661 | 1314683 | 3700 | Unit# 01 is on the bar with 3.6 MW load with low irrigation demand up to 07 cms as per request of irrigation SDO. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-06 | 2026 | 4 | 6 | Reshun HPS | 4.2 | 2.05 | 0.84 | 19000 | 18460 | 1.21 | 1.16 | 38.67 | 13.48 | 40.33 | 45 | 40656 | 548042.88 | 248840.8 | 299202.08 | 540 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-07 | 2026 | 4 | 7 | Daral Khwar HPS | 36.6 | 22.5 | 20.4 | 488540 | 485340 | 14.17 | 8.12 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 4012936.72 | 3249938 | 3200 | Unit No 02 and 03 were on bar delivering an average load equal to 20.4 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-07 | 2026 | 4 | 7 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 2.66 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 19.03.2026 to 07.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-04-07 | 2026 | 4 | 7 | Karora HPS | 11.8 | 11.81 | 11.78 | 279002 | 276980 | 10.11 | 9.15 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 2154904.4 | 48391.6 | 2022 | Both units are on bar ,collectively delivering an average load of 11.78 MW as per the available hydrology. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-07 | 2026 | 4 | 7 | Koto HPS | 40.8 | 7.5 | 0.52 | 13778 | 12500 | 177.7 | 1.61 | 53.67 | 8.24 | 100 | 58 | 979200 | 8068608 | 103000 | 7965608 | 1278 | The unit no 03 was on bar and deliver average power 0.52 with available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-07 | 2026 | 4 | 7 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 23.8 | 8 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Unit standstill due to low water inflow in canal due to weekly canal closure by irrigation department 11KV Line tripped at 0900hrs due to heavy storm and restored at 1910hrs | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-07 | 2026 | 4 | 7 | Malakand-3 HPS | 81 | 45 | 40.31 | 967494 | 959650 | 51 | 27.01 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2747190.06 | 2817898.74 | 7844 | As per the available hydrology from the Irrigation Department, two units are on bar. Load variation occurs due to variation in the hydrology of River Swat and heavy rainfall | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-07 | 2026 | 4 | 7 | Pehur HPS | 18 | 3.8 | 3.66 | 88000 | 84000 | 12.12 | 9 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 316428 | 1310916 | 4000 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-07 | 2026 | 4 | 7 | Reshun HPS | 4.2 | 2.02 | 0.73 | 17000 | 16435 | 1.21 | 1.04 | 34.67 | 13.48 | 40.33 | 45 | 40656 | 548042.88 | 221543.8 | 326499.08 | 565 | Line faults and less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-08 | 2026 | 4 | 8 | Daral Khwar HPS | 36.6 | 20 | 19 | 455110 | 451910 | 14.17 | 7.56 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3736527.45 | 3526347.27 | 3200 | Unit No 02 and 03 were on bar delivering an average load equal to 19 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-08 | 2026 | 4 | 8 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 2.66 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 08.04.2026 to 20.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-04-08 | 2026 | 4 | 8 | Karora HPS | 11.8 | 11.78 | 11.75 | 278675 | 275441 | 10.11 | 9.18 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 2142930.98 | 60365.02 | 3234 | 1-Unit#01 and are on bar, collectively delivering an average load of 11.75MW as per the available hydrology. 2- Rectification works mainly related to the SCADA system ,Governor,Cooling water system and protection system , as identified in the punch list, are still pending. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-08 | 2026 | 4 | 8 | Koto HPS | 40.8 | 26.83 | 15.48 | 371500 | 368689 | 177.7 | 47.8 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 3037997.36 | 5030610.64 | 2811 | The plant was operational on average load of 15.48 MW as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-08 | 2026 | 4 | 8 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 1 | 4 | 0 | 4.671 | 33.33 | 70 | 20800 | 97156.8 | 0 | 97156.8 | 0 | Unit stand still due to low hydrology in irrigation canal. | machai.12333@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated | Link_Generation_Data_Summary.xlsx
2026-04-08 | 2026 | 4 | 8 | Malakand-3 HPS | 81 | 42 | 37.73 | 905539 | 897990 | 51 | 25.83 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2570675.97 | 2994412.83 | 7549 | Due to heavy rainfall in the catchment area of Upper Swat Canal and contaminated water, a large amount of trash and debris has accumulated at the forebay, resulting in choking of the trash racks and fluctuations in hydrology. Consequently, load variation is occurring. At present, two units are operating as per the available hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-08 | 2026 | 4 | 8 | Pehur HPS | 18 | 4.18 | 3.85 | 92400 | 88000 | 12.12 | 8.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 331496 | 1295848 | 4400 | Generation is less because of low irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-08 | 2026 | 4 | 8 | Reshun HPS | 4.2 | 2.17 | 0.82 | 18000 | 17474 | 1.21 | 1.1 | 36.67 | 13.48 | 40.33 | 45 | 40656 | 548042.88 | 235549.52 | 312493.36 | 526 | Less hydrology and lines works. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-09 | 2026 | 4 | 9 | Daral Khwar HPS | 36.6 | 19 | 16.8 | 402300 | 399100 | 14.17 | 6.67 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3299878.53 | 3962996.19 | 3200 | Unit No 02 and 03 were on bar delivering an average load equal to 16.8 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-09 | 2026 | 4 | 9 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 2.66 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 08.04.2026 to 20.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-04-09 | 2026 | 4 | 9 | Karora HPS | 11.8 | 11.84 | 11.17 | 263721 | 260543 | 10.11 | 8.79 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 2027024.54 | 176271.46 | 3178 | 1.Unit#01 and unit#02 are on bar, collectively delivering in average load of 11.17MW as per the available hydrology. 2. Rectification works mainly related to the SCADA system, governor, cooling water system and protection system, as identified in the punch list, are still pending. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-09 | 2026 | 4 | 9 | Koto HPS | 40.8 | 27.23 | 26.92 | 646000 | 639910 | 177.7 | 83.13 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 5272858.4 | 2795749.6 | 6090 | The plant was operational an average load of 26.92 MW as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-09 | 2026 | 4 | 9 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 22.6 | 3 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Weekly canal closure. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-09 | 2026 | 4 | 9 | Malakand-3 HPS | 81 | 41 | 39.08 | 937840 | 930170 | 51 | 26.45 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2662797.66 | 2902291.14 | 7670 | At present Two units are running as per available hydrology ,however the heavy trash and debris have accumulated at Forebay, due to heavy rainfall in surrounding area causing choking of trash rack resulting load variation due to differential at Forebay. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-09 | 2026 | 4 | 9 | Pehur HPS | 18 | 4.25 | 4.17 | 100000 | 95000 | 12.12 | 10 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 357865 | 1269479 | 5000 | Generation is less due to low irrigation demand of 6 - 7 cms as per instructions of irrigation SDO. | phpcmw18@gmail.com | Original | Aux = Units - Net | Link_Generation_Data_Summary.xlsx
2026-04-09 | 2026 | 4 | 9 | Reshun HPS | 4.2 | 2.02 | 0.76 | 18000 | 17445 | 1.21 | 1.1 | 36.67 | 13.48 | 40.33 | 45 | 40656 | 548042.88 | 235158.6 | 312884.28 | 555 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-10 | 2026 | 4 | 10 | Daral Khwar HPS | 36.6 | 16 | 14.9 | 358750 | 355550 | 14.17 | 5.95 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2939794.06 | 4323080.66 | 3200 | Unit No 02 and 03 were on bar delivering an average load equal to 14.9 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-10 | 2026 | 4 | 10 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 2.66 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 08.04.2026 to 20.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-04-10 | 2026 | 4 | 10 | Karora HPS | 11.8 | 11.82 | 11.76 | 278199 | 275182 | 10.11 | 9.26 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 2140915.96 | 62380.04 | 3017 | 1. Both units are on bar, collectively delivering an average load of 11.17MW as per the available hydrology. 2. Rectification works mainly related to the SCADA system, Governor, cooling water system and protection system, as identified in the punch list, are still pending. | rekarorahps2000@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-10 | 2026 | 4 | 10 | Koto HPS | 40.8 | 26.85 | 23.07 | 545500 | 541482 | 177.7 | 68.65 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 4461811.68 | 3606796.32 | 4018 | Not reported | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-10 | 2026 | 4 | 10 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 22.5 | 4 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Weekly canal closure. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-10 | 2026 | 4 | 10 | Malakand-3 HPS | 81 | 45 | 41.13 | 987231 | 980450 | 51 | 26.94 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2806734.22 | 2758354.58 | 6781 | At present Two units are running as per available hydrology, however the heavy trash and debris have accumulated at Forebay due to heavy rainfall in surrounding area caused choking of trash racks. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-10 | 2026 | 4 | 10 | Pehur HPS | 18 | 4.45 | 4.06 | 97500 | 93000 | 12.12 | 9.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 350331 | 1277013 | 4500 | Generation is less because of low irrigation demand in the canal as per request of irrigation SDO. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-10 | 2026 | 4 | 10 | Reshun HPS | 4.2 | 2.04 | 1.73 | 17000 | 16479 | 1.21 | 1.04 | 34.67 | 13.48 | 40.33 | 45 | 40656 | 548042.88 | 222136.92 | 325905.96 | 521 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-11 | 2026 | 4 | 11 | Daral Khwar HPS | 36.6 | 15.5 | 14.9 | 357090 | 354090 | 14.17 | 5.93 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2927722.35 | 4335152.37 | 3000 | Unit No 02 and 03 were on bar delivering an average load equal to 14.9 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-11 | 2026 | 4 | 11 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 2.66 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 08.04.2026 to 20.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-04-11 | 2026 | 4 | 11 | Karora HPS | 11.8 | 11.85 | 10.07 | 237409 | 234479 | 12.19 | 7.57 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1824246.62 | 379049.38 | 2930 | Unit#01 and Unit#02 on bar, collectively delivering an average load of 10.07 MW as per the available hydrology. Unit #01 was shut down from 9:37 to 10:53 and from 12:41 to 18:48 upon the request of the GRC representative for governor rectification work. The total shutdown duration of Unit #01 was 7 hours and 23 minutes. Rectification works mainly related to the SCADA system,Governor,Cooling water system and Protection system, as identified in the punch list, are still pending. | 11.8mwkarorahps@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-11 | 2026 | 4 | 11 | Koto HPS | 40.8 | 26.25 | 22.81 | 549000 | 545047 | 177.7 | 66.38 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 4491187.28 | 3577420.72 | 3953 | Unit #02 and Unit #03 on bar, delivering an average load of 22.81 MW. Unit #01 is on standby due to a TRCM issue. The TRCM is not operational, and blockage of the intake trash rack has caused a drop in pressure and head. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-11 | 2026 | 4 | 11 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Weekly canal closure. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-11 | 2026 | 4 | 11 | Malakand-3 HPS | 81 | 44 | 41.62 | 998984 | 992320 | 51 | 27.25 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2840714.46 | 2724374.34 | 6664 | As per available hydrology from the Irrigation Department two units are on bar. Load variation occurs due to variation in the hydrology of River Swat. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-11 | 2026 | 4 | 11 | Pehur HPS | 18 | 4.32 | 4.13 | 99000 | 95000 | 12.12 | 10 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 357865 | 1269479 | 4000 | Generation is less because of restriction of flow in the canal as per request of irrigation SDO. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-11 | 2026 | 4 | 11 | Reshun HPS | 4.2 | 2.07 | 0.71 | 19000 | 18439 | 1.21 | 1.16 | 38.67 | 13.48 | 40.33 | 45 | 40656 | 548042.88 | 248557.72 | 299485.16 | 561 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-12 | 2026 | 4 | 12 | Daral Khwar HPS | 36.6 | 18 | 15.1 | 363010 | 360210 | 14.17 | 6.02 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 2978324.34 | 4284550.38 | 2800 | Unit No 02 and 03 were on bar delivering an average load equal to 15.1 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-12 | 2026 | 4 | 12 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 2.66 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 08.04.2026 to 20.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-04-12 | 2026 | 4 | 12 | Karora HPS | 11.8 | 11.84 | 10.1 | 243155 | 240777 | 12.19 | 8.19 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1873245.06 | 330050.94 | 2378 | Unit No.01 and 02 on bar, collectively delivering an average load of 10.1MW according to the available hydrology. Unit #01 was shut down from 10:23 to 12:48 and from 15:45 to 19:35 upon the request of the GRC representative for governor rectification work. The total shutdown duration of Unit #01 was 6 hours and 15 minutes. Rectification works mainly related to the SCADA system, Governor, Cooling Water System and Protection System, as identified in the punch list, are still pending. | 11.8mwkarorahps@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-12 | 2026 | 4 | 12 | Koto HPS | 40.8 | 26.23 | 24.25 | 582500 | 579511 | 177.7 | 71.5 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 4775170.64 | 3293437.36 | 2989 | Unit #02 and Unit #03 on bar, delivering an average load of 24.25MW. Unit #01 is on standby due to a TRCM issue. The TRCM is not operational, and blockage of the intake trash rack has caused a drop in pressure and head. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-12 | 2026 | 4 | 12 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 24 | 5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 0 | 291470.4 | 0 | Weekly canal closure. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-12 | 2026 | 4 | 12 | Malakand-3 HPS | 81 | 40 | 38.42 | 922126 | 915460 | 51 | 25.45 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2620687.34 | 2944401.46 | 6666 | As per available hydrology from the Irrigation Department two units are on bar. Load variation is due to variation in the Hydrology of River Swat. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-12 | 2026 | 4 | 12 | Pehur HPS | 18 | 4.52 | 4.37 | 105000 | 100000 | 12.12 | 9 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 376700 | 1250644 | 5000 | Plant remained operational throughout 24 hrs as per irrigation demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-12 | 2026 | 4 | 12 | Reshun HPS | 4.2 | 2.33 | 0.78 | 17000 | 16435 | 1.21 | 1.04 | 34.67 | 13.48 | 40.33 | 45 | 40656 | 548042.88 | 221543.8 | 326499.08 | 565 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-13 | 2026 | 4 | 13 | Daral Khwar HPS | 36.6 | 22.5 | 18.2 | 437430 | 435030 | 14.17 | 7.28 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 3596958.55 | 3665916.17 | 2400 | Unit No 02 and 03 were on bar delivering an average load equal to 18.2 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-13 | 2026 | 4 | 13 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 2.66 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 08.04.2026 to 20.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-04-13 | 2026 | 4 | 13 | Karora HPS | 11.8 | 11.8 | 9.94 | 236224 | 230549 | 12.19 | 7.89 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1793671.22 | 409624.78 | 5675 | The Plant was operational on average load 9.94MW and maximum load 11.80mw as per hydrology. | 11.8mwkarorahps@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-13 | 2026 | 4 | 13 | Koto HPS | 40.8 | 26.85 | 25.4 | 611280 | 610274 | 177.7 | 78.66 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 5028657.76 | 3039950.24 | 1006 | Unit #01 and Unit #03 on bar, delivering an average load of 25.40 MW and Maximum load of 26.85 MW. Unit #02 is on standby due to a TRCM issue. The TRCM is not operational, and blockage of the intake trash rack has caused a drop in pressure and head. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-13 | 2026 | 4 | 13 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 1 | 7 | 0 | 4.671 | 33.33 | 70 | 20800 | 97156.8 | 0 | 97156.8 | 0 | Unit stand still due to low hydrology in irrigation Canal. | machai.12333@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated | Link_Generation_Data_Summary.xlsx
2026-04-13 | 2026 | 4 | 13 | Malakand-3 HPS | 81 | 37 | 35.95 | 862885 | 855990 | 51 | 24.2 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2450442.57 | 3114646.23 | 6895 | The irrgation department informed that the flow tendency in the Swat river is towards decreasing. Therefore, two Units are runnig as per available hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-13 | 2026 | 4 | 13 | Pehur HPS | 18 | 4.2 | 4.4 | 107700 | 104000 | 12.12 | 10 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 391768 | 1235576 | 3700 | Generation is less because of restriction of flow in the canal as per request of irrigation SDO. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-13 | 2026 | 4 | 13 | Reshun HPS | 4.2 | 1.89 | 0.8 | 18000 | 17433 | 1.21 | 1.1 | 36.67 | 13.48 | 40.33 | 45 | 40656 | 548042.88 | 234996.84 | 313046.04 | 567 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-14 | 2026 | 4 | 14 | Daral Khwar HPS | 36.6 | 28 | 22.4 | 537130 | 534730 | 14.17 | 8.94 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 4421308.06 | 2841566.66 | 2400 | Unit No 02 and 03 were on bar delivering an average load equal to 22.4 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-14 | 2026 | 4 | 14 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 2.66 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 08.04.2026 to 20.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-04-14 | 2026 | 4 | 14 | Karora HPS | 11.8 | 11.8 | 9.11 | 218613 | 216525 | 12.19 | 7.46 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1684564.5 | 518731.5 | 2088 | Unit No.01 and 02 on bar, collectively delivering an average load of 9.11MW according to the available hydrology. Unit #01 was shut down from 10:20Hrs to 17:00Hrs upon the request of the GRC representative for governor rectification work. The total shutdown duration of Unit #01 was 5 hours and 20 minutes. Unit #02 was shut down from 13:04Hrs to 15:00Hrs upon the request of the GRC representative for Punch list activities. The total shutdown duration of Unit #01 was 1 hours and 56 minutes. Rectification works mainly related to the SCADA system, Governor, Cooling Water System and Protection System, as identified in the punch list, are still pending. | 11.8mwkarorahps@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-14 | 2026 | 4 | 14 | Koto HPS | 40.8 | 26.6 | 24.4 | 591250 | 584724 | 177.7 | 76.08 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 4818125.76 | 3250482.24 | 6526 | Unit # 01 and Unit # 03 were on bar, delivering an average load of 24.40 MW and Maximum load of 26.6 MW. Unit # 02 is standby due to a TRCM issue. The TRCM is not operational, and blockage of the intake trash rack has caused a drop in pressure and head. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-14 | 2026 | 4 | 14 | Machai HPS | 2.6 | 0.44 | 0.44 | 404 | 396 | 13 | 13 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 1849.72 | 289620.68 | 8 | Unit after all preliminary checks started and synced with system at 2311 as head was restored due to increase in canal discharge. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-14 | 2026 | 4 | 14 | Malakand-3 HPS | 81 | 38 | 35.14 | 843401 | 836130 | 51 | 23.8 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2393589.35 | 3171499.45 | 7271 | The irrgation department informed that the flow tendency in the Swat river is towards decreasing. Therefore, two Units are runnig as per available hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-14 | 2026 | 4 | 14 | Pehur HPS | 18 | 6.49 | 5.1 | 122500 | 118000 | 12.12 | 13 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 444506 | 1182838 | 4500 | Unit#01 ia on bar with 3.0 MW load, while Unit# 02 taken on bar with 3.0 MW at 1525 hours dated 14-04-2026 as per increase in irrigation demand, instructed by irrigation SDO. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-14 | 2026 | 4 | 14 | Reshun HPS | 4.2 | 1.77 | 0.79 | 18000 | 17428 | 1.21 | 1.1 | 36.67 | 13.48 | 40.33 | 45 | 40656 | 548042.88 | 234929.44 | 313113.44 | 572 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-15 | 2026 | 4 | 15 | Daral Khwar HPS | 36.6 | 36.6 | 27.9 | 668650 | 665850 | 14.17 | 11.14 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 5505447.56 | 1757427.16 | 2800 | 1. Unit No 01, 02 and 03 were on bar delivering an average load equal to 27.9 MW according to available hydrology. 2. Unit No 01 synchronized with the national grid at 18:28 Hrs due to increased hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-15 | 2026 | 4 | 15 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 2.66 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 08.04.2026 to 20.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-04-15 | 2026 | 4 | 15 | Karora HPS | 11.8 | 11.8 | 10.18 | 244257 | 242283 | 10.19 | 8.26 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1884961.74 | 318334.26 | 1974 | The plant was operational on average load 10.18MW and maximum load 11.80 MW as per hydrology. | 11.8mwkarorahps@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-15 | 2026 | 4 | 15 | Koto HPS | 40.8 | 26.6 | 18.46 | 445000 | 442120 | 177.7 | 57.26 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 3643068.8 | 4425539.2 | 2880 | Unit No.2 and 3 were on bar while unit No.1 as standby. Load maintained according to available hydrology. Trash Racks cleaning operation carried out for which initially load was reduced and then plant shut down as huge trashes were found stranded in the trash racks. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-15 | 2026 | 4 | 15 | Machai HPS | 2.6 | 0.44 | 0.08 | 1864 | 1804 | 25 | 13 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 8426.48 | 283043.92 | 60 | Unit stopped various times due to low inflow in canal. Unit stopped at 1143 due to low hydrology | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-15 | 2026 | 4 | 15 | Malakand-3 HPS | 81 | 40 | 36.05 | 865109 | 857770 | 51 | 24.3 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2455538.18 | 3109550.62 | 7339 | The flow tendency in the Swat river is low so As per available hydrology from the Irrigation Department two units are on bar | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-15 | 2026 | 4 | 15 | Pehur HPS | 18 | 6.91 | 6.7 | 160700 | 157000 | 12.12 | 16 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 591419 | 1035925 | 3700 | Plant operational 24 hrs as per available head. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-15 | 2026 | 4 | 15 | Reshun HPS | 4.2 | 1.62 | 0.83 | 19000 | 18550 | 1.21 | 1.16 | 38.67 | 13.48 | 40.33 | 45 | 40656 | 548042.88 | 250054 | 297988.88 | 450 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-16 | 2026 | 4 | 16 | Daral Khwar HPS | 36.6 | 33.3 | 29.2 | 700210 | 697010 | 14.17 | 11.66 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 5763087.78 | 1499786.94 | 3200 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 29.2 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-16 | 2026 | 4 | 16 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 2.66 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 08.04.2026 to 20.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-04-16 | 2026 | 4 | 16 | Karora HPS | 11.8 | 11.8 | 10.75 | 257928 | 255052 | 12.19 | 8.65 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1984304.56 | 218991.44 | 2876 | The plant was operational on average load 10.75MW and maximum load 11.8MW as per hydrology. | 11.8mwkarorahps@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-16 | 2026 | 4 | 16 | Koto HPS | 40.8 | 30.83 | 26.36 | 640250 | 631760 | 177.7 | 82.39 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 5205702.4 | 2862905.6 | 8490 | Unit No.1 was started and synchronized with Grid at 20:11 hours, after consulting the representative of EPC contractor. With addition of 3rd unit, now all units are on bar. Load is being maintained as per instructions issued by the representative of EPC contractor. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-16 | 2026 | 4 | 16 | Machai HPS | 2.6 | 0.68 | 0.16 | 3524 | 3344 | 25 | 14 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 15619.82 | 275850.58 | 180 | Unit synced with system after water inflow in canal increased at 1528. Unit tripped at 1651 and 2216 due to line tripping from grid while line restored at 1718 and 2238 and unit synced with system at 1740 and 2241 | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-16 | 2026 | 4 | 16 | Malakand-3 HPS | 81 | 41 | 37.32 | 895635 | 888320 | 51 | 25.17 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2542993.66 | 3022095.14 | 7315 | As per available hydrology from the Irrigation Department two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-16 | 2026 | 4 | 16 | Pehur HPS | 18 | 7.03 | 6.93 | 166400 | 161000 | 12.12 | 16.5 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 606487 | 1020857 | 5400 | Plant remained operational as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-16 | 2026 | 4 | 16 | Reshun HPS | 4.2 | 2.22 | 0.95 | 22000 | 21400 | 1.21 | 1.34 | 44.67 | 13.48 | 40.33 | 45 | 40656 | 548042.88 | 288472 | 259570.88 | 600 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-17 | 2026 | 4 | 17 | Daral Khwar HPS | 36.6 | 36.6 | 35.2 | 843830 | 840630 | 14.17 | 14.06 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 6950581.03 | 312293.69 | 3200 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 35.2 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-17 | 2026 | 4 | 17 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 2.66 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 08.04.2026 to 20.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-04-17 | 2026 | 4 | 17 | Karora HPS | 11.8 | 11.8 | 11.61 | 278521 | 275506 | 12.19 | 9.24 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 2143436.68 | 59859.32 | 3015 | Unit No.01 and 02 on bar, collectively delivering an average load of 11.61MW according to the available hydrology. Rectification works mainly related to the SCADA system, Governor, Cooling Water System and Protection System, as identified in the punch list, are still pending. | 11.8mwkarorahps@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-17 | 2026 | 4 | 17 | Koto HPS | 40.8 | 33.17 | 27.7 | 669750 | 664051 | 177.7 | 86.18 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 5471780.24 | 2596827.76 | 5699 | The plant was operated in accordance with available hydrology. However, a failure in the cooling water strainer cleaning system resulted in insufficient cooling water pressure, which caused repeated unit trips. Consequently, Unit No. 3 is being maintained on standby to ensure adequate cooling water for the remaining two units. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-17 | 2026 | 4 | 17 | Machai HPS | 2.6 | 1.61 | 0.31 | 6504 | 6072 | 14 | 14 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 28362.31 | 263108.09 | 432 | Unit synced with system after 11 KV line restored at 2458. Unit tripped due to 11 KV line tripping at 0204, 1201 and 2303 while line restored at 0802 and 1435 and unit synced with system at 0959 and 1441 | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-17 | 2026 | 4 | 17 | Malakand-3 HPS | 81 | 41 | 36.85 | 884333 | 877280 | 51 | 25.33 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2511389.46 | 3053699.34 | 7053 | Due to heavy rainfall in the catchment area of Upper Swat Canal and contaminated water, a large amount of trash and debris has accumulated at the forebay, resulting fluctuations in hydrology. Consequently, load variation is occurring. At present, two units are operating as per the available hydrology. 132kv line DRG 1 & DGR2 tripped at 09:31HRS resulting tripping of Units.132KV Supply restored at 09:59HRS.Unit # 02 synchronized with the system at 10:30hrs & Unit # 03 synchronized with the system at 10:32hrs respectively. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-17 | 2026 | 4 | 17 | Pehur HPS | 18 | 7.05 | 6.95 | 166800 | 162000 | 12.12 | 16 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 610254 | 1017090 | 4800 | Plant remained operational throughout 24 hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-17 | 2026 | 4 | 17 | Reshun HPS | 4.2 | 2.37 | 0.89 | 19000 | 18490 | 1.21 | 1.16 | 38.67 | 13.48 | 40.33 | 45 | 40656 | 548042.88 | 249245.2 | 298797.68 | 510 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-18 | 2026 | 4 | 18 | Daral Khwar HPS | 36.6 | 36.6 | 36.5 | 875950 | 872350 | 14.17 | 14.59 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7212851.5 | 50023.22 | 3600 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.5 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-18 | 2026 | 4 | 18 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 2.66 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 08.04.2026 to 20.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-04-18 | 2026 | 4 | 18 | Karora HPS | 11.8 | 11.8 | 10.34 | 248276 | 245445 | 11.36 | 8.59 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1909562.1 | 293733.9 | 2831 | 1. Unit No.01 and 02 on bar, collectively delivering an average load of 10.34MW according to the available hydrology. 2. Rectification works mainly related to the SCADA system, Governor, Cooling Water System and Protection System, as identified in the punch list, are still pending. | 11.8mwkarorahps@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-18 | 2026 | 4 | 18 | Koto HPS | 40.8 | 26.7 | 23.12 | 556500 | 554093 | 177.7 | 71.61 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 4565726.32 | 3502881.68 | 2407 | Due to the failure of the cleaning mechanism of both cooling water strainers, one of our units is currently offline. We are forced to perform manual cleaning by dismantling the strainer housing, which is a labor-intensive and time-consuming process. This activity requires the shutdown of two additional operating units as well, resulting in substantial generation loss. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-18 | 2026 | 4 | 18 | Machai HPS | 2.6 | 0.8 | 0.54 | 13456 | 12848 | 25 | 14 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 60013.01 | 231457.39 | 608 | Unit tripped at 1458hrs due to line tripped, and back restored at 1600hrs, while Unit restored at 1619hrs. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-18 | 2026 | 4 | 18 | Malakand-3 HPS | 81 | 42 | 38.91 | 933861 | 926660 | 51 | 25.69 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2652749.58 | 2912339.22 | 7201 | As per available hydrology from the Irrigation Department two units are on bar. Load variation is due to variation in the Hydrology of River Swat. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-18 | 2026 | 4 | 18 | Pehur HPS | 18 | 7.03 | 6.21 | 149000 | 145000 | 12.12 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 546215 | 1081129 | 4000 | Plant remained operational throughout 24 hrs against restricted flow of 12 cms as per instruction of irrigation officials. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-18 | 2026 | 4 | 18 | Reshun HPS | 4.2 | 2.1 | 0.88 | 18000 | 17520 | 1.21 | 1.1 | 36.67 | 13.48 | 40.33 | 45 | 40656 | 548042.88 | 236169.6 | 311873.28 | 480 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-19 | 2026 | 4 | 19 | Daral Khwar HPS | 36.6 | 36.6 | 36.5 | 874850 | 871650 | 14.17 | 14.58 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7207063.7 | 55811.02 | 3200 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.5 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-19 | 2026 | 4 | 19 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 2.66 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 08.04.2026 to 20.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-04-19 | 2026 | 4 | 19 | Karora HPS | 11.8 | 11.8 | 11.58 | 277978 | 275097 | 11.36 | 9.82 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 2140254.66 | 63041.34 | 2881 | 1. Unit No. 01 and 02 on bar, collectively delivering an average load of 11.58MW according to the available hydrology. 2. Rectification works mainly related to the SCADA system, Governor, Cooling Water System and Protection System, as identified in the punch list, are still pending. | 11.8mwkarorahps@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-19 | 2026 | 4 | 19 | Koto HPS | 40.8 | 24.52 | 20.98 | 505000 | 502636 | 177.7 | 64.98 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 4141720.64 | 3926887.36 | 2364 | The plant was operational an average load of 20.98 MW as per available hydrology. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-19 | 2026 | 4 | 19 | Machai HPS | 2.6 | 0.78 | 0.66 | 16380 | 15564 | 23.8 | 14 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 72699.44 | 218770.96 | 816 | Smooth Operation | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-19 | 2026 | 4 | 19 | Malakand-3 HPS | 81 | 43 | 39.15 | 939590 | 932460 | 51 | 25.95 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 2669353.24 | 2895735.56 | 7130 | As per available hydrology from the Irrigation Department two units are on bar. Load variation is due to variation in the Hydrology of River Swat. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-19 | 2026 | 4 | 19 | Pehur HPS | 18 | 6.98 | 6.13 | 147100 | 143000 | 12.12 | 14 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 538681 | 1088663 | 4100 | Generation is less because of restriction of floe in the canal due to irrigation less demand. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-19 | 2026 | 4 | 19 | Reshun HPS | 4.2 | 2.42 | 0.9 | 21000 | 20520 | 1.21 | 1.28 | 42.67 | 13.48 | 40.33 | 45 | 40656 | 548042.88 | 276609.6 | 271433.28 | 480 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-20 | 2026 | 4 | 20 | Daral Khwar HPS | 36.6 | 36.6 | 36.2 | 867980 | 864380 | 14.17 | 14.46 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7146953.15 | 115921.57 | 3600 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.2 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-20 | 2026 | 4 | 20 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 2.66 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 08.04.2026 to 20.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-04-20 | 2026 | 4 | 20 | Karora HPS | 11.8 | 11.8 | 10.75 | 257903 | 255187 | 11.36 | 8.42 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1985354.86 | 217941.14 | 2716 | 1. Unit No. 01 and 02 on bar, collectively delivering an average load of 10.75MW according to the available hydrology. 2. Rectification works mainly related to the SCADA system, Governor, Cooling Water System and Protection System, as identified in the punch list, are still pending. | 11.8mwkarorahps@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-20 | 2026 | 4 | 20 | Koto HPS | 40.8 | 26.63 | 14.23 | 348500 | 345428 | 177.7 | 44.84 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 2846326.72 | 5222281.28 | 3072 | The plant was shut down for 06 hours due to intake cleaning performed by staff manually due to TRCM is not functional and now Unit no 01 and 03 are on bar, while unit no 02 is stand by due to cooling water strainers issues. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-20 | 2026 | 4 | 20 | Machai HPS | 2.6 | 0.79 | 0.53 | 13512 | 12892 | 23.8 | 14 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 60218.53 | 231251.87 | 620 | Unit on bar and delivering power to the National Grid accordance with available water inflow and prevailing system conditions. Unit tripped at 1948hrs due to 11KV Machai HPS line tripping from Katlang Grid by Earth-fault. 11 KV Machai HPS line restored at 1950hrs and Unit synchronised with the system at 2010hrs. Unit tripped at 2300hrs due to 11KV Machai HPS line tripping from Katlang Grid because of Load Shedding on Machai Feeder. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-20 | 2026 | 4 | 20 | Malakand-3 HPS | 81 | 52 | 44.41 | 1065903 | 1058030 | 51 | 29.64 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3028822.48 | 2536266.32 | 7873 | As hydrology improved by irrigation department Unti # 01 synchronized with the systemat 11:49Hrs ,and Hydrology in the River Swat has reduced, as informed by the Irrigation Department; therefore, Unit # 01 was desynchronized from the system at 19:20Hrs and kept on standby due to less hydrology. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-20 | 2026 | 4 | 20 | Pehur HPS | 18 | 7.46 | 7.1 | 170300 | 166000 | 12.12 | 17 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 625322 | 1002022 | 4300 | Not reported | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-20 | 2026 | 4 | 20 | Reshun HPS | 4.2 | 1.85 | 0.82 | 19000 | 18550 | 1.21 | 1.16 | 38.67 | 13.48 | 40.33 | 45 | 40656 | 548042.88 | 250054 | 297988.88 | 450 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-21 | 2026 | 4 | 21 | Daral Khwar HPS | 36.6 | 36.6 | 36.3 | 872020 | 868820 | 14.17 | 14.53 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7183664.41 | 79210.31 | 3200 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-21 | 2026 | 4 | 21 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 2.66 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 21.04.2026 to 26.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-04-21 | 2026 | 4 | 21 | Karora HPS | 11.8 | 11.8 | 11.53 | 246728 | 274022 | 11.36 | 9.26 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 2131891.16 | 71404.84 | 27294 | 1. Unit No. 01 and 02 on bar, collectively delivering an average load of 11.53MW according to the available hydrology. 2. Rectification works mainly related to the SCADA system, Governor, Cooling Water System and Protection System, as identified in the punch list, are still pending. | 11.8mwkarorahps@gmail.com | Original | CHECK: Net > Units (source me verify karein) | Link_Generation_Data_Summary.xlsx
2026-04-21 | 2026 | 4 | 21 | Koto HPS | 40.8 | 26.98 | 26.67 | 642000 | 639243 | 177.7 | 82.61 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 5267362.32 | 2801245.68 | 2757 | Unit # 01 and Unit # 03 on bar delivering an average load of 26.67 MW .Unit # 02 is stand by due to TRCM and cooling water strainers issue. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-21 | 2026 | 4 | 21 | Machai HPS | 2.6 | 0.99 | 0.78 | 18496 | 17908 | 23.8 | 16 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 83648.27 | 207822.13 | 588 | 2 hours of load shedding on Machai HPS line. i.e. from 0000hrs to 0100 hrs and 2300 hrs to 2400 hrs. Unit on bar and delivering power to the National Grid accordance with available water inflow and prevailing system conditions. Unit tripped at 1405hrs due to 11KV Machai HPS line tripping from Katlang Grid. 11 KV Machai HPS line restored at 1416hrs and Unit synchronised with the system at 1423hrs. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-21 | 2026 | 4 | 21 | Malakand-3 HPS | 81 | 52 | 48.96 | 1175093 | 1167010 | 51 | 32.13 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3340799.53 | 2224289.27 | 8083 | Unit # 03 synchronized with the system at 10:16Hrs while Unit # 02 kept standby at 10:27Hrs due to less hydrology. and As per available hydrology from the Irrigation Department two units are on bar. Load variation is due to variation in the Hydrology of River Swat. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-21 | 2026 | 4 | 21 | Pehur HPS | 18 | 7.76 | 7.34 | 176200 | 173000 | 12.12 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 651691 | 975653 | 3200 | Plant remained operational throughout 24 hrs against restricted flow as per instruction of irrigation officials due to less demand.. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-21 | 2026 | 4 | 21 | Reshun HPS | 4.2 | 1.86 | 0.86 | 20000 | 19540 | 1.21 | 1.22 | 40.67 | 13.48 | 40.33 | 45 | 40656 | 548042.88 | 263399.2 | 284643.68 | 460 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-22 | 2026 | 4 | 22 | Daral Khwar HPS | 36.6 | 36.6 | 36.5 | 875150 | 872350 | 14.17 | 14.59 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7212851.5 | 50023.22 | 2800 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.5 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-22 | 2026 | 4 | 22 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 2.66 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 21.04.2026 to 26.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-04-22 | 2026 | 4 | 22 | Karora HPS | 11.8 | 11.8 | 11.64 | 279431 | 276674 | 11.77 | 9.26 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 2152523.72 | 50772.28 | 2757 | Unit#01 and Unit#02 on bar ,collectively an average load of 11.64 MW according to the available hydrology. 2: Rectification works mainly related to the SCADA system, Governor, Cooling water system and protection system, as identified in the punch list, are still pending. | 11.8mwkarorahps@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-22 | 2026 | 4 | 22 | Koto HPS | 40.8 | 27.02 | 26.72 | 642749 | 637454 | 177.7 | 74.34 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 5252620.96 | 2815987.04 | 5295 | Unit #01 and Unit #03 are on bar , delivering an average load of 26.72 MW to National Grid. Unit #02 is on standby due to TRCM and cooling water strainer issues.. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-22 | 2026 | 4 | 22 | Machai HPS | 2.6 | 1.35 | 0.86 | 19552 | 18920 | 23.8 | 17 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 88375.32 | 203095.08 | 632 | 1. 2 Hours Daily Load shedding on Machai Feeder. 2. Unit tripped at 2128hrs due to stormy weather. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-22 | 2026 | 4 | 22 | Malakand-3 HPS | 81 | 26 | 48.32 | 1159773 | 1151440 | 51 | 31.94 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3296227.29 | 2268861.51 | 8333 | As per available hydrology from the Irrigation Department two units are on bar. Load variation is due to variation in the hydrology of River Swat. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-22 | 2026 | 4 | 22 | Pehur HPS | 18 | 7.04 | 7.03 | 168900 | 164000 | 12.12 | 17 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 617788 | 1009556 | 4900 | Plant remained operational throughout 24 hrs as per available hydrology + irrigation valve open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-22 | 2026 | 4 | 22 | Reshun HPS | 4.2 | 1.68 | 0.8 | 19000 | 18575 | 1.21 | 1.16 | 38.67 | 13.48 | 40.33 | 45 | 40656 | 548042.88 | 250391 | 297651.88 | 425 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-23 | 2026 | 4 | 23 | Daral Khwar HPS | 36.6 | 36.6 | 36.4 | 873610 | 870810 | 14.17 | 14.56 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7200118.32 | 62756.4 | 2800 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.4 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-23 | 2026 | 4 | 23 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 2.66 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 21.04.2026 to 26.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-04-23 | 2026 | 4 | 23 | Karora HPS | 11.8 | 11.88 | 11.69 | 280557 | 277916 | 11.36 | 9.22 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 2162186.48 | 41109.52 | 2641 | 1:Unit#01 & 02 on bar collectively delivering an average load of 11.69MW according to the available hydrology. 2: Contractor Technical team for punch list clearance related to governor system and SCADA system were deputed from 11-April 2026 to 17-April 2026 rectified some of the pending issues. 3: Both cooling water Pumps are running to maintain the required flow. However, proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and energy loss in case of pump failure or flow/pressure. | 11.8mwkarorahps@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-23 | 2026 | 4 | 23 | Koto HPS | 40.8 | 26.88 | 26.68 | 641250 | 636574 | 177.7 | 76.35 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 5245369.76 | 2823238.24 | 4676 | Unit #01 and Unit #03 are on bar , delivering an average load of 26.72 MW Unit #02 is on standby due to TRCM and cooling water strainer issues.. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-23 | 2026 | 4 | 23 | Machai HPS | 2.6 | 1.29 | 0.68 | 16836 | 16324 | 20 | 20 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 76249.4 | 215221 | 512 | 11kv Machai HPS line restored at 1000hrs, while Unit synchronized with the system at 1008hrs. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-23 | 2026 | 4 | 23 | Malakand-3 HPS | 81 | 53 | 48.29 | 1159009 | 1150370 | 51 | 31.63 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3293164.2 | 2271924.6 | 8639 | As per available hydrology from the Irrigation Department all the Three units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-23 | 2026 | 4 | 23 | Pehur HPS | 18 | 7.43 | 6.63 | 159200 | 154000 | 12.12 | 16 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 580118 | 1047226 | 5200 | Plant remained operational throughout 24 hrs as per available hydrology + irrigation valve open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-23 | 2026 | 4 | 23 | Reshun HPS | 4.2 | 2 | 0.85 | 22000 | 21530 | 1.21 | 1.34 | 44.67 | 13.48 | 40.33 | 45 | 40656 | 548042.88 | 290224.4 | 257818.48 | 470 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-24 | 2026 | 4 | 24 | Daral Khwar HPS | 36.6 | 36.6 | 36.4 | 874270 | 871070 | 14.17 | 14.57 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7202268.08 | 60606.64 | 3200 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.4 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-24 | 2026 | 4 | 24 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 2.66 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 21.04.2026 to 26.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-04-24 | 2026 | 4 | 24 | Karora HPS | 11.8 | 11.87 | 11.49 | 275833 | 273176 | 11.36 | 9.2 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 2125309.28 | 77986.72 | 2657 | Unit No.01 and 02 on bar, collectively delivering an average load of 11.49 MW according to the available hydrology. 2: Contractor technical team for punch list clearance related to Governor system and SCADA system were deputed from 11 April 2026 to 17 April 2026 rectified some of the pending issues. 3: Both cooling water pumps are running to maintain the required flow. However , proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and energy loss in case of pump failure or flow/pressure. | 11.8mwkarorahps@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-24 | 2026 | 4 | 24 | Koto HPS | 40.8 | 26.73 | 25.37 | 608566 | 604687 | 177.7 | 78.3 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 4982620.88 | 3085987.12 | 3879 | Unit #01 and Unit #03 are on bar , delivering an average load of 25.37MW. Unit #02 is on standby due to TRCM and cooling water strainer issues.. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-24 | 2026 | 4 | 24 | Machai HPS | 2.6 | 1.31 | 1 | 25956 | 25208 | 20 | 18.5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 117746.57 | 173723.83 | 748 | Smooth operation except: daily PTW issues on Machai 11 KV line during 2300 hrs. & 0100 hrs. for 2 hours; meanwhile, unit remains still. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-24 | 2026 | 4 | 24 | Malakand-3 HPS | 81 | 54 | 49.71 | 1193001 | 1184000 | 51 | 31.91 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3389436.8 | 2175652 | 9001 | As per available Hydrology from Irrigation department two Units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-24 | 2026 | 4 | 24 | Pehur HPS | 18 | 7.4 | 6.5 | 157300 | 153000 | 12.12 | 17 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 576351 | 1050993 | 4300 | Plant remained operational throughout 24 hrs as per available hydrology + irrigation valve open. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-24 | 2026 | 4 | 24 | Reshun HPS | 4.2 | 2.27 | 0.86 | 18000 | 17530 | 1.21 | 1.1 | 36.67 | 13.48 | 40.33 | 45 | 40656 | 548042.88 | 236304.4 | 311738.48 | 470 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-25 | 2026 | 4 | 25 | Daral Khwar HPS | 36.6 | 36.6 | 36.1 | 865840 | 863040 | 14.17 | 14.43 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7135873.63 | 127001.09 | 2800 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.1 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-25 | 2026 | 4 | 25 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 2.66 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 21.04.2026 to 26.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-04-25 | 2026 | 4 | 25 | Karora HPS | 11.8 | 11.7 | 9.92 | 238143 | 235682 | 11.36 | 7.98 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 1833605.96 | 369690.04 | 2461 | Unit No. 01 and 02 on bar, collectively delivering an average load of 9.92 MW according to the available hydrology. Contractor technical team for punch list clearance related to Governor system and SCADA system were deputed from 11 April 2026 to 17 April 2026 rectified some of the pending issues . Both cooling water pumps are running to maintain the required flow. However, proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and Energy loss in case of pump failure or flow/pressure. Unit #01 and Unit #02 were shut down at 09:05 hrs and 09:14 hrs, respectively, for intake gate trash rack cleaning and maintenance work on the cooling water system, and were subsequently re-synchronized to the system at 11:35 hrs and 12:00 hrs, respectively. | 11.8mwkarorahps@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-25 | 2026 | 4 | 25 | Koto HPS | 40.8 | 24.23 | 20.61 | 495250 | 493697 | 177.7 | 63.73 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 4068063.28 | 4000544.72 | 1553 | Unit # 02 and Unit # 03 on bar, delivering an average load of 20.61MW. Unit # 01 is standby due to TRCM and cooling water strainers issue. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-25 | 2026 | 4 | 25 | Machai HPS | 2.6 | 1.42 | 1.09 | 27920 | 27196 | 18 | 18.5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 127032.52 | 164437.88 | 724 | Smooth operation for the entire day & night except, daily load-shedding from Katlang grid on Machai 11 KV line during 2300 hrs. to 0100 hrs. for 02 hours; meanwhile, unit remains still. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-25 | 2026 | 4 | 25 | Malakand-3 HPS | 81 | 49 | 47.32 | 1135615 | 1127540 | 51 | 30.88 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3227808.76 | 2337280.04 | 8075 | As per available hydrology from irrigation department two units are on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-25 | 2026 | 4 | 25 | Pehur HPS | 18 | 7.38 | 7.09 | 170300 | 166000 | 12.12 | 18 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 625322 | 1002022 | 4300 | Plant remained operational throughout 24 hrs. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-25 | 2026 | 4 | 25 | Reshun HPS | 4.2 | 1.98 | 0.88 | 21000 | 20520 | 1.21 | 1.28 | 42.67 | 13.48 | 40.33 | 45 | 40656 | 548042.88 | 276609.6 | 271433.28 | 480 | Less Hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-26 | 2026 | 4 | 26 | Daral Khwar HPS | 36.6 | 36.6 | 36.5 | 875300 | 872500 | 14.17 | 14.59 | 100 | 8.2683 | 100 | 48 | 878400 | 7262874.72 | 7214091.75 | 48782.97 | 2800 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.5 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-26 | 2026 | 4 | 26 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 2.66 | 100 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 0 | 1397612.16 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 21.04.2026 to 26.04.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Link_Generation_Data_Summary.xlsx
2026-04-26 | 2026 | 4 | 26 | Karora HPS | 11.8 | 11.8 | 11.6 | 278285 | 275573 | 11.36 | 9.2 | 100 | 7.78 | 100 | 0.69 | 283200 | 2203296 | 2143957.94 | 59338.06 | 2712 | Unit No. 01 and 02 on bar, collectively delivering an average load of 11.60 MW according to the available hydrology. Contractor technical team for punch list clearance related to Governor system and SCADA system were deputed from 11 April 2026 to 17 April 2026 rectified some of the pending issues . Both cooling water pumps are running to maintain the required flow. However, proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and Energy loss in case of pump failure or flow/pressure. | 11.8mwkarorahps@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-26 | 2026 | 4 | 26 | Koto HPS | 40.8 | 19.73 | 18.12 | 435500 | 434087 | 177.7 | 56.04 | 100 | 8.24 | 100 | 58 | 979200 | 8068608 | 3576876.88 | 4491731.12 | 1413 | Unit # 02 and Unit # 03 on bar, delivering an average load of 18.12MW. Unit # 01 is standby due to TRCM and cooling water strainers issue. | rekotohpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-26 | 2026 | 4 | 26 | Machai HPS | 2.6 | 1.48 | 0.94 | 23184 | 22616 | 18 | 18.5 | 100 | 4.671 | 100 | 70 | 62400 | 291470.4 | 105639.34 | 185831.06 | 568 | Smooth operation except: 02 hours daily midnight load-shedding from PESCO on Machai 11 KV line, causing generation loss, despite available hydrology, which needs serious attention and consideration. | machai.12333@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-26 | 2026 | 4 | 26 | Malakand-3 HPS | 81 | 54 | 46.1 | 1106441 | 1097960 | 51 | 30 | 100 | 2.8627 | 100 | 77.5 | 1944000 | 5565088.8 | 3143130.09 | 2421958.71 | 8481 | As per available hydrology from Irrigation Department all three units are currently on bar. | malakand03hpc@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-26 | 2026 | 4 | 26 | Pehur HPS | 18 | 7.35 | 6.93 | 166400 | 162000 | 12.12 | 17 | 100 | 3.767 | 100 | 41 | 432000 | 1627344 | 610254 | 1017090 | 4400 | The plant remained operational throughout 24 hours. | phpcmw18@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-26 | 2026 | 4 | 26 | Reshun HPS | 4.2 | 2.19 | 0.93 | 21000 | 20439 | 1.21 | 1.28 | 42.67 | 13.48 | 40.33 | 45 | 40656 | 548042.88 | 275517.72 | 272525.16 | 561 | Less hydrology. | zafar.src@gmail.com | Original |  | Link_Generation_Data_Summary.xlsx
2026-04-27 | 2026 | 4 | 27 | Daral Khwar HPS | 36.6 | 36.6 | 36.47 | 875358 | 872558 | 16.76 | 14.59 | 99.65 | 8.2683 | 97.19 | 48 | 853720 | 7058813.08 | 7214571.31 | -155758.24 | 2800 | No data submitted for this date | passion.to.programe@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-27 | 2026 | 4 | 27 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 2.66 | 0 | 5.7092 | 99.77 | 79.57 | 244240 | 1394415.01 | 0 | 1394415.01 | 0 | No data submitted for this date | faizanbabar5@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-27 | 2026 | 4 | 27 | Karora HPS | 11.8 | 11.8 | 11.62 | 278801 | 276067 | 11.66 | 9.2 | 98.45 | 7.78 | 99.77 | 0.69 | 282560 | 2198316.8 | 2147801.26 | 50515.54 | 2734 | No data submitted for this date | rekarorahps2000@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-27 | 2026 | 4 | 27 | Koto HPS | 40.8 | 24.21 | 19.44 | 466600 | 465290 | 176.98 | 59.52 | 47.65 | 8.24 | 99.18 | 58 | 971160 | 8002358.4 | 3833989.6 | 4168368.8 | 1310 | No data submitted for this date | rekotohpc@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-27 | 2026 | 4 | 27 | Machai HPS | 2.6 | 1.34 | 1 | 23940 | 23311 | 19.2 | 18.4 | 38.37 | 4.671 | 95.38 | 70 | 59520 | 278017.92 | 108885.68 | 169132.24 | 629 | No data submitted for this date | engr.atifwazir@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-27 | 2026 | 4 | 27 | Malakand-3 HPS | 81 | 51.39 | 47.3 | 1135288 | 1126650 | 51 | 30.83 | 58.4 | 2.8627 | 98.87 | 77.5 | 1922000 | 5502109.4 | 3225260.95 | 2276848.44 | 8638 | No data submitted for this date | malakand03hpc@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-27 | 2026 | 4 | 27 | Pehur HPS | 18 | 7.17 | 6.74 | 161760 | 157400 | 12.76 | 16.7 | 37.44 | 3.767 | 86.2 | 41 | 372400 | 1402830.8 | 592925.8 | 809905 | 4360 | No data submitted for this date | phpcmw18@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-27 | 2026 | 4 | 27 | Reshun HPS | 4.2 | 1.57 | 0.93 | 22400 | 21841 | 1.24 | 1.35 | 22.22 | 13.48 | 51 | 45 | 51408 | 692979.84 | 294416.68 | 398563.16 | 559 | No data submitted for this date | zafar.src@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-28 | 2026 | 4 | 28 | Daral Khwar HPS | 36.6 | 36.6 | 36.48 | 875416 | 872616 | 19.36 | 14.59 | 99.66 | 8.2683 | 94.38 | 48 | 829040 | 6854751.43 | 7215050.87 | -360299.44 | 2800 | No data submitted for this date | passion.to.programe@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-28 | 2026 | 4 | 28 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 2.66 | 0 | 5.7092 | 99.54 | 79.57 | 243680 | 1391217.86 | 0 | 1391217.86 | 0 | No data submitted for this date | faizanbabar5@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-28 | 2026 | 4 | 28 | Karora HPS | 11.8 | 11.8 | 11.64 | 279316 | 276561 | 11.96 | 9.2 | 98.63 | 7.78 | 99.55 | 0.69 | 281920 | 2193337.6 | 2151644.58 | 41693.02 | 2755 | No data submitted for this date | rekarorahps2000@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-28 | 2026 | 4 | 28 | Koto HPS | 40.8 | 25.82 | 20.74 | 497700 | 496492 | 176.26 | 62.99 | 50.83 | 8.24 | 98.36 | 58 | 963120 | 7936108.8 | 4091094.08 | 3845014.72 | 1208 | No data submitted for this date | rekotohpc@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-28 | 2026 | 4 | 28 | Machai HPS | 2.6 | 1.38 | 1.03 | 24696 | 24006 | 20.4 | 18.3 | 39.58 | 4.671 | 90.77 | 70 | 56640 | 264565.44 | 112132.03 | 152433.41 | 690 | No data submitted for this date | engr.atifwazir@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-28 | 2026 | 4 | 28 | Malakand-3 HPS | 81 | 52.69 | 48.51 | 1164135 | 1155340 | 51 | 31.66 | 59.88 | 2.8627 | 97.74 | 77.5 | 1900000 | 5439130 | 3307391.82 | 2131738.18 | 8795 | No data submitted for this date | malakand03hpc@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-28 | 2026 | 4 | 28 | Pehur HPS | 18 | 6.96 | 6.55 | 157120 | 152800 | 13.4 | 16.4 | 36.37 | 3.767 | 72.41 | 41 | 312800 | 1178317.6 | 575597.6 | 602720 | 4320 | No data submitted for this date | phpcmw18@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-28 | 2026 | 4 | 28 | Reshun HPS | 4.2 | 1.67 | 0.99 | 23800 | 23243 | 1.28 | 1.43 | 23.61 | 13.48 | 51 | 45 | 51408 | 692979.84 | 313315.64 | 379664.2 | 557 | No data submitted for this date | zafar.src@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-29 | 2026 | 4 | 29 | Daral Khwar HPS | 36.6 | 36.6 | 36.48 | 875474 | 872674 | 21.95 | 14.6 | 99.67 | 8.2683 | 91.57 | 48 | 804360 | 6650689.79 | 7215530.43 | -564840.65 | 2800 | No data submitted for this date | passion.to.programe@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-29 | 2026 | 4 | 29 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 2.66 | 0 | 5.7092 | 99.31 | 79.57 | 243120 | 1388020.7 | 0 | 1388020.7 | 0 | No data submitted for this date | faizanbabar5@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-29 | 2026 | 4 | 29 | Karora HPS | 11.8 | 11.8 | 11.66 | 279832 | 277055 | 12.25 | 9.2 | 98.81 | 7.78 | 99.32 | 0.69 | 281280 | 2188358.4 | 2155487.9 | 32870.5 | 2777 | No data submitted for this date | rekarorahps2000@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-29 | 2026 | 4 | 29 | Koto HPS | 40.8 | 27.43 | 22.03 | 528800 | 527695 | 175.54 | 66.47 | 54 | 8.24 | 97.54 | 58 | 955080 | 7869859.2 | 4348206.8 | 3521652.4 | 1105 | No data submitted for this date | rekotohpc@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-29 | 2026 | 4 | 29 | Machai HPS | 2.6 | 1.42 | 1.06 | 25452 | 24702 | 21.6 | 18.2 | 40.79 | 4.671 | 86.15 | 70 | 53760 | 251112.96 | 115383.04 | 135729.92 | 750 | No data submitted for this date | engr.atifwazir@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-29 | 2026 | 4 | 29 | Malakand-3 HPS | 81 | 54 | 49.71 | 1192981 | 1184030 | 51 | 32.5 | 61.37 | 2.8627 | 96.6 | 77.5 | 1878000 | 5376150.6 | 3389522.68 | 1986627.92 | 8951 | No data submitted for this date | malakand03hpc@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-29 | 2026 | 4 | 29 | Pehur HPS | 18 | 6.76 | 6.35 | 152480 | 148200 | 14.05 | 16.1 | 35.3 | 3.767 | 58.61 | 41 | 253200 | 953804.4 | 558269.4 | 395535 | 4280 | No data submitted for this date | phpcmw18@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-29 | 2026 | 4 | 29 | Reshun HPS | 4.2 | 1.77 | 1.05 | 25200 | 24646 | 1.31 | 1.5 | 25 | 13.48 | 51 | 45 | 51408 | 692979.84 | 332228.08 | 360751.76 | 554 | No data submitted for this date | zafar.src@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-30 | 2026 | 4 | 30 | Daral Khwar HPS | 36.6 | 36.6 | 36.48 | 875532 | 872732 | 24.55 | 14.6 | 99.67 | 8.2683 | 88.76 | 48 | 779680 | 6446628.14 | 7216010 | -769381.85 | 2800 | No data submitted for this date | passion.to.programe@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-30 | 2026 | 4 | 30 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 0.39 | 2.66 | 0 | 5.7092 | 99.08 | 79.57 | 242560 | 1384823.55 | 0 | 1384823.55 | 0 | No data submitted for this date | faizanbabar5@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-30 | 2026 | 4 | 30 | Karora HPS | 11.8 | 11.8 | 11.68 | 280347 | 277549 | 12.55 | 9.2 | 98.99 | 7.78 | 99.1 | 0.69 | 280640 | 2183379.2 | 2159331.22 | 24047.98 | 2798 | No data submitted for this date | rekarorahps2000@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-30 | 2026 | 4 | 30 | Koto HPS | 40.8 | 29.05 | 23.33 | 559900 | 558897 | 174.82 | 69.94 | 57.18 | 8.24 | 96.72 | 58 | 947040 | 7803609.6 | 4605311.28 | 3198298.32 | 1003 | No data submitted for this date | rekotohpc@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-30 | 2026 | 4 | 30 | Machai HPS | 2.6 | 1.46 | 1.09 | 26208 | 25397 | 22.8 | 18.1 | 42 | 4.671 | 81.54 | 70 | 50880 | 237660.48 | 118629.39 | 119031.09 | 811 | No data submitted for this date | engr.atifwazir@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-30 | 2026 | 4 | 30 | Malakand-3 HPS | 81 | 55.3 | 50.91 | 1221828 | 1212720 | 51 | 33.33 | 62.85 | 2.8627 | 95.47 | 77.5 | 1856000 | 5313171.2 | 3471653.54 | 1841517.66 | 9108 | No data submitted for this date | malakand03hpc@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-30 | 2026 | 4 | 30 | Pehur HPS | 18 | 6.55 | 6.16 | 147840 | 143600 | 14.69 | 15.8 | 34.22 | 3.767 | 44.81 | 41 | 193600 | 729291.2 | 540941.2 | 188350 | 4240 | No data submitted for this date | phpcmw18@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-04-30 | 2026 | 4 | 30 | Reshun HPS | 4.2 | 1.86 | 1.11 | 26600 | 26048 | 1.35 | 1.58 | 26.39 | 13.48 | 51 | 45 | 51408 | 692979.84 | 351127.04 | 341852.8 | 552 | No data submitted for this date | zafar.src@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-05-01 | 2026 | 5 | 1 | Daral Khwar HPS | 36.6 | 36.6 | 36.5 | 875590 | 872790 | 27.14 | 14.6 | 99.68 | 8.2683 | 85.95 | 48 | 755000 | 6241232.9 | 7216490 | -975256.65 | 2800 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.5 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-01 | 2026 | 5 | 1 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 8.54 | 4 | 0 | 5.7092 | 98.86 | 79.57 | 242000 | 1383099.74 | 0 | 1383099.74 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 27.04.2026 to 03.05.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Generation_Data.xlsx
2026-05-01 | 2026 | 5 | 1 | Karora HPS | 11.8 | 11.85 | 11.7 | 280863 | 278043 | 12.85 | 9.2 | 99.17 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 2163175 | 15225.46 | 2820 | 1: Unit No. 01 and 02 on bar, collectively delivering an average load of 11.70MWaccording to the available hydrology. 2: Contractor technical team for punch list clearance related to Governor system and SCADA system were deputed from 11 April 2026 to 17 April 2026 rectified some of the pending issues. 3: Both cooling water pumps are running to maintain the required flow. However, proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and Energy loss in case of pump failure or flow/pressure. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-05-01 | 2026 | 5 | 1 | Koto HPS | 40.8 | 31.65 | 24.84 | 591000 | 590100 | 174.1 | 73.42 | 60.36 | 8.24 | 95.89 | 58 | 939000 | 7737625.81 | 4862424 | 2875201.81 | 900 | Unit #01 and Unit #03 are on bar , delivering an average load of 24.85 MW. Unit #02 is on standby due to cooling water and strainer issues.. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-01 | 2026 | 5 | 1 | Machai HPS | 2.6 | 1.28 | 1.11 | 26964 | 26092 | 24 | 18 | 43.21 | 4.671 | 76.92 | 70 | 48000 | 222833.82 | 121876 | 100958.09 | 872 | System operation normal according to available inflow in canal | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-05-01 | 2026 | 5 | 1 | Malakand-3 HPS | 81 | 56 | 52.11 | 1250675 | 1241410 | 51 | 34.16 | 64.34 | 2.8627 | 94.34 | 77.5 | 1834000 | 5248898.97 | 3553784 | 1695114.56 | 9265 | Due to rainfall in the catchment area, the inflow has become highly turbid with significant garbages accumulation at the forebay, leading to reduced load. Load fluctuations are also occurring due to variations in the hydrology of the River Swat. However, as per available hydrology from the Irrigation Department, all three units are currently on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-01 | 2026 | 5 | 1 | Pehur HPS | 18 | 6.11 | 6 | 143200 | 139000 | 15.33 | 15.5 | 33.15 | 3.767 | 31.02 | 41 | 134000 | 505507.1 | 523613 | -18105.9 | 4200 | Plant operational 24 hrs + irrigation valves opening | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-01 | 2026 | 5 | 1 | Reshun HPS | 4.2 | 2.37 | 1.24 | 28000 | 27450 | 1.38 | 1.65 | 27.78 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 370026 | 437091.7 | 550 | Outgoing feeder breaker remained Off for 3.40hours for storage of water. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-05-02 | 2026 | 5 | 2 | Daral Khwar HPS | 36.6 | 36.6 | 34.6 | 829320 | 826520 | 27.14 | 13.82 | 94.41 | 8.2683 | 85.95 | 48 | 755000 | 6241232.9 | 6833915 | -592682.41 | 2800 | 1. Units No. 01,02 and 03 were on bar delivering an average load equal to 34.6 MW according to the available hydrology. 2. 132 kV line failed at 1517Hrs and was restored at 1549Hrs. 3. Units No. 02, 01 and 03 synchronized with national Grid at 1557Hrs, 1600Hrs and 1600Hrs respectively. 4. Again 132 kV line failed at 1829Hrs and was restored at 1844Hrs. 5. Units No. 02, 03 and 01 synchronized with national Grid at 1903Hrs, 1905Hrs and 1911Hrs respectively. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-02 | 2026 | 5 | 2 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 8.54 | 4 | 0 | 5.7092 | 98.86 | 79.57 | 242000 | 1383099.74 | 0 | 1383099.74 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 27.04.2026 to 03.05.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Generation_Data.xlsx
2026-05-02 | 2026 | 5 | 2 | Karora HPS | 11.8 | 11.87 | 11.64 | 279437 | 276680 | 12.99 | 9.2 | 98.67 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 2152570 | 25829.6 | 2757 | 1:Unit No. 01 and 02 on bar, collectively delivering an average load of 11.64 MW according to the available hydrology. 2: Contractor technical team for punch list clearance related to Governor system and SCADA system were deputed from 11 April 2026 to 17 April 2026 rectified some of the pending issues . 3: Both cooling water pumps are running to maintain the required flow. However, proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and Energy loss in case of pump failure or flow/pressure. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-05-02 | 2026 | 5 | 2 | Koto HPS | 40.8 | 29.66 | 23.82 | 571750 | 570850 | 174.1 | 72.26 | 58.39 | 8.24 | 95.89 | 58 | 939000 | 7737360 | 4703804 | 3033556 | 900 | No data submitted for this date | rekotohpc@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-05-02 | 2026 | 5 | 2 | Machai HPS | 2.6 | 1.22 | 1.01 | 23436 | 22792 | 23.5 | 18 | 37.56 | 4.671 | 76.92 | 70 | 48000 | 222833.82 | 106461 | 116372.39 | 644 | Unit tripped at 1902hrs due to 132kv line tripe, 11kv line restored at 1953hrs but unit stand still because of stormy weather, while Unit synchronized with the system at 2056hrs. | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-05-02 | 2026 | 5 | 2 | Malakand-3 HPS | 81 | 57 | 52.28 | 1254739 | 1245190 | 51 | 33.9 | 64.54 | 2.8627 | 94.34 | 77.5 | 1834000 | 5248898.97 | 3564605 | 1684293.55 | 9549 | Due to rainfall in the catchment area, inflow is muddy with heavy debris accumulation at the Forebay, resulting in reduced load. However, as per available hydrology from the Irrigation Department, all three units are currently on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-02 | 2026 | 5 | 2 | Pehur HPS | 18 | 6.86 | 6.21 | 149100 | 145000 | 15.33 | 16 | 34.51 | 3.767 | 31.02 | 41 | 134000 | 505507.1 | 546215 | -40707.9 | 4100 | Plant operational 24 hrs + irrigation valves open | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-02 | 2026 | 5 | 2 | Reshun HPS | 4.2 | 1.96 | 1.29 | 30000 | 29448 | 1.88 | 1.83 | 29.76 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 396959 | 410158.7 | 552 | Outgoing Feeder breaker tripped 03 times due to lines faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-05-03 | 2026 | 5 | 3 | Daral Khwar HPS | 36.6 | 36.6 | 36.4 | 874600 | 871400 | 27.14 | 14.57 | 99.57 | 8.2683 | 85.95 | 48 | 755000 | 6241232.9 | 7204997 | -963763.72 | 3200 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.4 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-03 | 2026 | 5 | 3 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 8.54 | 4 | 0 | 5.7092 | 98.86 | 79.57 | 242000 | 1383099.74 | 0 | 1383099.74 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 27.04.2026 to 03.05.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Generation_Data.xlsx
2026-05-03 | 2026 | 5 | 3 | Karora HPS | 11.8 | 11.84 | 11.8 | 277193 | 274345 | 12.83 | 9.25 | 97.88 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 2134404 | 43995.9 | 2848 | 1. Unit No. 01 and 02 on bar, collectively delivering an average load of 11.80MW according to the available hydrology. 2. Contractor technical team for punch list clearance related to Governor system and SCADA system were deputed from 11 April 2026 to 17 April 2026 rectified some of the pending issues . 3. Both cooling water pumps are running to maintain the required flow. However, proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and Energy loss in case of pump failure or flow/pressure. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-05-03 | 2026 | 5 | 3 | Koto HPS | 40.8 | 26.9 | 23.16 | 552500 | 551600 | 174.1 | 71.09 | 56.42 | 8.24 | 95.89 | 58 | 939000 | 7737625.81 | 4545184 | 3192441.81 | 900 | Unit #01 and Unit #03 are on bar , delivering an average load of 23.16MW. Unit #02 is on standby due to cooling water and strainer issues. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-03 | 2026 | 5 | 3 | Machai HPS | 2.6 | 1.32 | 1.21 | 29080 | 28292 | 23.5 | 18 | 46.6 | 4.671 | 76.92 | 70 | 48000 | 222833.82 | 132152 | 90681.89 | 788 | Unit tripped at 0802hrs due to 11kv line tripped from katlang grid, and 11kv line restored at 0815hrs, while Unit synchronized with the system at 0829hrs. | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-05-03 | 2026 | 5 | 3 | Malakand-3 HPS | 81 | 56 | 52.37 | 1256981 | 1247600 | 51 | 34.09 | 64.66 | 2.8627 | 94.34 | 77.5 | 1834000 | 5248898.97 | 3571505 | 1677394.45 | 9381 | Due to rainfall in the catchment area, inflow is muddy with heavy debris accumulation at the Forebay, resulting in reduced load. However, as per available hydrology from the Irrigation Department, all three units are currently on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-03 | 2026 | 5 | 3 | Pehur HPS | 18 | 6.77 | 6 | 144900 | 141000 | 15.33 | 15.5 | 33.54 | 3.767 | 31.02 | 41 | 134000 | 505507.1 | 531147 | -25639.9 | 3900 | Plant remained operational throughout 24 hrs as per available hydrology + irrigation valve open. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-03 | 2026 | 5 | 3 | Reshun HPS | 4.2 | 2.2 | 1.44 | 33000 | 32451 | 2.1 | 2.02 | 32.74 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 437439 | 369678.7 | 549 | Outgoing Feeder Breaker remained off for 1.30hours for storage of water. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-05-04 | 2026 | 5 | 4 | Daral Khwar HPS | 36.6 | 36.6 | 36.4 | 873450 | 870650 | 27.14 | 14.56 | 99.44 | 8.2683 | 85.95 | 48 | 755000 | 6241232.9 | 7198795 | -957562.49 | 2800 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.4 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-04 | 2026 | 5 | 4 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 8.54 | 4 | 0 | 5.7092 | 98.86 | 79.57 | 242000 | 1383099.74 | 0 | 1383099.74 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 04.05.2026 to 06.05.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Generation_Data.xlsx
2026-05-04 | 2026 | 5 | 4 | Karora HPS | 11.8 | 11.84 | 11.65 | 279710 | 276863 | 12.85 | 9.25 | 98.77 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 2153994 | 24405.86 | 2847 | 1. Unit No. 01 and 02 on bar, collectively delivering an average load of 11.65MW according to the available hydrology. 2. Contractor technical team for punch list clearance related to Governor system and SCADA system were deputed from 11 April 2026 to 17 April 2026 rectified some of the pending issues. 3. Both cooling water pumps are running to maintain the required flow. However, proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and Energy loss in case of pump failure or flow/pressure. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-05-04 | 2026 | 5 | 4 | Koto HPS | 40.8 | 27.08 | 23.54 | 568500 | 564625 | 174.1 | 71.25 | 58.06 | 8.24 | 95.89 | 58 | 939000 | 7737625.81 | 4652510 | 3085115.81 | 3875 | Unit #01 and Unit #03 are on bar , delivering an average load of 23.54 MW. Unit #02 is on standby due to TRCM and cooling water strainer issues.. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-04 | 2026 | 5 | 4 | Machai HPS | 2.6 | 1.33 | 1.02 | 23840 | 23140 | 31.6 | 18 | 38.21 | 4.671 | 76.92 | 70 | 48000 | 222833.82 | 108087 | 114746.88 | 700 | Unit operated normally as per available inflow but tripped at 2003hrs due to 11kv line tripped from katlang grid while synchronized with the system at 2252hrs. Spillway gate was operated to remove the dead animals and trash. | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-05-04 | 2026 | 5 | 4 | Malakand-3 HPS | 81 | 53 | 48.43 | 1162425 | 1152990 | 51 | 31.48 | 59.8 | 2.8627 | 94.34 | 77.5 | 1834000 | 5248898.97 | 3300664 | 1948234.49 | 9435 | Due to rainfall in the catchment area, inflow is muddy with heavy debris accumulation at the Forebay, resulting in reduced load. However, as per available hydrology from the Irrigation Department all three units are currently on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-04 | 2026 | 5 | 4 | Pehur HPS | 18 | 5.77 | 5.6 | 135100 | 130000 | 15.33 | 15 | 31.27 | 3.767 | 31.02 | 41 | 134000 | 505507.1 | 489710 | 15797.1 | 5100 | Plant remained operational throughout 24 hrs as per available hydrology + irrigation valve open. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-04 | 2026 | 5 | 4 | Reshun HPS | 4.2 | 2.1 | 1.13 | 29000 | 28451 | 1.82 | 1.77 | 28.77 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 383519 | 423598.7 | 549 | Outgoing feeder breaker remained off 2.35hours due to line faults and less hydrology. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-05-05 | 2026 | 5 | 5 | Daral Khwar HPS | 36.6 | 36.6 | 36.4 | 873680 | 870480 | 27.14 | 14.56 | 99.46 | 8.2683 | 85.95 | 48 | 755000 | 6241232.9 | 7197390 | -956156.88 | 3200 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.4 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-05 | 2026 | 5 | 5 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 8.54 | 4 | 0 | 5.7092 | 98.86 | 79.57 | 242000 | 1383099.74 | 0 | 1383099.74 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 04.05.2026 to 10.05.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Generation_Data.xlsx
2026-05-05 | 2026 | 5 | 5 | Karora HPS | 11.8 | 11.87 | 11.12 | 266790 | 264089 | 12.85 | 9.24 | 94.21 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 2054612 | 123787.58 | 2701 | 1. Unit No. 01 and 02 on bar, collectively delivering an average load of 11.12MW according to the available hydrology. 2. Contractor technical team for punch list clearance related to Governor system and SCADA system were deputed from 11 April 2026 to 17 April 2026 rectified some of the pending issues. 3. Both cooling water pumps are running to maintain the required flow. However, proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and Energy loss in case of pump failure or flow/pressure. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-05-05 | 2026 | 5 | 5 | Koto HPS | 40.8 | 26.38 | 23.83 | 569750 | 565778 | 174.1 | 67.32 | 58.19 | 8.24 | 95.89 | 58 | 939000 | 7737625.81 | 4662011 | 3075615.09 | 3972 | Unit #02 and Unit #03 are on bar , delivering an average load of 23.83 MW. Unit #01 is on standby due to TRCM and cooling water strainer issues.. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-05 | 2026 | 5 | 5 | Machai HPS | 2.6 | 1.48 | 1.16 | 27920 | 27064 | 31.6 | 19 | 44.74 | 4.671 | 76.92 | 70 | 48000 | 222833.82 | 126416 | 96417.88 | 856 | Unit operated normally as per available inflow but tripped at 1534hrs due to 11kv line tripping from katlang grid while synchronized with the system at 1547hrs. | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-05-05 | 2026 | 5 | 5 | Malakand-3 HPS | 81 | 53 | 47 | 1129469 | 1119830 | 51 | 30.61 | 58.1 | 2.8627 | 94.34 | 77.5 | 1834000 | 5248898.97 | 3205737 | 2043161.63 | 9639 | Load variation is due to variation in the hydrology of River Swat. However, as per available hydrology from the Irrigation Department all three units are currently on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-05 | 2026 | 5 | 5 | Pehur HPS | 18 | 5.8 | 4.7 | 114100 | 112000 | 15.33 | 15 | 26.41 | 3.767 | 31.02 | 41 | 134000 | 505507.1 | 421904 | 83603.1 | 2100 | The plant remained shut down from 0000 hrs to 0300 hrs because there was no 132 kV supply available due to maintenance work at Gadoon Grid, as Gadoon Grid SSO Mr. Zahoor requested an NOC to de-energize the 132 kV Gadoon Grid - PHPC line. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-05 | 2026 | 5 | 5 | Reshun HPS | 4.2 | 2.19 | 1.28 | 29000 | 28455 | 1.82 | 1.77 | 28.77 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 383573 | 423544.7 | 545 | Outgoing Feeder Breaker remained Off due to line works and shortage of water for 2.50hours. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-05-06 | 2026 | 5 | 6 | Daral Khwar HPS | 36.6 | 36.6 | 36.3 | 872350 | 869550 | 27.14 | 14.54 | 99.31 | 8.2683 | 85.95 | 48 | 755000 | 6241232.9 | 7189700 | -948467.36 | 2800 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-06 | 2026 | 5 | 6 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 8.54 | 4 | 0 | 5.7092 | 98.86 | 79.57 | 242000 | 1383099.74 | 0 | 1383099.74 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 04.05.2026 to 10.05.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Generation_Data.xlsx
2026-05-06 | 2026 | 5 | 6 | Karora HPS | 11.8 | 11.85 | 11.61 | 278535 | 275744 | 12.85 | 9.26 | 98.35 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 2145288 | 33111.68 | 2791 | 1. Unit No. 01 and 02 on bar, collectively delivering an average load of 11.61 according to the available hydrology. 2. Contractor technical team for punch list clearance related to Governor system and SCADA system were deputed from 11 April 2026 to 17 April 2026 rectified some of the pending issues. 3. Both cooling water pumps are running to maintain the required flow. However, proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and Energy loss in case of pump failure or flow/pressure. 4. At the request of M/s GRC, the load on Units No. 01 & 02 was reduced to 2.8 MW each at 09:01 hrs. Unit 01 was then placed on FSNL at 09:03 hrs to allow an excavator to pass in front of the tailrace. Subsequently, both units were resynchronized with the national grid at 09:05 hrs. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-05-06 | 2026 | 5 | 6 | Koto HPS | 40.8 | 26.8 | 23.6 | 570500 | 565332 | 174.1 | 69.94 | 58.26 | 8.24 | 95.89 | 58 | 939000 | 7737625.81 | 4658336 | 3079290.13 | 5168 | Unit #02 and Unit #03 are on bar , delivering an average load of 23.60MW. Unit #01 is on standby due to TRCM and cooling water strainer issues.. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-06 | 2026 | 5 | 6 | Machai HPS | 2.6 | 1.28 | 1.24 | 30240 | 29348 | 31.6 | 19 | 48.46 | 4.671 | 76.92 | 70 | 48000 | 222833.82 | 137085 | 85749.31 | 892 | Smooth Operation as per available inflow | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-05-06 | 2026 | 5 | 6 | Malakand-3 HPS | 81 | 49 | 44.86 | 1076686 | 1066950 | 51 | 29.49 | 55.39 | 2.8627 | 94.34 | 77.5 | 1834000 | 5248898.97 | 3054358 | 2194541.2 | 9736 | As per available hydrology from the Irrigation Department all the three Units are on bar. Load variation is due to variation in the Hydrology of River Swat. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-06 | 2026 | 5 | 6 | Pehur HPS | 18 | 5.74 | 5.57 | 133900 | 129000 | 15.33 | 14 | 31 | 3.767 | 31.02 | 41 | 134000 | 505507.1 | 485943 | 19564.1 | 4900 | The plant remained operational throughout 24 hours as per available hydrilogy+irrigation valve opened. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-06 | 2026 | 5 | 6 | Reshun HPS | 4.2 | 2.2 | 1.38 | 33000 | 32435 | 2.06 | 2.02 | 32.74 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 437224 | 369893.7 | 565 | Outgoing feeder remained off 1.05hours for storage of water. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-05-07 | 2026 | 5 | 7 | Daral Khwar HPS | 36.6 | 36.6 | 36.5 | 877030 | 874230 | 27.14 | 14.62 | 99.84 | 8.2683 | 85.95 | 48 | 755000 | 6241232.9 | 7228396 | -987163.01 | 2800 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.5 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-07 | 2026 | 5 | 7 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 8.54 | 4 | 0 | 5.7092 | 98.86 | 79.57 | 242000 | 1383099.74 | 0 | 1383099.74 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 04.05.2026 to 10.05.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Generation_Data.xlsx
2026-05-07 | 2026 | 5 | 7 | Karora HPS | 11.8 | 11.8 | 11.59 | 278171 | 275376 | 12.85 | 9.26 | 98.22 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 2142425 | 35974.72 | 2795 | 1. Unit No. 01 and 02 on bar, collectively delivering an average load of 11.59MW according to the available hydrology. 2. Contractor's technical team for punch list activities' clearance, mainly related to the Governor system and SCADA system was deputed at site from 11 April 2026 to 17 April 2026 and rectified some of the pending issues. 3. Both of the cooling water pumps are running to maintain the required flow/pressure. However, proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and energy loss in case of any single pump failure or low flow/pressure issue. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-05-07 | 2026 | 5 | 7 | Koto HPS | 40.8 | 24.98 | 10.53 | 252750 | 251338 | 174.1 | 32.52 | 25.81 | 8.24 | 95.89 | 58 | 939000 | 7737625.81 | 2071025 | 5666600.69 | 1412 | The plant remain shutdown for more than 12 hours due to Trash Racks cleaning by hands. Main bottlenecks are non availability of Trash Racks cleaning machine and non functional strainers for cooling water lines. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-07 | 2026 | 5 | 7 | Machai HPS | 2.6 | 1.33 | 1.34 | 30544 | 29744 | 31.6 | 19 | 48.95 | 4.671 | 76.92 | 70 | 48000 | 222833.82 | 138934 | 83899.6 | 800 | Unit operating normally on available inflow but tripped 3 times due to line tripping from Katlang grid at 1014, 2228 & 2327 hrs and synched back at 1107, 2254 & 2349 hrs respectively. | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-05-07 | 2026 | 5 | 7 | Malakand-3 HPS | 81 | 57 | 49.46 | 1186973 | 1176940 | 51 | 31.34 | 61.06 | 2.8627 | 94.34 | 77.5 | 1834000 | 5248898.97 | 3369226 | 1879672.83 | 10033 | As per available hydrology from Irrigation Department all three units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-07 | 2026 | 5 | 7 | Pehur HPS | 18 | 5.53 | 5.3 | 126700 | 123000 | 15.33 | 15 | 29.33 | 3.767 | 31.02 | 41 | 134000 | 505507.1 | 463341 | 42166.1 | 3700 | The plant remained operational throughout 24 hours as per available hydrilogy+irrigation valve opened. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-07 | 2026 | 5 | 7 | Reshun HPS | 4.2 | 2.38 | 1.4 | 31000 | 30464 | 1.93 | 1.89 | 30.75 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 410655 | 396462.7 | 536 | outgoing feeder breaker tripped 01 time due to line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-05-08 | 2026 | 5 | 8 | Daral Khwar HPS | 36.6 | 36.6 | 36.4 | 872630 | 869830 | 27.14 | 14.55 | 99.34 | 8.2683 | 85.95 | 48 | 755000 | 6241232.9 | 7192015 | -950782.49 | 2800 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.4 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-08 | 2026 | 5 | 8 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 8.54 | 4 | 0 | 5.7092 | 98.86 | 79.57 | 242000 | 1383099.74 | 0 | 1383099.74 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 04.05.2026 to 10.05.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Generation_Data.xlsx
2026-05-08 | 2026 | 5 | 8 | Karora HPS | 11.8 | 11.8 | 11.43 | 274307 | 271622 | 12.99 | 9.2 | 96.86 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 2113219 | 65180.84 | 2685 | 1. Unit No. 01 and 02 on bar, collectively delivering an average load of 11.43 MW according to the available hydrology. 2. At 12:42 HR,s, Unit No. 01 tripped. Upon inspection, it was found that the F512 relay and 86T2 lockout relay had tripped. Both relays were reset, and the GCB close command was initiated twice from SCADA; however, the unit failed to synchronize automatically and timed out. Subsequently, the unit was successfully synchronized manually from the local control panel at 13:04 HR,s 3. Contractor's technical team for punch list activities' clearance, mainly related to the Governor system and SCADA system was deputed at site from 11 April 2026 to 17 April 2026 and rectified some of the pending issues. 4. Both of the cooling water pumps are running to maintain the required flow/pressure. However, proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and energy loss in case of any single pump failure or low flow/pressure issue. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-05-08 | 2026 | 5 | 8 | Koto HPS | 40.8 | 27.08 | 25.95 | 622750 | 619797 | 174.1 | 80.13 | 63.6 | 8.24 | 95.89 | 58 | 939000 | 7737625.81 | 5107127 | 2630498.53 | 2953 | The shortfall in required production is due to non-functional strainers installed on the cooling water lines, making it impossible to operate all three units simultaneously. A secondary bottleneck is the unavailability of the Trash Rack Cleaning Machine (TRCM). | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-08 | 2026 | 5 | 8 | Machai HPS | 2.6 | 1.89 | 1.58 | 37096 | 36124 | 20 | 22 | 59.45 | 4.671 | 76.92 | 70 | 48000 | 222833.82 | 168735 | 54098.62 | 972 | Unit tripped at 2302hrs due to 132kv line tripped, and 11kv line restored at 2338hrs, while Unit synchronized with the system at 2347hrs. | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-05-08 | 2026 | 5 | 8 | Malakand-3 HPS | 81 | 60 | 54 | 1296055 | 1285600 | 51 | 32.93 | 66.67 | 2.8627 | 94.34 | 77.5 | 1834000 | 5248898.97 | 3680287 | 1568611.85 | 10455 | As per available hydrology from Irrigation Department all three units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-08 | 2026 | 5 | 8 | Pehur HPS | 18 | 7.16 | 5.57 | 133700 | 130000 | 15.35 | 15 | 30.95 | 3.767 | 31.02 | 41 | 134000 | 505507.1 | 489710 | 15797.1 | 3700 | Maximum operating head for unit#03 is achived therefore, unit #03 taken on bar while unit #02 taken off the bar (operating head dropped). Unit#01= 2.0 mw load. unit#03= 4.8 mw load. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-08 | 2026 | 5 | 8 | Reshun HPS | 4.2 | 2.13 | 1.38 | 31000 | 30423 | 1.93 | 1.89 | 30.75 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 410102 | 397015.7 | 577 | Outgoing feeder remained Off 0.30 hour due to line fault and storage of water. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-05-09 | 2026 | 5 | 9 | Daral Khwar HPS | 36.6 | 36.6 | 36.3 | 871570 | 868770 | 27.14 | 14.53 | 99.22 | 8.2683 | 85.95 | 48 | 755000 | 6241232.9 | 7183251 | -942018.09 | 2800 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-09 | 2026 | 5 | 9 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 8.54 | 4 | 0 | 5.7092 | 98.86 | 79.57 | 242000 | 1383099.74 | 0 | 1383099.74 | 0 | The power house is still shutdown due to the collapsing of Tower # 29 of the 132 KV Transmission line which occurred as a result of extreme snowfall and wind during the night of 23.01.2026. Shutdown permit extended from 04.05.2026 to 10.05.2026 , for the erection of collapsed Tower No. 29 and associated stringing works. | faizanbabar5@gmail.com | Original | Avg Historical Hydrology filled with plant-month median; Actual Avg Cumic filled with plant-month median | Generation_Data.xlsx
2026-05-09 | 2026 | 5 | 9 | Karora HPS | 11.8 | 11.9 | 11.04 | 265063 | 262432 | 12.99 | 8.87 | 93.6 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 2041721 | 136679.04 | 2631 | 1. Unit No. 01 and 02 on bar, collectively delivering an average load of 11.04MW according to the available hydrology. 2. It was observed that the water level at the sand trap was gradually decreasing due to blockage at the intake trash rack. Therefore, at 16:33 hrs, the plant was shut down to facilitate cleaning of the intake trash rack. The cleaning activity was successfully completed, and Unit #02 and Unit #01 were subsequently synchronized with the grid at 17:40 hrs and 17:48 hrs, respectively. 3. Contractor's technical team for punch list activities' clearance, mainly related to the Governor system and SCADA system was deputed at site from 11 April 2026 to 17 April 2026 and rectified some of the pending issues. 4. Both of the cooling water pumps are running to maintain the required flow/pressure. However, proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and energy loss in case of any single pump failure or low flow/pressure issue. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-05-09 | 2026 | 5 | 9 | Koto HPS | 40.8 | 26.42 | 26.26 | 630250 | 628237 | 174.1 | 81.1 | 64.36 | 8.24 | 95.89 | 58 | 939000 | 7737625.81 | 5176673 | 2560952.93 | 2013 | Targeted power generation was not met due to two critical plant bottlenecks: Malfunctioning strainers failing to maintain cooling water pressure for tri-unit operation, and the absence of a Trash Rack Cleaning Machine. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-09 | 2026 | 5 | 9 | Machai HPS | 2.6 | 1.85 | 1.52 | 37896 | 37136 | 20 | 22 | 60.73 | 4.671 | 76.92 | 70 | 48000 | 222833.82 | 173462 | 49371.57 | 760 | Unit tripped twice due to Machai 11 KV line tripping from PESCO: Katlang grid, without informing; due to which wastage of generation occurred for almost 2 hours. | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-05-09 | 2026 | 5 | 9 | Malakand-3 HPS | 81 | 60 | 55.67 | 1335972 | 1325380 | 51 | 35.14 | 68.72 | 2.8627 | 94.34 | 77.5 | 1834000 | 5248898.97 | 3794165 | 1454733.64 | 10592 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-09 | 2026 | 5 | 9 | Pehur HPS | 18 | 7.42 | 7.17 | 172200 | 168000 | 15.33 | 18 | 39.86 | 3.767 | 31.02 | 41 | 134000 | 505507.1 | 632856 | -127348.9 | 4200 | Plant operational 24 hrs as per available hydrology | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-09 | 2026 | 5 | 9 | Reshun HPS | 4.2 | 1.96 | 1.04 | 24000 | 23475 | 1.56 | 1.46 | 23.81 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 316443 | 490674.7 | 525 | Outgoing feeder breaker remaine Off 5.20hours due to mechanical works at Intake Gates No.1. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-05-10 | 2026 | 5 | 10 | Daral Khwar HPS | 36.6 | 36.6 | 33.7 | 809760 | 807360 | 27.14 | 13.5 | 92.19 | 8.2683 | 85.95 | 48 | 755000 | 6241232.9 | 6675495 | -434261.78 | 2400 | 1. Units No. 01,02 and 03 were on bar delivering an average load equal to 33.7 MW according to the available hydrology. 2. Plant tripped at 1730 Hrs due to the fluctuations in 132 kV line. 3. Unit No. 03 synchronized at 1740 Hrs, and Units No. 01 and 02 synchronized at 1801 Hrs. 4. 132 kV line tripped at 1818 Hrs causing in Plant shutdown. The line restored at 1908 Hrs. 5. Units No. 02,03 and 01 synchronized at 1927 Hrs, 1928 Hrs and 1934 Hrs respectively. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-10 | 2026 | 5 | 10 | Jabori HPS | 10.2 | 5.1 | 5.1 | 90979 | 89370 | 9.65 | 2.97 | 37.16 | 5.7092 | 98.86 | 79.57 | 242000 | 1383099.74 | 510231 | 872868.54 | 1609 | 132KV supply restored at 1616 Hrs dated 09-05-2026 after erection of collapsed Tower and clearing fault on Transmission line. After preliminary check and inspection of powerhouse, unit #01 was run on Full speed no load (FSNL) to dry stator from moisture and subsequently unit #01 was synchronized with the national grid at 0356 Hrs dated 10-05-2026. Unit #02 is in stop state due to fault in governor system. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-05-10 | 2026 | 5 | 10 | Karora HPS | 11.8 | 11.88 | 9.24 | 223796 | 221683 | 12.99 | 9.24 | 79.02 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1724694 | 453706.26 | 2113 | 1. Unit No. 01 and 02 on bar, collectively delivering an average load of 9.24MW according to the available hydrology. 2 At 18:50 hrs, Unit #01 tripped due to a unit frequency fault and governor system fault. Similarly, at 19:32 hrs, Unit #02 also tripped, and upon inspection, it was observed that the 86T2 relay had operated. 3 At 19:35 hrs, the gate operator at the weir site informed the CCR of heavy flash flooding and muddy flow caused by intense rainfall at upstream of the weir. The shift engineer was accordingly notified that the channel gate had been closed as a precautionary measure. Similarly, both unit main inlet valves were also closed to ensure safe operation. 4 Contractor's technical team for punch list activities' clearance, mainly related to the Governor system and SCADA system was deputed at site from 11 April 2026 to 17 April 2026 and rectified some of the pending issues. 5 Both of the cooling water pumps are running to maintain the required flow/pressure. However, proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and energy loss in case of any single pump failure or low flow/pressure issue. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-05-10 | 2026 | 5 | 10 | Koto HPS | 40.8 | 26.52 | 22.54 | 537420 | 537120 | 174.1 | 69.61 | 54.88 | 8.24 | 95.89 | 58 | 939000 | 7737625.81 | 4425869 | 3311757.01 | 300 | Tripping of 132kV lines resulted in tripping of running units at Koto HPC. Tripping restricted power generation. Main Bottlenecks for Koto HPC are non-functional strainers on cooling water line and non-availability of Trash Racks cleaning machine. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-10 | 2026 | 5 | 10 | Machai HPS | 2.6 | 1.74 | 1.14 | 28124 | 27500 | 16 | 22 | 45.07 | 4.671 | 76.92 | 70 | 48000 | 222833.82 | 128453 | 94381.32 | 624 | Unit tripped at 1757 hrs. with Machai 11 KV line tripping from PESCO Katlang grid, due to very bad weather conditions; while remained still due to fault on 11 KV line for the rest of the hours. | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-05-10 | 2026 | 5 | 10 | Malakand-3 HPS | 81 | 57 | 47.66 | 1143923 | 1134480 | 51 | 33.23 | 58.84 | 2.8627 | 94.34 | 77.5 | 1834000 | 5248898.97 | 3247676 | 2001223.07 | 9443 | As per information received from the Irrigation Department, the water supply has been reduced due to gate repair work at Dargai Head. Consequently, the load was reduced accordingly. As per available hydrology from the Irrigation Department all the three Units are on bar. Units tripped due to tripping of 132KV supply at 17:44 hrs caused by heavy rain, wind, and thunderstorm, Informed RCC . After restoration of 132KV supply lines, Unit # 01, 02 & 03 synchronized with the system at 19:45 hrs, 19:35 hrs & 19:50 hrs respectively. Due to rainfall in the catchment area, inflow is muddy with heavy trashes accumulation at the Forebay, resulting in reduced load. However, as per available hydrology from the Irrigation Department, all three units are currently on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-10 | 2026 | 5 | 10 | Pehur HPS | 18 | 7.7 | 5.7 | 136700 | 132000 | 15.33 | 14 | 31.64 | 3.767 | 31.02 | 41 | 134000 | 505507.1 | 497244 | 8263.1 | 4700 | Plant remained shutdown for about 05 hrs due to failure of 132 KV line because of heavy rain storm. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-10 | 2026 | 5 | 10 | Reshun HPS | 4.2 | 1.91 | 1.26 | 28000 | 27424 | 1.75 | 1.65 | 27.78 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 369676 | 437441.7 | 576 | Outgoing feeder Breaker remained Off for 4.55 hours due to line heavy wind/line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-05-11 | 2026 | 5 | 11 | Daral Khwar HPS | 36.6 | 36.6 | 36.3 | 872040 | 869240 | 27.14 | 14.54 | 99.28 | 8.2683 | 85.95 | 48 | 755000 | 6241232.9 | 7187137 | -945904.19 | 2800 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-11 | 2026 | 5 | 11 | Jabori HPS | 10.2 | 5.1 | 5.1 | 122715 | 121200 | 8.54 | 4.01 | 50.13 | 5.7092 | 98.86 | 79.57 | 242000 | 1383099.74 | 691955 | 691144.7 | 1515 | Unit 01 was on bar delivering average load of 5.1MW to the system while unit 02 standstill due to Scada issue. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-05-11 | 2026 | 5 | 11 | Karora HPS | 11.8 | 0 | 0 | 0 | 0 | 13.41 | 0 | 0 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 0 | 2178400 | 0 | 1. The complex remains shut down due to flash flooding and excessive muddy water flow at the upstream side of the weir 2. Contractor's technical team for punch list activities' clearance, mainly related to the Governor system and SCADA system was deputed at site from 11 April 2026 to 17 April 2026 and rectified some of the pending issues. 3. Both of the cooling water pumps are running to maintain the required flow/pressure. However, proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and energy loss in case of any single pump failure or low flow/pressure issue. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-05-11 | 2026 | 5 | 11 | Koto HPS | 40.8 | 26.9 | 24.79 | 595000 | 590760 | 174.1 | 76.56 | 60.76 | 8.24 | 95.89 | 58 | 939000 | 7737625.81 | 4867862 | 2869763.41 | 4240 | Despite the exhaustive efforts of our limited maintenance staff to perform repeated manual cleaning, the non-functional strainers cannot maintain adequate water pressure. Furthermore, frequent trash rack choking is causing significant head loss. These technical bottlenecks, combined with a shortage of personnel, are severely impacting power generation and resulting in deficient output at the Koto Hydropower Plant. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-11 | 2026 | 5 | 11 | Machai HPS | 2.6 | 1.78 | 0.34 | 10784 | 10428 | 17 | 22 | 17.28 | 4.671 | 76.92 | 70 | 48000 | 222833.82 | 48709 | 174124.63 | 356 | (1) Previous day line restored at 1117 hrs., while unit synched at 1132 hrs.; which tripped again at 1139 hrs. due to governor fault. Meanwhile unit remained still due to governor fault till 1715 hrs.. (2) Unit tripped twice due to 11 KV line tripping from PESCO Katlang grid, due to bad weather condition. | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-05-11 | 2026 | 5 | 11 | Malakand-3 HPS | 81 | 60 | 54.27 | 1302528 | 1292480 | 51 | 35.6 | 67 | 2.8627 | 94.34 | 77.5 | 1834000 | 5248898.97 | 3699982 | 1548916.47 | 10048 | Due to Heavy rainfall in the catchment area, the inflow is muddy with heavy trash accumulation at the Forebay, resulting in reduced load. However, as per the available hydrology from the Irrigation Department, all three units are currently on bar. Load variation is due to fluctuations in the hydrology of River Swat. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-11 | 2026 | 5 | 11 | Pehur HPS | 18 | 7.4 | 2.27 | 54500 | 53000 | 15.33 | 6 | 12.62 | 3.767 | 31.02 | 41 | 134000 | 505507.1 | 199651 | 305856.1 | 1500 | Plant shut down since 0850 hrs due to nil irrigation demand as per irrigation SDO request. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-11 | 2026 | 5 | 11 | Reshun HPS | 4.2 | 1.95 | 1.34 | 30000 | 29485 | 1.9 | 1.83 | 29.76 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 397458 | 409659.7 | 515 | Outgoing feeder breaker remained Off due to heavy wind for 2.05hours. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-05-12 | 2026 | 5 | 12 | Daral Khwar HPS | 36.6 | 36.6 | 36.1 | 866120 | 863320 | 27.14 | 14.44 | 98.6 | 8.2683 | 85.95 | 48 | 755000 | 6241232.9 | 7138189 | -896955.85 | 2800 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.1 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-12 | 2026 | 5 | 12 | Jabori HPS | 10.2 | 10.2 | 6.8 | 150440 | 148920 | 8.54 | 4.92 | 61.45 | 5.7092 | 98.86 | 79.57 | 242000 | 1383099.74 | 850214 | 532885.68 | 1520 | Both units (01 & 02) were operational delivering an average load equals to 6.84 MW to the national grid as per available hydrology. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-05-12 | 2026 | 5 | 12 | Karora HPS | 11.8 | 0 | 0 | 0 | 0 | 12.85 | 0 | 0 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 0 | 2178400 | 0 | 1) The complex remains shut down due to flash flooding and excessive muddy water flow at the upstream side of the weir. 2) Contractor's technical team for punch list activities' clearance, mainly related to the Governor system and SCADA system was deputed at site from 11 April 2026 to 17 April 2026 and rectified some of the pending issues. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-05-12 | 2026 | 5 | 12 | Koto HPS | 40.8 | 26.88 | 17.67 | 424000 | 416555 | 174.1 | 54.56 | 43.3 | 8.24 | 95.89 | 58 | 939000 | 7737625.81 | 3432413 | 4305212.61 | 7445 | Power generation at Koto HPC was curtailed today to facilitate trash racks cleaning. This hectic manual cleaning was performed by the maintenance crew of Koto HPC. System efficiency is currently hampered by two critical factors: non-functional cooling water strainers and the lack of a Trash Rack Cleaning Machine (TRCM). | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-12 | 2026 | 5 | 12 | Machai HPS | 2.6 | 2.07 | 1.51 | 36288 | 35464 | 17 | 21 | 58.15 | 4.671 | 76.92 | 70 | 48000 | 222833.82 | 165652 | 57181.48 | 824 | Unit stopped at 1806 hrs. due to flushing of water, while resynched at 1946 hrs.. | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-05-12 | 2026 | 5 | 12 | Malakand-3 HPS | 81 | 59 | 54.92 | 1318195 | 1307610 | 51 | 37.11 | 67.81 | 2.8627 | 94.34 | 77.5 | 1834000 | 5248898.97 | 3743295 | 1505603.82 | 10585 | Due to Heavy rainfall in the catchment area, the inflow is muddy with heavy trash accumulation at the Forebay, resulting in reduced load. However, as per the available hydrology from the Irrigation Department, all three units are currently on bar. Load variation is due to fluctuations in the hydrology of River Swat. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-12 | 2026 | 5 | 12 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 15.33 | 0 | 0 | 3.767 | 31.02 | 41 | 134000 | 505507.1 | 0 | 505507.1 | 0 | Plant shut down since 0850 hrs dated 11-05-2026, due to nil irrigation demand. And unstable 132KV line supply from Gadoon grid due to fault on 132 KV Wah-Gadoon feeding line. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-12 | 2026 | 5 | 12 | Reshun HPS | 4.2 | 1.8 | 1.14 | 27000 | 26448 | 1.65 | 1.75 | 26.79 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 356519 | 450598.7 | 552 | Outgoing Feeder Breaker remained Off 1.14hours due to line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-05-13 | 2026 | 5 | 13 | Daral Khwar HPS | 36.6 | 36.6 | 36.4 | 873470 | 870670 | 27.14 | 14.56 | 99.44 | 8.2683 | 85.95 | 48 | 755000 | 6241232.9 | 7198961 | -957727.86 | 2800 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.4 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-13 | 2026 | 5 | 13 | Jabori HPS | 10.2 | 10.2 | 8.94 | 196760 | 195120 | 8.54 | 6.43 | 80.38 | 5.7092 | 98.86 | 79.57 | 242000 | 1383099.74 | 1113979 | 269120.64 | 1640 | Unit 01 and 02 were on bar delivering an average load equals to 8.94 MW. 132 KV line tripped at 1755 Hrs while restored at 1810 Hrs. Unit 01 and 02 was synchronized at 1821 Hrs. 132 KV line tripped again at 1832 Hrs while restored at 1945 Hrs. Unit 01 and 02 were resynchronized at 1955 Hrs. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-05-13 | 2026 | 5 | 13 | Karora HPS | 11.8 | 0 | 0 | 0 | 0 | 13.41 | 0 | 0 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 0 | 2178400 | 0 | 1 The complex remains shut down due to flash flooding and excessive muddy water flow at the upstream side of the weir 2 Contractor's technical team for punch list activities' clearance, mainly related to the Governor system and SCADA system was deputed at site from 11 April 2026 to 17 April 2026 and rectified some of the pending issues. 3 Both of the cooling water pumps are running to maintain the required flow/pressure. However, proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and energy loss in case of any single pump failure or low flow/pressure issue. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-05-13 | 2026 | 5 | 13 | Koto HPS | 40.8 | 26.9 | 26.71 | 642527 | 641000 | 174.1 | 42.48 | 65.62 | 8.24 | 95.89 | 58 | 939000 | 7737625.81 | 5281840 | 2455785.81 | 1527 | Unit#02 and 03 on bar delivering average load of 26.71MW and unit#01 on standby due to cooling water strainer issue. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-13 | 2026 | 5 | 13 | Machai HPS | 2.6 | 1.52 | 1.21 | 33720 | 32868 | 31 | 20 | 54.04 | 4.671 | 76.92 | 70 | 48000 | 222833.82 | 153526 | 69307.39 | 852 | Unit Operates Normally | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-05-13 | 2026 | 5 | 13 | Malakand-3 HPS | 81 | 59 | 51.1 | 1226508 | 1216320 | 51 | 38.07 | 63.09 | 2.8627 | 94.34 | 77.5 | 1834000 | 5248898.97 | 3481959 | 1766939.7 | 10188 | Unit # 01, 02 & 03 were desynchronized from the system at 18:37Hrs to avoid flooding in the drainage pit. However, all other pumps were not sucking water due to trash coming from the forebay during cleaning of trash racks at the sediment excluder and forebay, which got stuck in the non-return valves (NRVs). At that time, only Drainage Pump No. 2 was in operation; however, its discharge was very low and it was unable to control the water level in the drainage pit. Unit # 01, 02 & 03 synchronized with the system at 20:31, 20:34 & 2054Hrs after rectification of drainage pit pumps. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-13 | 2026 | 5 | 13 | Pehur HPS | 18 | 6.76 | 3.05 | 73000 | 71000 | 15.33 | 7 | 16.9 | 3.767 | 31.02 | 41 | 134000 | 505507.1 | 267457 | 238050.1 | 2000 | Generation is less because of nil irrigation demand. At 0900 Hrs unit 1 started and after increase in irrigation demand at 1800 hrs unit 3 taken on bar. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-13 | 2026 | 5 | 13 | Reshun HPS | 4.2 | 2.09 | 1.15 | 26000 | 25428 | 1.69 | 1.59 | 25.79 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 342769 | 464348.7 | 572 | Line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-05-14 | 2026 | 5 | 14 | Daral Khwar HPS | 36.6 | 36.6 | 36.5 | 874800 | 872000 | 27.14 | 14.58 | 99.59 | 8.2683 | 85.95 | 48 | 755000 | 6241232.9 | 7209958 | -968724.7 | 2800 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.5 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-14 | 2026 | 5 | 14 | Jabori HPS | 10.2 | 10.2 | 9.7 | 233180 | 231530 | 8.54 | 7.62 | 95.25 | 5.7092 | 98.86 | 79.57 | 242000 | 1383099.74 | 1321851 | 61248.67 | 1650 | Unit 01 and 02 were on the bar delivering an average load equals to 9.72 MW to the national grid according to available hydrology. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-05-14 | 2026 | 5 | 14 | Karora HPS | 11.8 | 11.81 | 5.94 | 142596 | 141683 | 13.41 | 4.98 | 50.35 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1102294 | 1076106.26 | 913 | 1: Unit No. 01 and 02 on bar, collectively delivering an average load of 5.94 MW according to the available hydrology. 2 At 11:21 hrs, Unit # 01 was synchronized with the grid and its load was gradually increased to 5.9 MW. Subsequently, at 11:43 hrs, Unit # 02 synchronized with the grid and its load was also gradually increased to 5.9MW. 3 Contractor's technical team for punch list activities' clearance, mainly related to the Governor system and SCADA system was deputed at site from 11 April 2026 to 17 April 2026 and rectified some of the pending issues. 4 Both cooling water pumps are running to maintain the required flow. However, proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and Energy loss in case of pump failure or flow/pressure. 5 At 17:43 hrs, Unit #01 electrically tripped and was subsequently resynchronized with the grid: the load was then gradually increased to 5.9MW. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-05-14 | 2026 | 5 | 14 | Koto HPS | 40.8 | 27.02 | 26.73 | 641500 | 640090 | 174.1 | 82.55 | 65.51 | 8.24 | 95.89 | 58 | 939000 | 7737625.81 | 5274342 | 2463284.21 | 1410 | Unit#2 and unit#03 on bar delivering average load of 26.73MW and unit#01 on standby due to cooling water strainer issue. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-14 | 2026 | 5 | 14 | Machai HPS | 2.6 | 1.76 | 1.12 | 26308 | 25740 | 31 | 20 | 42.16 | 4.671 | 76.92 | 70 | 48000 | 222833.82 | 120232 | 102602.28 | 568 | Unit normally stopped at 0802 due to permit taken from Katlang grid PTW#683 for trimming of tree branches while line restored at 1350 and unit synced with system at 1357 | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-05-14 | 2026 | 5 | 14 | Malakand-3 HPS | 81 | 59 | 55.6 | 1334382 | 1323800 | 51 | 36.57 | 68.64 | 2.8627 | 94.34 | 77.5 | 1834000 | 5248898.97 | 3789642 | 1459256.71 | 10582 | As per available hydrology from the Irrigation Department all the three Units are on bar. Load variation is due to fluctuations in the hydrology of River Swat. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-14 | 2026 | 5 | 14 | Pehur HPS | 18 | 5.91 | 4.02 | 96500 | 93000 | 15.33 | 10 | 22.34 | 3.767 | 31.02 | 41 | 134000 | 505507.1 | 350331 | 155176.1 | 3500 | Generation is less because of unit 3 remained off the bar from 0100 hrs to 1340 hrs due to excitation system fault. At 1605 hrs unit # 3 again tripped due to the said fault. After that keeping in view the available operating head for unit # 2, it was taken on bar at 1755 hrs along with unit # 1. Also the irrigation valves open. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-14 | 2026 | 5 | 14 | Reshun HPS | 4.2 | 1.94 | 1.32 | 31000 | 30428 | 1.93 | 1.89 | 30.75 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 410169 | 396948.7 | 572 | works in line. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-05-15 | 2026 | 5 | 15 | Daral Khwar HPS | 36.6 | 36.6 | 36.6 | 877600 | 874400 | 14.27 | 14.62 | 99.91 | 8.2683 | 85.95 | 48 | 755000 | 6241232.9 | 7229802 | -988568.62 | 3200 | Units No. 01,02 and 03 were on bar delivering an average load equal to 36.6 MW according to the available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-15 | 2026 | 5 | 15 | Jabori HPS | 10.2 | 10.2 | 9.8 | 226450 | 224840 | 8.54 | 7.4 | 92.5 | 5.7092 | 98.86 | 79.57 | 242000 | 1383099.74 | 1283657 | 99443.21 | 1610 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 9.85 MW to the national grid according to the available hydrology. 2: The 132 kV line tripped at 0942 Hrs. The line was restored at 1015 Hrs, and Units 01 and 02 were subsequently synchronized at 1055 Hrs. Cleaning of strainer was carried out during line trip period. 3: Cooling Water Pump #02 has remained non-functional since 12-10-2025. The contractor has already been formally intimated regarding the issue. The non-availability of a standby pump poses a significant risk of forced unit shutdown and consequent generation loss in the event of pump failure or low flow/pressure conditions. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-05-15 | 2026 | 5 | 15 | Karora HPS | 11.8 | 11.7 | 8.87 | 212805 | 210342 | 13.41 | 6.77 | 75.14 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1636461 | 541939.24 | 2463 | 1: Unit No. 01 and 02 on bar, collectively delivering an average load of 8.87 MW according to the available hydrology. 2: At 09:43 hrs, both Khan Khwar and Dubair Khwar lines tripped. Both lines were restored at 10:47 hrs. 3: At 11:40 hrs, Unit # 02 was synchronized with the grid and its load was gradually increased to 5.9 MW. Subsequently, at 12:07 hrs, Unit # 01 synchronized with the grid and its load was also gradually increased to 5.9MW. 4: Both cooling water pumps are running to maintain the required flow. However, proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and Energy loss in case of pump failure or flow/pressure. 5: Contractor's technical team for punch list activities' clearance, mainly related to the Governor system and SCADA system was deputed at site from 11 April 2026 to 17 April 2026 and rectified some of the pending issues. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-05-15 | 2026 | 5 | 15 | Koto HPS | 40.8 | 27.23 | 26.4 | 624000 | 622275 | 174.1 | 80.29 | 63.73 | 8.24 | 95.89 | 58 | 939000 | 7737625.81 | 5127546 | 2610079.81 | 1725 | Unit no 01 and unit 2 are running on bar while and unit no 03 is on standby due to a cooling water strainer issue. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-15 | 2026 | 5 | 15 | Machai HPS | 2.6 | 1.78 | 1.3 | 30744 | 29876 | 31 | 25 | 49.27 | 4.671 | 76.92 | 70 | 48000 | 222833.82 | 139551 | 83283.03 | 868 | Unit tripped due to reverse power fault at 0250 and 0510 while synced with system at 0312 and 0752 | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-05-15 | 2026 | 5 | 15 | Malakand-3 HPS | 81 | 59 | 54.58 | 1310003 | 1299800 | 51 | 36.99 | 67.39 | 2.8627 | 94.34 | 77.5 | 1834000 | 5248898.97 | 3720937 | 1527961.51 | 10203 | 132kv line DRG1&2 Tripped at 22.20hrs ,supply resorted at 22:30hrs and unit # 02 synchronized with the system at 22.45hrs,unit 03, 22:57hrs and unit # 01 at 23:00hrs and As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-15 | 2026 | 5 | 15 | Pehur HPS | 18 | 5.51 | 5.07 | 121900 | 118000 | 15.33 | 15 | 28.22 | 3.767 | 31.02 | 41 | 134000 | 505507.1 | 444506 | 61001.1 | 3900 | Plant remained operational throughout 24 hrs as per available hydrology + irrigation valve open. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-15 | 2026 | 5 | 15 | Reshun HPS | 4.2 | 2.22 | 1.49 | 36000 | 35680 | 2.28 | 2.2 | 35.71 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 480966 | 326151.7 | 320 | line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-05-16 | 2026 | 5 | 16 | Daral Khwar HPS | 36.6 | 36.6 | 36.6 | 879150 | 876350 | 27.14 | 14.66 | 100.09 | 8.2683 | 85.95 | 48 | 755000 | 6241232.9 | 7245925 | -1004691.8 | 2800 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.6 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-16 | 2026 | 5 | 16 | Jabori HPS | 10.2 | 10.3 | 10.28 | 246675 | 245180 | 8.54 | 8.06 | 100.77 | 5.7092 | 98.86 | 79.57 | 242000 | 1383099.74 | 1399782 | -16681.91 | 1495 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 10.28 MW to the national grid according to the available hydrology. 2: Cooling Water Pump #02 has remained non-functional since 12-10-2025. The contractor has already been formally intimated regarding the issue. The non-availability of a standby pump poses a significant risk of forced unit shutdown and consequent generation loss in the event of pump failure or low flow/pressure conditions. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-05-16 | 2026 | 5 | 16 | Karora HPS | 11.8 | 11.81 | 9.29 | 222883 | 220361 | 12.85 | 7.25 | 78.7 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1714409 | 463991.42 | 2522 | 1: Unit No. 01 and 02 on bar, collectively delivering an average load of 9.29MW according to the available hydrology. 2: At 6:13 hrs, Complex Shutdown for trash rack cleaning, Unit # 02 was synchronized with the grid at 7:24 hrs and its load gradually increased to 5.9 MW. Subsequently, at 07:33 hrs, Unit # 01 synchronized with the grid and its load was also gradually increased to 5.9MW. 3: Both cooling water pumps are running to maintain the required flow. However, proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and Energy loss in case of pump failure or flow/pressure. 4: The increase in leakages through the under-sluice gates has adversely affected the adequate inflow of water into the intake channel 5: No rectification work on punch list items related to power house has been carried out since 17-April-2026. Except for the installation of motors at the intake side by the sub-contractor, without any effective supervision. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-05-16 | 2026 | 5 | 16 | Koto HPS | 40.8 | 27.17 | 26.18 | 634750 | 627928 | 174.1 | 73.39 | 64.82 | 8.24 | 95.89 | 58 | 939000 | 7737625.81 | 5174127 | 2563499.09 | 6822 | Unit #01 and Unit #02 are on bar , delivering an average load of 26.18MW. Unit #03 is on standby due to TRCM and cooling water strainer issues.. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-16 | 2026 | 5 | 16 | Machai HPS | 2.6 | 1.87 | 1.61 | 38104 | 37180 | 32 | 23 | 61.06 | 4.671 | 76.92 | 70 | 48000 | 222833.82 | 173668 | 49166.04 | 924 | Unit tripped due to tripping from Katlang Grid at 1318 while line restored at 1340 and unit synced with system at | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-05-16 | 2026 | 5 | 16 | Malakand-3 HPS | 81 | 57 | 53.68 | 1288201 | 1277890 | 51 | 35.36 | 66.27 | 2.8627 | 94.34 | 77.5 | 1834000 | 5248898.97 | 3658216 | 1590683.26 | 10311 | As per available hydrology from the Irrigation Department all the three Units are on bar. Load variation is due to fluctuations in the hydrology of River Swat. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-16 | 2026 | 5 | 16 | Pehur HPS | 18 | 6.35 | 5.28 | 126700 | 124000 | 15.33 | 18 | 29.33 | 3.767 | 31.02 | 41 | 134000 | 505507.1 | 467108 | 38399.1 | 2700 | Plant remained out of the system for 01 hour due to the tripping of the 132 KV Pehur-Gadoon circuit breaker. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-16 | 2026 | 5 | 16 | Reshun HPS | 4.2 | 1.81 | 1.32 | 29000 | 28694 | 1.82 | 1.77 | 28.77 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 386795 | 420322.7 | 306 | outgoing feeder breaker remained Off 1.25hours due to lines faults | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-05-17 | 2026 | 5 | 17 | Daral Khwar HPS | 36.6 | 36.6 | 36.6 | 878970 | 876170 | 27.14 | 14.65 | 100.06 | 8.2683 | 85.95 | 48 | 755000 | 6241232.9 | 7244436 | -1003203.51 | 2800 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.6 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-17 | 2026 | 5 | 17 | Jabori HPS | 10.2 | 10.2 | 9.95 | 238810 | 237320 | 8.54 | 7.8 | 97.55 | 5.7092 | 98.86 | 79.57 | 242000 | 1383099.74 | 1354907 | 28192.4 | 1490 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 9.95 MW to the national grid according to the available hydrology. 2: plant was shutdown normally at 2122 Hrs for cleaning of cooling water strainer. Both the units were resynchronized at 2201 Hrs with the national grid. 3: Cooling Water Pump #02 has remained non-functional since 12-10-2025. The contractor has already been formally intimated regarding the issue. The non-availability of a standby pump poses a significant risk of forced unit shutdown and consequent generation loss in the event of pump failure or low flow/pressure conditions. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-05-17 | 2026 | 5 | 17 | Karora HPS | 11.8 | 10.28 | 5.68 | 136395 | 134769 | 12.85 | 7.25 | 48.16 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1048503 | 1129897.18 | 1626 | 1: Unit No. 01 and 02 on bar, collectively delivering an average load of 5.68 MW as per available head. . 2: At 15:27 hrs, the Complex was shutdown to stop leakages, ensure complete closure of the under-sluice gates, and clean the intake trash rack for operation at rated capacity. However, the contractor failed to close the under-sluice gates. One gate, manually operated, became stuck at approximately 30-40% opening. To relieve hydraulic pressure and facilitate its closure, the 2nd gate was fully opened through motorized control by the contractor. Despite repeated attempts, both gates could not be closed successfully. Consequently, the complex was remained under shutdown since 15:27 hrs. 3: Both cooling water pumps are running to maintain the required flow. However, proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and Energy loss in case of pump failure or flow/pressure. 4: No rectification work on punch list items related to power house has been carried out since 17-April-2026. Except for the installation of motors at the intake side by the sub-contractor, without any effective supervision. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-05-17 | 2026 | 5 | 17 | Koto HPS | 40.8 | 26.65 | 25.16 | 604250 | 600013 | 174.1 | 75.33 | 61.71 | 8.24 | 95.89 | 58 | 939000 | 7737625.81 | 4944107 | 2793518.69 | 4237 | Unit #01 and Unit #02 are on bar , delivering an average load of 25.16 MW. Unit #03 is on standby due to TRCM and cooling water strainer issues.. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-17 | 2026 | 5 | 17 | Machai HPS | 2.6 | 1.79 | 1.6 | 37952 | 37092 | 28 | 22 | 60.82 | 4.671 | 76.92 | 70 | 48000 | 222833.82 | 173257 | 49577.09 | 860 | Unit stopped normally due to choking at 0956 and unit started and synced with system at 1050 after flushing. | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-05-17 | 2026 | 5 | 17 | Malakand-3 HPS | 81 | 60 | 55.32 | 1327748 | 1317140 | 51 | 36.44 | 68.3 | 2.8627 | 94.34 | 77.5 | 1834000 | 5248898.97 | 3770577 | 1478322.29 | 10608 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-17 | 2026 | 5 | 17 | Pehur HPS | 18 | 6.9 | 6.1 | 145300 | 142000 | 15.33 | 16 | 33.63 | 3.767 | 31.02 | 41 | 134000 | 505507.1 | 534914 | -29406.9 | 3300 | At 1644 hrs, Units #01 & #03 tripped due to failure of the 132 KV line supply due to tripping of the Wah-7 & Wah-8 lines. 132 KV supply restored at 1700 hrs, after which Units #01 & #03 were taken on bar with a total load of 6.4 MW. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-17 | 2026 | 5 | 17 | Reshun HPS | 4.2 | 2.19 | 1.58 | 37000 | 36640 | 2.26 | 2.27 | 36.71 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 493907 | 313210.7 | 360 | Nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-05-18 | 2026 | 5 | 18 | Daral Khwar HPS | 36.6 | 36.6 | 36.6 | 877960 | 875160 | 27.14 | 14.64 | 99.95 | 8.2683 | 85.95 | 48 | 755000 | 6241232.9 | 7236085 | -994852.52 | 2800 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.6 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-18 | 2026 | 5 | 18 | Jabori HPS | 10.2 | 10.4 | 10.28 | 246810 | 245280 | 8.54 | 8.07 | 100.82 | 5.7092 | 98.86 | 79.57 | 242000 | 1383099.74 | 1400353 | -17252.83 | 1530 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 10.28 MW to the national grid according to the available hydrology. 2: Cooling Water Pump #02 has remained non-functional since 12-10-2025. The contractor has already been formally intimated regarding the issue. The non-availability of a standby pump poses a significant risk of forced unit shutdown and consequent generation loss in the event of pump failure or low flow/pressure conditions. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-05-18 | 2026 | 5 | 18 | Karora HPS | 11.8 | 11.8 | 5.34 | 128138 | 127376 | 12.85 | 4.22 | 45.25 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 990985 | 1187414.72 | 762 | 1) Unit No. 01 and 02 on bar, collectively delivering an average load of 5.34 MW according to the available hydrology. 2) At 12:30 Hrs, the under-sluice gates were closed; however, significant leakage through the gates still persists. Furthermore, the operation of the under-sluice gates is unsatisfactory in both manual and motorized modes, requiring proper rectification to prevent further energy loss and to ensure immediate opening and closing during emergency or flood conditions. 3) At 12:50 hrs, Unit #01 was synchronized with the system, and its load was gradually increased to 5.9 MW. Subsequently, at 12:56 hrs, Unit #02 was synchronized with the system, and its load was also gradually increased to 5.9 MW. However, at 13:25 hrs, Unit #01 electrically tripped and reached to FSNL. After resetting the alarms, Unit #01 was re-synchronized with the system at 13:39 hrs. 4) Both cooling water pumps are running to maintain the required flow. However, proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and Energy loss in case of pump failure or flow/pressure. 5) No rectification work on punch list items related to power house has been carried out since 17-April-2026. Except for the installation of motors at the intake side by the sub-contractor, without any effective supervision. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-05-18 | 2026 | 5 | 18 | Koto HPS | 40.8 | 27.17 | 26.05 | 625250 | 618266 | 174.1 | 74.24 | 63.85 | 8.24 | 95.89 | 58 | 939000 | 7737625.81 | 5094512 | 2643113.97 | 6984 | Unit #01 and Unit #02 are on bar , delivering an average load of 26.05 MW. Unit #03 is on standby due to TRCM and cooling water strainer issues.. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-18 | 2026 | 5 | 18 | Machai HPS | 2.6 | 1.92 | 1.48 | 38204 | 37224 | 31.6 | 24 | 61.22 | 4.671 | 76.45 | 70 | 47705.81 | 222833.82 | 173873.3 | 48960.52 | 980 | Unit stopped normally due to choking at 0450hrs and synced at 0508hrs. Unit tripped at 1301hrs due to 11 KV line tripping and synced at 1309 hrs Unit tripped at 1301hrs due to heavy storm. | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-05-18 | 2026 | 5 | 18 | Malakand-3 HPS | 81 | 60 | 54.65 | 1311594 | 1301210 | 51 | 37.46 | 67.47 | 2.8627 | 94.34 | 77.5 | 1834000 | 5248898.97 | 3724973.87 | 1523925.1 | 10384 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-18 | 2026 | 5 | 18 | Pehur HPS | 18 | 7.72 | 5.88 | 141300 | 139000 | 15.33 | 18 | 32.71 | 3.767 | 31.02 | 41 | 134000 | 505507.1 | 523613 | -18105.9 | 2300 | The plant remained shutdown from 1625 hrs to 1825 hrs in search of dead body in the canal. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-18 | 2026 | 5 | 18 | Reshun HPS | 4.2 | 2.04 | 1.32 | 30000 | 29649 | 1.89 | 1.83 | 29.76 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 399669 | 407448.7 | 351 | Outgoing feeder breaker remain off for 01 hour due to line fault and work in iine. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-05-19 | 2026 | 5 | 19 | Daral Khwar HPS | 36.6 | 36.6 | 25.4 | 608500 | 606500 | 27.14 | 10.14 | 69.27 | 8.2683 | 85.93 | 48 | 754838.71 | 6241232.9 | 5014723.95 | 1226508.95 | 2000 | 1. Units No. 01,02 and 03 were on bar delivering an average load equal to 25.4 MW according to the available hydrology. 2: The plant was shut down at 0901Hrs against PESCO permit Swat-3 dated 19-05-2026 for emergency maintenance on the 132KV GSS matta line and hotspot removal on the yellow phase isolator.during the shutdown, flushing, monthly maintenance, and cleaning of intake and sand trap trask rack were carried out. The 132KV line was restored at 1040Hrs, however the plant remained shut down until 1557Hrs for comprehensive flushing. 3: Units No. 01,02 and 03 were synchronized with the national grid at 1557hrs, 1558hrs and 1605hrs, respectively. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-19 | 2026 | 5 | 19 | Jabori HPS | 10.2 | 10.2 | 9.51 | 118870 | 117960 | 8.54 | 3.88 | 48.56 | 5.7092 | 98.96 | 79.57 | 242258.06 | 1383099.74 | 673457.23 | 709642.51 | 910 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 9.51 MW to the national grid according to the available hydrology. 2: The 132 kV transmission line tripped at 0040 hrs and was restored at 1018 hrs. Subsequently, Units 01 and 02 were synchronized at 1110 hrs, and the load was gradually increased to 10.2 MW. 3: At 1350 hrs, the cooling water pressure dropped to 0.8 bar, resulting in the tripping of Unit 01 and 02. Both units were subsequently resynchronized at 1426 hrs. 4: At 1652 hrs, Unit 01 tripped again due to malfunctioning of stator winding RTD no. 5 and 13, showing false temperature indications of 117°C. Unit 01 was then synchronized at 1819 hrs. 5: Cooling Water Pump #02 has remained non-functional since 12-10-2025. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-05-19 | 2026 | 5 | 19 | Karora HPS | 11.8 | 11.8 | 9.76 | 234330 | 231765 | 12.85 | 7.5 | 82.74 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1803131.7 | 375268.3 | 2565 | 1) Unit No. 01 and 02 on bar, collectively delivering an average load of 9.76 MW according to the available hydrology. 2) At 00:32 hrs, The circuit breaker (E2Q1) of the 132 kV transmission line at the Khan Khwar HPP side tripped due to adverse weather conditions. The RCC was informed accordingly and they instructed to wait until weather conditions improved. Upon restoration of normal weather conditions, RCC granted permission at 01:10 hrs to close the breaker, and the line was successfully energized at 01:12 hrs. Subsequently, Unit #01 and Unit #02 were synchronized with the system at 01:47 hrs and 02:00 hrs, respectively. NOTE : The delay in units startup and synchronization occurred due to the manual operation of the intake gate. 3) The plant was shut down at 11:47 hrs due to blockage of the intake trash rack, causing a gradually reduction in available hydrology . After completion of trash rack cleaning, the Unit #02 and Unit #01 were synchronized with the system at 13:08 hrs and 13:15 hrs, respectively. 4) Both cooling water pumps are running to maintain the required flow. However, proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and Energy loss in case of pump failure or flow/pressure. 5) No rectification work on punch list items related to power house has been carried out since 17-April-2026. Except for the installation of motors at the intake side by the sub-contractor, without any effective supervision. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-05-19 | 2026 | 5 | 19 | Koto HPS | 40.8 | 27.02 | 26.32 | 630500 | 628131 | 174.1 | 81.13 | 64.39 | 8.24 | 95.9 | 58 | 939032.26 | 7737625.81 | 5175799.44 | 2561826.37 | 2369 | Main hurdles for limiting power generation at Koto, is still : Non-Functional cooling water strainer and Non-Available TRCM. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-19 | 2026 | 5 | 19 | Machai HPS | 2.6 | 1.52 | 1.13 | 27140 | 26422 | 31.6 | 25 | 43.49 | 4.671 | 76.45 | 70 | 47705.81 | 222833.82 | 123417.16 | 99416.66 | 718 | No data submitted for this date | engr.atifwazir@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-05-19 | 2026 | 5 | 19 | Malakand-3 HPS | 81 | 61 | 54.43 | 1306214 | 1295210 | 51 | 36.71 | 67.19 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3707797.67 | 1541101.3 | 11004 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-19 | 2026 | 5 | 19 | Pehur HPS | 18 | 7.45 | 6.44 | 154600 | 150000 | 15.33 | 18 | 35.79 | 3.767 | 31.06 | 41 | 134193.55 | 505507.1 | 565050 | -59542.9 | 4600 | At 1040 hrs, Unit#01 & 03 tripped due to failure of 132 KV line supply (gaz-5 tripped). 132 KV supply restored, Unit#01 & 03 taken on bar at 11:00 & 11:20 hrs respectively with a total load of 5.8 MW. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-19 | 2026 | 5 | 19 | Reshun HPS | 4.2 | 1.98 | 1.23 | 27000 | 26450 | 1.71 | 1.65 | 26.79 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 356546 | 450571.7 | 550 | outgoing feeder breaker remained off 3.46 hours due to line faults | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-05-20 | 2026 | 5 | 20 | Daral Khwar HPS | 36.6 | 36.6 | 36.8 | 883420 | 880220 | 27.14 | 14.72 | 100.57 | 8.2683 | 85.93 | 48 | 754838.71 | 6241232.9 | 7277923.03 | -1036690.12 | 3200 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.8 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-20 | 2026 | 5 | 20 | Jabori HPS | 10.2 | 10.3 | 10.09 | 242275 | 240720 | 8.54 | 7.92 | 98.97 | 5.7092 | 98.96 | 79.57 | 242258.06 | 1383099.74 | 1374318.62 | 8781.12 | 1555 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 10.09 MW to the national grid according to the available hydrology. 2: Cooling Water Pump #02 has remained non-functional since 12-10-2025. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-05-20 | 2026 | 5 | 20 | Karora HPS | 11.8 | 11.8 | 11.04 | 265036 | 262092 | 12.85 | 8.73 | 93.59 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 2039075.76 | 139324.24 | 2944 | Units No. 01 and 02 on bar, collectively delivering an average load of 11.04 MW according to the available hydrology. Both cooling water pumps are running to maintain the required flow. However, proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and Energy loss in case of pump failure or flow/pressure issue. No rectification work on punch list items related to power house has been carried out since 17-April-2026. Except for the installation of motors at the intake site by the sub-contractor, without any effective supervision. | nasimkhan20661@gmail.com | Original |  | Generation_Data.xlsx
2026-05-20 | 2026 | 5 | 20 | Koto HPS | 40.8 | 26.9 | 15.71 | 377000 | 374907 | 174.1 | 48.51 | 38.5 | 8.24 | 95.9 | 58 | 939032.26 | 7737625.81 | 3089233.68 | 4648392.13 | 2093 | Generation of Koto HPC for the day was limited due to Trash Racks cleaning. Main bottlenecks at Koto HPC are non-functional Strainers for cooling water line and non-availability of Trash Rack Cleaning machine. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-20 | 2026 | 5 | 20 | Machai HPS | 2.6 | 2.07 | 0.67 | 16076 | 15620 | 31.6 | 26 | 25.76 | 4.671 | 76.45 | 70 | 47705.81 | 222833.82 | 72961.02 | 149872.8 | 456 | 11KV Line restored at 1242hrs which was tripped at 2250hrs on 18/05/2026. Unit synched at 1406 hrs. unit ripped twice due to 11KV line tripping at 1759 and 2126 hrs while synched back at 1905 and 2153 hrs respectively | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-05-20 | 2026 | 5 | 20 | Malakand-3 HPS | 81 | 60 | 56.85 | 1364308 | 1352930 | 51 | 38.69 | 70.18 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3873032.71 | 1375866.26 | 11378 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-20 | 2026 | 5 | 20 | Pehur HPS | 18 | 7.54 | 5.58 | 133900 | 133000 | 16.35 | 16 | 31 | 3.767 | 31.06 | 41 | 134193.55 | 505507.1 | 501011 | 4496.1 | 900 | The plant remained shutdown from 01:30 hrs to 04:20 hrs because there was no 132 kv supply available due to maintenance work at Gadoon Grid as Gadon Grid SSO Mr. Zahoor requested for an NOC to de-energize 132 kv Gadoon Grid - PHPC line. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-20 | 2026 | 5 | 20 | Reshun HPS | 4.2 | 1.93 | 1.49 | 36000 | 35440 | 2.26 | 2.2 | 35.71 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 477731.2 | 329386.5 | 560 | Nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-05-21 | 2026 | 5 | 21 | Daral Khwar HPS | 36.6 | 36.6 | 36.6 | 877440 | 874640 | 27.14 | 14.63 | 99.89 | 8.2683 | 85.93 | 48 | 754838.71 | 6241232.9 | 7231785.91 | -990553.01 | 2800 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.6 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-21 | 2026 | 5 | 21 | Jabori HPS | 10.2 | 10.4 | 10.44 | 250602 | 249050 | 8.54 | 8.19 | 102.37 | 5.7092 | 98.96 | 79.57 | 242258.06 | 1383099.74 | 1421876.26 | -38776.52 | 1552 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 10.44 MW to the national grid according to the available hydrology. 2: Cooling Water Pump #02 has remained non-functional since 12-10-2025. | faizanbabar5@gmail.com | Original | CHECK: units > installed capacity x 24h (source me verify karein) | Generation_Data.xlsx
2026-05-21 | 2026 | 5 | 21 | Karora HPS | 11.8 | 11.8 | 10.33 | 247918 | 245194 | 12.85 | 8.35 | 87.54 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1907609.32 | 270790.68 | 2724 | 1) Unit No. 01 and 02 on bar, collectively delivering an average load of 10.33 MW according to the available hydrology. 2) The plant was shut down at 08:09 hrs due to blockage of the intake trash rack, causing a gradually reduction in available hydrology . After completion of trash rack cleaning, the Unit #02 and Unit #01 were synchronized with the system at 9:00 hrs and 9:07 hrs, respectively. 3) Both cooling water pumps are running to maintain the required flow. However, proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and Energy loss in case of pump failure or flow/pressure. 4) No rectification work on punch list items related to power house has been carried out since 17-April-2026. Except for the installation of motors at the intake side by the sub-contractor, without any effective supervision. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-05-21 | 2026 | 5 | 21 | Koto HPS | 40.8 | 27.15 | 24.93 | 598250 | 596362 | 174.1 | 76.98 | 61.1 | 8.24 | 95.9 | 58 | 939032.26 | 7737625.81 | 4914022.88 | 2823602.93 | 1888 | Main bottlenecks at Koto HPC are non-functional Strainers for cooling water and non-availability of Trash Rack Cleaning machine. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-21 | 2026 | 5 | 21 | Machai HPS | 2.6 | 1.87 | 1.69 | 40924 | 39992 | 31.6 | 27 | 65.58 | 4.671 | 76.45 | 70 | 47705.81 | 222833.82 | 186802.63 | 36031.19 | 932 | Normal Operation as per available inflow | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-05-21 | 2026 | 5 | 21 | Malakand-3 HPS | 81 | 59 | 55.1 | 1322292 | 1311010 | 51 | 37.2 | 68.02 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3753028.33 | 1495870.64 | 11282 | As per available hydrology from Irrigation Department all three units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-21 | 2026 | 5 | 21 | Pehur HPS | 18 | 7.81 | 6.92 | 166300 | 162000 | 15.33 | 18 | 38.5 | 3.767 | 31.06 | 41 | 134193.55 | 505507.1 | 610254 | -104746.9 | 4300 | Plant operational 24 hrs | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-21 | 2026 | 5 | 21 | Reshun HPS | 4.2 | 2.15 | 1.55 | 36000 | 35490 | 2.26 | 2.2 | 35.71 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 478405.2 | 328712.5 | 510 | Outgoing feeder breaker tripped 3times due to line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-05-22 | 2026 | 5 | 22 | Daral Khwar HPS | 36.6 | 36.6 | 36.4 | 874620 | 871820 | 27.14 | 14.58 | 99.57 | 8.2683 | 85.93 | 48 | 754838.71 | 6241232.9 | 7208469.31 | -967236.4 | 2800 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.4 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-22 | 2026 | 5 | 22 | Jabori HPS | 10.2 | 10.6 | 10.25 | 245982 | 244400 | 8.54 | 8.04 | 100.48 | 5.7092 | 98.96 | 79.57 | 242258.06 | 1383099.74 | 1395328.48 | -12228.74 | 1582 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 10.25 MW to the national grid according to the available hydrology. 2: Cooling Water Pump #02 has remained non-functional since 12-10-2025. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-05-22 | 2026 | 5 | 22 | Karora HPS | 11.8 | 11.8 | 11.6 | 279918 | 277086 | 12.85 | 9.2 | 98.84 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 2155729.08 | 22670.92 | 2832 | Unit No. 01 and 02 on bar, collectively delivering an average load of 11.66 MW according to the available hydrology. Both cooling water pumps are running to maintain the required flow. However, proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and Energy loss in case of pump failure or flow/pressure. No rectification work on punch list items related to power house has been carried out since 17-April-2026. Except for the installation of motors at the intake side by the sub-contractor, without any effective supervision. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-05-22 | 2026 | 5 | 22 | Koto HPS | 40.8 | 27.17 | 24.79 | 595000 | 587911 | 174.1 | 76.56 | 60.76 | 8.24 | 95.9 | 58 | 939032.26 | 7737625.81 | 4844386.64 | 2893239.17 | 7089 | Units 1 and 3 were operated during the day while Unit 2 remained shut down on standby due to cooling water strainers issue, as the cooling water strainers cannot supply water to all units simultaneously due to an automatic operation malfunction. Today's reduced generation was caused by choking at the intake, as well as a shutdown forced by the closure of the intake gates. This closure was required to facilitate the Rescue 1122 Department's search for a dead body in the Panjkora River. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-22 | 2026 | 5 | 22 | Machai HPS | 2.6 | 2 | 1.58 | 40520 | 39516 | 31.6 | 27 | 64.94 | 4.671 | 76.45 | 70 | 47705.81 | 222833.82 | 184579.24 | 38254.59 | 1004 | Unit ripped twice due to 11KV line tripping at 1153 and 2254 hrs while synched back at 1212 and 2307 hrs respectively | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-05-22 | 2026 | 5 | 22 | Malakand-3 HPS | 81 | 64 | 49.56 | 1189423 | 1179590 | 51 | 38.7 | 61.18 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3376812.29 | 1872086.68 | 9833 | Units desynchronized from the system at 05:57 on emergency basis to avoid flooding in the drainage pit. As all drainage pumps are not working and need proper maintenance. Unit# 01,02 & 03 synchronized with the system at 09:19,08:49 & 09:00 after normalization of the drainage system. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-22 | 2026 | 5 | 22 | Pehur HPS | 18 | 8.5 | 7.1 | 170400 | 165000 | 15.33 | 20 | 39.44 | 3.767 | 31.06 | 41 | 134193.55 | 505507.1 | 621555 | -116047.9 | 5400 | Plant remained operational throughout 24 hrs as per available hydrology+Irrigation valve open. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-22 | 2026 | 5 | 22 | Reshun HPS | 4.2 | 2.83 | 1.72 | 39000 | 0 | 2.43 | 2.38 | 38.69 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 0 | 807117.7 | 39000 | Outgoing feeder breaker reamined Off 2.55 hours due to line faults and Intake channel washing. | zafar.src@gmail.com | Original | Net = Units - Aux; Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-05-23 | 2026 | 5 | 23 | Daral Khwar HPS | 36.6 | 36.6 | 36.5 | 876740 | 873940 | 27.14 | 14.62 | 99.81 | 8.2683 | 85.93 | 48 | 754838.71 | 6241232.9 | 7225998.1 | -984765.2 | 2800 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.5 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-23 | 2026 | 5 | 23 | Jabori HPS | 10.2 | 10.4 | 10.34 | 248133 | 246580 | 7.72 | 7.87 | 101.36 | 5.7092 | 98.96 | 79.57 | 242258.06 | 1383099.74 | 1407774.54 | -24674.79 | 1553 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 10.34 MW to the national grid according to the available hydrology. 2: Cooling Water Pump #02 has remained non-functional since 12-10-2025. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-05-23 | 2026 | 5 | 23 | Karora HPS | 11.8 | 11.82 | 11.59 | 278120 | 275271 | 12.15 | 9.22 | 98.21 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 2141608.38 | 36791.62 | 2849 | Unit No. 01 and 02 on bar, collectively delivering an average load of 11.59 MW according to the available hydrology. Both cooling water pumps are running to maintain the required flow. However, proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and Energy loss in case of pump failure or flow/pressure. No rectification work on punch list items related to power house has been carried out since 17-April-2026. Except for the installation of motors at the intake side by the sub-contractor, without any effective supervision. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-05-23 | 2026 | 5 | 23 | Koto HPS | 40.8 | 27.02 | 24.19 | 580500 | 577615 | 174.1 | 74.7 | 59.28 | 8.24 | 95.9 | 58 | 939032.26 | 7737625.81 | 4759547.6 | 2978078.21 | 2885 | The Unit#02 and 03 are operational on average load 24.19MW. while the unit#01 on standby due to cooling water issue. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-23 | 2026 | 5 | 23 | Machai HPS | 2.6 | 1.95 | 1.12 | 29032 | 28380 | 30 | 27 | 46.53 | 4.671 | 76.45 | 70 | 47705.81 | 222833.82 | 132562.98 | 90270.84 | 652 | 1) Unit normally stopped due to issued PTW at 0800hr to 1300hrs from katlang grid, 11kv line restored at 1303hrs, while Unit synch with the system at 1319hrs. 2) Unit tripped at 2228hrs due to 11kv line tripped, because of stormy weather, and issued unknow fault in the line. | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-05-23 | 2026 | 5 | 23 | Malakand-3 HPS | 81 | 62 | 57.79 | 1386881 | 1376350 | 51 | 38.77 | 71.34 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3940077.14 | 1308821.82 | 10531 | As per available hydrology from the Irrigation Department all the three Units are on bar. Load variation is due to fluctuations in the hydrology of River Swat. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-23 | 2026 | 5 | 23 | Pehur HPS | 18 | 7.78 | 7.09 | 170200 | 166000 | 15.33 | 20 | 39.4 | 3.767 | 31.06 | 41 | 134193.55 | 505507.1 | 625322 | -119814.9 | 4200 | Plant remained operational throughout 24 hrs as per available hydrology+Irrigation valve open. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-23 | 2026 | 5 | 23 | Reshun HPS | 4.2 | 2.32 | 1.22 | 28000 | 27685 | 1.65 | 1.65 | 27.78 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 373193.8 | 433923.9 | 315 | Outgoing feeder breaker remained off 1.50 hours due to Line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-05-24 | 2026 | 5 | 24 | Daral Khwar HPS | 36.6 | 36.6 | 36.6 | 877740 | 875340 | 27.14 | 14.64 | 99.92 | 8.2683 | 85.93 | 48 | 754838.71 | 6241232.9 | 7237573.72 | -996340.82 | 2400 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.6 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-24 | 2026 | 5 | 24 | Jabori HPS | 10.2 | 10.4 | 10.26 | 246315 | 244690 | 7.72 | 7.87 | 100.62 | 5.7092 | 98.96 | 79.57 | 242258.06 | 1383099.74 | 1396984.15 | -13884.41 | 1625 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 10.26 MW to the national grid according to the available hydrology. 2: Cooling Water Pump #02 has remained non-functional since 12-10-2025. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-05-24 | 2026 | 5 | 24 | Karora HPS | 11.8 | 11.81 | 11.58 | 277890 | 275018 | 12.15 | 9.19 | 98.12 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 2139640.04 | 38759.96 | 2872 | Unit No. 01 and 02 on bar, collectively delivering an average load of 11.58 MW according to the available hydrology. Both cooling water pumps are running to maintain the required flow. However, proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and Energy loss in case of pump failure or flow/pressure. No rectification work on punch list items related to power house has been carried out since 17-April-2026. Except for the installation of motors at the intake side by the sub-contractor, without any effective supervision. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-05-24 | 2026 | 5 | 24 | Koto HPS | 40.8 | 27.38 | 26.26 | 630250 | 625677 | 174.1 | 81.1 | 64.36 | 8.24 | 95.9 | 58 | 939032.26 | 7737625.81 | 5155578.48 | 2582047.33 | 4573 | Non functional Strainers and Non availability of TRCM are the main bottlenecks | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-24 | 2026 | 5 | 24 | Machai HPS | 2.6 | 1.89 | 1.05 | 26208 | 25520 | 29.5 | 27 | 42 | 4.671 | 76.45 | 70 | 47705.81 | 222833.82 | 119203.92 | 103629.9 | 688 | 11 KV line which tripped yesterday at 2228 hrs., restored at 0955 hrs. today, while unit resynched at 1015 hrs.. It is reported to you, that PESCO grid staff is not cooperative, as well as trips the 11 KV line without informing Machai operators. | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-05-24 | 2026 | 5 | 24 | Malakand-3 HPS | 81 | 60 | 56.78 | 1362746 | 1352500 | 51 | 38.35 | 70.1 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3871801.75 | 1377097.22 | 10246 | As per available hydrology from the Irrigation Department all the three Units are on bar. Load variation is due to fluctuations in the hydrology of River Swat. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-24 | 2026 | 5 | 24 | Pehur HPS | 18 | 7.82 | 7.16 | 171800 | 168000 | 15.33 | 20 | 39.77 | 3.767 | 31.06 | 41 | 134193.55 | 505507.1 | 632856 | -127348.9 | 3800 | Plant remained operational throughout 24 hrs as per available hydrology + Irrigation valve open. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-24 | 2026 | 5 | 24 | Reshun HPS | 4.2 | 1.9 | 1.48 | 26000 | 25688 | 1.65 | 1.59 | 25.79 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 346274.24 | 460843.46 | 312 | Outgoing Feeder Breaker remained Off 1.00 hour due to tripping. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-05-25 | 2026 | 5 | 25 | Daral Khwar HPS | 36.6 | 36.6 | 36.6 | 878960 | 876160 | 27.14 | 14.65 | 100.06 | 8.2683 | 85.93 | 48 | 754838.71 | 6241232.9 | 7244353.73 | -1003120.82 | 2800 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.6 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-25 | 2026 | 5 | 25 | Jabori HPS | 10.2 | 10.3 | 10.27 | 248547 | 247020 | 7.72 | 7.87 | 101.53 | 5.7092 | 98.96 | 79.57 | 242258.06 | 1383099.74 | 1410286.58 | -27186.84 | 1527 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 10.27 MW to the national grid according to the available hydrology. 2: Cooling Water Pump #02 has remained non-functional since 12-10-2025. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-05-25 | 2026 | 5 | 25 | Karora HPS | 11.8 | 11.83 | 10.28 | 246689 | 244290 | 12.15 | 8.37 | 87.11 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1900576.2 | 277823.8 | 2399 | Unit No. 01 and 02 on bar, collectively delivering an average load of 10.28 MW according to the available hydrology. At 06:33 hrs, the plant was shut down for intake trash rack cleaning. After completion of the cleaning activity, Unit #01 and Unit #02 were subsequently synchronized with the system at 08:19 hrs and 08:24 hrs, respectively. Both cooling water pumps are running to maintain the required flow. However, proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and Energy loss in case of pump failure or flow/pressure. No rectification work on punch list items related to power house has been carried out since 17-April-2026. Except for the installation of motors at the intake side by the sub-contractor, without any effective supervision. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-05-25 | 2026 | 5 | 25 | Koto HPS | 40.8 | 27 | 22.53 | 540750 | 536453 | 174.1 | 69.58 | 55.22 | 8.24 | 95.9 | 58 | 939032.26 | 7737625.81 | 4420372.72 | 3317253.09 | 4297 | Unit#2 and 03 are on bar delivering average 22.53MW and Unit #01 on standby due to cooling water strainer and TRCM issue. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-25 | 2026 | 5 | 25 | Machai HPS | 2.6 | 2.06 | 1.62 | 38404 | 37576 | 28 | 26 | 61.54 | 4.671 | 76.45 | 70 | 47705.81 | 222833.82 | 175517.5 | 47316.33 | 828 | Unit tripped twice due to Machai 11 KV line tripping from PESCO without informing. (No operation for 01 hour & 53 mins). | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-05-25 | 2026 | 5 | 25 | Malakand-3 HPS | 81 | 59 | 57.3 | 1375221 | 1364720 | 51 | 38.69 | 70.74 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3906783.94 | 1342115.02 | 10501 | As per available hydrology from the Irrigation Department all the three Units are on bar. Load variation is due to fluctuations in the hydrology of River Swat. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-25 | 2026 | 5 | 25 | Pehur HPS | 18 | 7.23 | 6.9 | 165700 | 161000 | 15.33 | 18 | 38.36 | 3.767 | 31.06 | 41 | 134193.55 | 505507.1 | 606487 | -100979.9 | 4700 | Unit # 3 remained off the bar from 1157 Hrs to 1241 Hrs due to excitation trouble. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-25 | 2026 | 5 | 25 | Reshun HPS | 4.2 | 2.18 | 1.59 | 38000 | 37682 | 2.37 | 2.32 | 37.7 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 507953.36 | 299164.34 | 318 | Outgoing breaker remained off 1.00 due to line works. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-05-26 | 2026 | 5 | 26 | Daral Khwar HPS | 36.6 | 36.6 | 36.6 | 878900 | 876100 | 27.14 | 14.65 | 100.06 | 8.2683 | 85.93 | 48 | 754838.71 | 6241232.9 | 7243857.63 | -1002624.73 | 2800 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.6 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-26 | 2026 | 5 | 26 | Jabori HPS | 10.2 | 10.4 | 9.6 | 230443 | 228920 | 7.72 | 7.48 | 94.14 | 5.7092 | 98.96 | 79.57 | 242258.06 | 1383099.74 | 1306950.06 | 76149.68 | 1523 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 10.6 MW to the national grid according to the available hydrology. 2: Cooling Water Pump #02 has remained non-functional since 12-10-2025. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-05-26 | 2026 | 5 | 26 | Karora HPS | 11.8 | 11.82 | 10.61 | 254565 | 252034 | 12.15 | 8.85 | 89.89 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1960824.52 | 217575.48 | 2531 | Unit No. 01 and 02 on bar, collectively delivering an average load of 10.61 MW according to the available hydrology. At 13:11 hrs, Unit #01 operating at full load tripped due to hydraulic mechanical shutdown. After resetting all parameters, the unit was synchronized with the system at 14:04 hrs and its load was gradually increased to 5.9 MW. However, the unit again tripped at 15:02 hrs on the same fault indication and was re-synchronized at 15:46 hrs. Subsequently, Unit #01 experienced multiple trips. During observation, it was found that the unit remained stable at 80% of rated load. Therefore, the load was maintained at 80% of rated capacity for approximately four hours to monitor its performance. After stable operation, the unit load was increased to full load at 22:54 hrs. Both cooling water pumps are running to maintain the required flow. However, proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and Energy loss in case of pump failure or flow/pressure. No rectification work on punch list items related to power house has been carried out since 17-April-2026. Except for the installation of motors at the intake side by the sub-contractor, without any effective supervision. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-05-26 | 2026 | 5 | 26 | Koto HPS | 40.8 | 27.2 | 25.46 | 612500 | 609264 | 174.1 | 72.8 | 62.55 | 8.24 | 95.9 | 58 | 939032.26 | 7737625.81 | 5020335.36 | 2717290.45 | 3236 | Unit #02 and Unit #03 are on bar , delivering an average load of 25.46 MW. Unit #01 is on standby due to TRCM and cooling water strainer issues.. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-26 | 2026 | 5 | 26 | Machai HPS | 2.6 | 1.98 | 1.63 | 39564 | 38632 | 29 | 26 | 63.4 | 4.671 | 76.45 | 70 | 47705.81 | 222833.82 | 180450.07 | 42383.75 | 932 | Unit tripped due to reverse power at 2202 hrs., while resynched at 2330 hrs., lately due to fault in excitation system. (No operation for 01 hour & 28 mins.) | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-05-26 | 2026 | 5 | 26 | Malakand-3 HPS | 81 | 60 | 56.76 | 1362339 | 1352280 | 51 | 38.42 | 70.08 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3871171.96 | 1377727.01 | 10059 | As per available hydrology from the Irrigation Department all the three Units are on bar. Load variation is due to fluctuations in the hydrology of River Swat. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-26 | 2026 | 5 | 26 | Pehur HPS | 18 | 7.79 | 7.44 | 178600 | 174000 | 15.33 | 19 | 41.34 | 3.767 | 31.06 | 41 | 134193.55 | 505507.1 | 655458 | -149950.9 | 4600 | Plant oprational 24 hrs. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-26 | 2026 | 5 | 26 | Reshun HPS | 4.2 | 2.66 | 1.56 | 38000 | 37679 | 2.37 | 2.32 | 37.7 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 507912.92 | 299204.78 | 321 | outgoing feeder breaker remained Off 1.30hours due to less hydrology. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-05-27 | 2026 | 5 | 27 | Daral Khwar HPS | 36.6 | 36.6 | 36.6 | 879300 | 876900 | 27.14 | 14.66 | 100.1 | 8.2683 | 85.93 | 48 | 754838.71 | 6241232.9 | 7250472.27 | -1009239.37 | 2400 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.6 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-27 | 2026 | 5 | 27 | Jabori HPS | 10.2 | 10.3 | 9.52 | 228584 | 227060 | 7.72 | 7.38 | 93.38 | 5.7092 | 98.96 | 79.57 | 242258.06 | 1383099.74 | 1296330.95 | 86768.79 | 1524 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 9.52 MW to the national grid according to the available hydrology. 2: Cooling Water Pump #02 has remained non-functional since 12-10-2025. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-05-27 | 2026 | 5 | 27 | Karora HPS | 11.8 | 11.86 | 11.62 | 278998 | 276187 | 12.85 | 9.29 | 98.52 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 2148734.86 | 29665.14 | 2811 | Unit No. 01 and 02 on bar, collectively delivering an average load of 11.62 MW according to the available hydrology. Both cooling water pumps are running to maintain the required flow. However, proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and Energy loss in case of pump failure or flow/pressure. No rectification work on punch list items related to power house has been carried out since 17-April-2026. Except for the installation of motors at the intake side by the sub-contractor, without any effective supervision. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-05-27 | 2026 | 5 | 27 | Koto HPS | 40.8 | 25.42 | 26.39 | 633250 | 627942 | 174.1 | 81.48 | 64.67 | 8.24 | 95.9 | 58 | 939032.26 | 7737625.81 | 5174242.08 | 2563383.73 | 5308 | Unit #02 and Unit #03are on bar , delivering an average load of 26.39 MW. Unit #01 is on standby due to TRCM and cooling water strainer issues.. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-27 | 2026 | 5 | 27 | Machai HPS | 2.6 | 1.99 | 1.14 | 27420 | 26840 | 26 | 25 | 43.94 | 4.671 | 76.45 | 70 | 47705.81 | 222833.82 | 125369.64 | 97464.18 | 580 | Unit tripped due to reverse power at 1043 hrs., while resynched at 1942 hrs., lately, due to fault in excitation system; as no maintenance staff available at Machai. So, all the maintenance activities are also carried out, mere by operators (contract staff). | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-05-27 | 2026 | 5 | 27 | Malakand-3 HPS | 81 | 60 | 55.47 | 1331217 | 1321100 | 51 | 37.74 | 68.48 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3781912.97 | 1466986 | 10117 | As per available hydrology from the Irrigation Department all the three Units are on bar. Load variation is due to fluctuations in the hydrology of River Swat. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-27 | 2026 | 5 | 27 | Pehur HPS | 18 | 7.9 | 7.6 | 183100 | 178000 | 16.35 | 18 | 42.38 | 3.767 | 31.06 | 41 | 134193.55 | 505507.1 | 670526 | -165018.9 | 5100 | Not reported | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-27 | 2026 | 5 | 27 | Reshun HPS | 4.2 | 2.15 | 1 | 23000 | 22688 | 1.59 | 1.49 | 22.82 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 305834.24 | 501283.46 | 312 | Outgoing feeder breaker remained Off due to line hours for 2.15hours. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-05-28 | 2026 | 5 | 28 | Daral Khwar HPS | 36.6 | 36.6 | 36.7 | 880730 | 877930 | 27.14 | 14.68 | 100.27 | 8.2683 | 85.93 | 48 | 754838.71 | 6241232.9 | 7258988.62 | -1017755.72 | 2800 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.7 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-28 | 2026 | 5 | 28 | Jabori HPS | 10.2 | 10.2 | 9.57 | 229857 | 228340 | 7.72 | 7.43 | 93.9 | 5.7092 | 98.96 | 79.57 | 242258.06 | 1383099.74 | 1303638.73 | 79461.01 | 1517 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 9.57 MW to the national grid according to the available hydrology. 2: Cooling Water Pump #02 has remained non-functional since 12-10-2025. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-05-28 | 2026 | 5 | 28 | Karora HPS | 11.8 | 11.9 | 10.95 | 262710 | 259870 | 12.85 | 8.6 | 92.76 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 2021788.6 | 156611.4 | 2840 | 1. Unit No. 01 and 02 on bar, collectively delivering an average load of 10.95MW according to the available hydrology. 2. Both cooling water pumps are running to maintain the required flow. However, proper testing is still pending. Additionally, the absence of a standby pump poses a risk of forced unit shutdown and Energy loss in case of pump failure or flow/pressure. 3. No rectification work on punch list items related to power house has been carried out since 17-April-2026. Except for the installation of motors at the intake side by the sub-contractor, without any effective supervision. 4. The combine flow and pressure of both cooling water pumps are inadequate; resulting in rising temperatures of GCC of both the units and subsequently in plant's load reduction. 5. TRB and TTB temperatures raised abnormally due to lube oil flow deficiency. Immediately, standby lube oil pump was started to restore rated flow & stabilize bearing temperatures. Also, Unit No. 2 & 1 tripped at 15:56 hrs and 16:23 hrs respectively. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-05-28 | 2026 | 5 | 28 | Koto HPS | 40.8 | 26.67 | 26.39 | 595500 | 580375 | 174.1 | 70.84 | 60.81 | 8.24 | 95.9 | 58 | 939032.26 | 7737625.81 | 4782290 | 2955335.81 | 15125 | Unit #02 and Unit #03 are on bar , delivering an average load of 26.39 MW. Unit #01 is on standby due to TRCM and cooling water strainer issues.. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-28 | 2026 | 5 | 28 | Machai HPS | 2.6 | 1.87 | 1.49 | 36488 | 35552 | 30 | 27 | 58.47 | 4.671 | 76.45 | 70 | 47705.81 | 222833.82 | 166063.39 | 56770.43 | 936 | 1) Unit tripped at 2101,2142 due to 11kv line tripped, and 11kv line restored at 2115,2154hrs, while Unit synched at 2133,2200hrs. 2) Unit tripped at 2243hrs due to revers Power, while unit synched with system at 2325hrs | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-05-28 | 2026 | 5 | 28 | Malakand-3 HPS | 81 | 61 | 56.9 | 1365619 | 1355480 | 51 | 38.52 | 70.25 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3880332.6 | 1368566.37 | 10139 | As per available hydrology from the Irrigation Department all the three Units are on bar. Load variation is due to fluctuations in the hydrology of River Swat. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-28 | 2026 | 5 | 28 | Pehur HPS | 18 | 7.59 | 7.22 | 173400 | 169000 | 15.33 | 18 | 40.14 | 3.767 | 31.06 | 41 | 134193.55 | 505507.1 | 636623 | -131115.9 | 4400 | The plant remained operational throughout 24 hours as per available hydrology | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-28 | 2026 | 5 | 28 | Reshun HPS | 4.2 | 2.06 | 1.42 | 30000 | 29691 | 1.88 | 1.83 | 29.76 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 400234.68 | 406883.02 | 309 | nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-05-29 | 2026 | 5 | 29 | Daral Khwar HPS | 36.6 | 36.6 | 36.7 | 880280 | 877880 | 27.14 | 14.68 | 100.21 | 8.2683 | 85.93 | 48 | 754838.71 | 6241232.9 | 7258575.2 | -1017342.3 | 2400 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.7 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-29 | 2026 | 5 | 29 | Jabori HPS | 10.2 | 10.2 | 9.22 | 221195 | 219700 | 7.72 | 7.22 | 90.36 | 5.7092 | 98.96 | 79.57 | 242258.06 | 1383099.74 | 1254311.24 | 128788.5 | 1495 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 9.22 MW to the national grid according to the available hydrology. 2: Cooling Water Pump #02 has remained non-functional since 12-10-2025. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-05-29 | 2026 | 5 | 29 | Karora HPS | 11.8 | 11.82 | 10.56 | 251004 | 248325 | 12.85 | 8.33 | 88.63 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1931968.5 | 246431.5 | 2679 | 1. Unit No. 01 and 02 on bar, collectively delivering an average load of 10.46MW according to the available hydrology. 2. With both Cooling Water Pumps being operational and no standby pump, GCC temperatures of both the units are increasing resulting in partial load reduction/generation loss. 3. Despite of units on load, the Electrical Overall Window in SCADA System do not display active & reactive power; reported vide TR No. 44/2026. 4. Lube oil Pump No. 01 & 02 for both units do not provide sufficient oil flow, as a result TRB & TTB temperatures increases continuously; reported vide TR No. 45/2026. 5. Plant remained shutdown for cleaning of TRCM, Unit No. 02 shutdown at 10:37 hrs & Unit No. 01 at 10:38 hrs; likewise, Unit No. 02 & Unit No. 01 synchronized to the National Grid at 11:24 hrs & 11:29 hrs, respectively. 6. No rectification work on punch list items pertaining to the power house been carried out since 17-Apr-2026 except for installation of motors at the intake site by the sub-contractor, without effective supervision. 7. Motors for weir site gates being installed by the sub-contractor are neither tested/commissioned nor have protection from rain/theft. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-05-29 | 2026 | 5 | 29 | Koto HPS | 40.8 | 26.95 | 26.43 | 636500 | 629501 | 174.1 | 74.66 | 65 | 8.24 | 95.9 | 58 | 939032.26 | 7737625.81 | 5187088.24 | 2550537.57 | 6999 | Unit #02 and Unit #03 are on bar , delivering an average load of 26.43 MW. Unit #01 is on standby due to TRCM and cooling water strainer issues.. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-29 | 2026 | 5 | 29 | Machai HPS | 2.6 | 2.02 | 1.62 | 38908 | 37884 | 0 | 28 | 62.35 | 4.671 | 76.45 | 70 | 47705.81 | 222833.82 | 176956.16 | 45877.66 | 1024 | Unit Tripped due to line tripping at 0809 and 1233 from Katlang Grid, Line restored at 0950 and 1238 while unit synced at 1000 and 1251 respectively | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-05-29 | 2026 | 5 | 29 | Malakand-3 HPS | 81 | 60 | 56.32 | 1351689 | 1341590 | 51 | 38.46 | 69.53 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3840569.69 | 1408329.28 | 10099 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-29 | 2026 | 5 | 29 | Pehur HPS | 18 | 7.06 | 6.77 | 162500 | 159000 | 15.33 | 18 | 37.62 | 3.767 | 31.06 | 41 | 134193.55 | 505507.1 | 598953 | -93445.9 | 3500 | Plant remained operational throughout 24 hrs as per available hydrology and irrigation valve is open. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-29 | 2026 | 5 | 29 | Reshun HPS | 4.2 | 2.04 | 1.57 | 41000 | 40690 | 2.56 | 2.45 | 40.67 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 548501.2 | 258616.5 | 310 | nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-05-30 | 2026 | 5 | 30 | Daral Khwar HPS | 36.6 | 36.6 | 36.7 | 879830 | 877430 | 27.14 | 14.67 | 100.16 | 8.2683 | 85.93 | 48 | 754838.71 | 6241232.9 | 7254854.47 | -1013621.57 | 2400 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.7 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-30 | 2026 | 5 | 30 | Jabori HPS | 10.2 | 9.2 | 8.7 | 188805 | 187310 | 7.72 | 6.2 | 77.13 | 5.7092 | 98.96 | 79.57 | 242258.06 | 1383099.74 | 1069390.25 | 313709.49 | 1495 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 8.7 MW to the national grid according to the available hydrology. 2: Unit 01 and unit 02 were stopped at 1005 Hrs and 1130 Hrs respectively for refreshing governor PLC memory and adjustment of oil leakage from breakpads. Both units were then synchronized at 1200 Hrs 3: Unit 01 and 02 got tripped at 1637 Hrs due to low cooling water pressure and synchronized at 1715 Hrs. 4: Cooling Water Pump #02 has remained non-functional since 12-10-2025. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-05-30 | 2026 | 5 | 30 | Karora HPS | 11.8 | 11.82 | 10.69 | 256602 | 253988 | 12.85 | 8.53 | 90.61 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1976026.64 | 202373.36 | 2614 | 1. Unit No. 01 and 02 on bar, collectively delivering an average load of 10.69 MW according to the available hydrology. 2. Unit No. 02 was shut down at 11:19 hrs for cleaning of Cooling Water Pump (CWP) No. 02. Simultaneously, Unit No. 01 load was reduced to 2.85 MW; however, it subsequently tripped at 12:13 hrs due to low cooling water pressure. This indicates that a single CWP is insufficient to sustain even half of the load of one generating unit. 3. Unit No. 01 synchronized with the National Grid at 12:30 hrs and Unit No. 02 at 12:59 hrs, respectively. 4. Since 17-Apr-2026, rectification of powerhouse punch list items has remained inactive. The sole activity recorded was motor installation at the intake site by the sub-contractor, without adequate supervision. 5. Motors for weir site gates, being installed by the sub-contractor, are neither tested/commissioned nor have protection from rain/theft. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-05-30 | 2026 | 5 | 30 | Koto HPS | 40.8 | 27.23 | 26.63 | 617250 | 612848 | 174.1 | 74.37 | 63.04 | 8.24 | 95.9 | 58 | 939032.26 | 7737625.81 | 5049867.52 | 2687758.29 | 4402 | Unit #02 and Unit #03 are on bar , delivering an average load of 25.68 MW. Unit #01 is on standby due to TRCM and cooling water strainer issues.. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-30 | 2026 | 5 | 30 | Machai HPS | 2.6 | 2.06 | 1.37 | 33216 | 32472 | 0 | 28 | 53.23 | 4.671 | 76.45 | 70 | 47705.81 | 222833.82 | 151676.71 | 71157.11 | 744 | Unit stopped normally at 0957 due to choking and spillway inlet gate was opened for flushing unit was synced with system at 1254. Unit tripped due to 11 KV Line tripping at 1310 and 1525 line restored at 1328 and 1545 while unit was synced with system at 1335 and 1616 respectively | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-05-30 | 2026 | 5 | 30 | Malakand-3 HPS | 81 | 59 | 56.01 | 1344352 | 1333720 | 51 | 38.23 | 69.15 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3818040.24 | 1430858.72 | 10632 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-30 | 2026 | 5 | 30 | Pehur HPS | 18 | 6.7 | 3.9 | 94800 | 92000 | 15.33 | 12 | 21.94 | 3.767 | 31.06 | 41 | 134193.55 | 505507.1 | 346564 | 158943.1 | 2800 | Plant remained shutdown from 1110 hrs to 2025 hrs due to in search of dead body in irrigation canal | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-30 | 2026 | 5 | 30 | Reshun HPS | 4.2 | 2.2 | 1.66 | 36000 | 35680 | 2.21 | 2.2 | 35.71 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 480966.4 | 326151.3 | 320 | Line faults | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-05-31 | 2026 | 5 | 31 | Daral Khwar HPS | 36.6 | 36.6 | 36.7 | 880370 | 877570 | 27.14 | 14.68 | 100.22 | 8.2683 | 85.93 | 48 | 754838.71 | 6241232.9 | 7256012.03 | -1014779.13 | 2800 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.7 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-05-31 | 2026 | 5 | 31 | Jabori HPS | 10.2 | 8.4 | 8.24 | 197860 | 196310 | 7.72 | 6.47 | 80.83 | 5.7092 | 98.96 | 79.57 | 242258.06 | 1383099.74 | 1120773.05 | 262326.69 | 1550 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 8.24 MW to the national grid according to the available hydrology. 2: Cooling Water Pump #02 has remained non-functional since 12-10-2025. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-05-31 | 2026 | 5 | 31 | Karora HPS | 11.8 | 11.82 | 11.44 | 274480 | 271613 | 12.83 | 9.04 | 96.92 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 2113149.14 | 65250.86 | 2867 | 1. Unit No. 01 and 02 on bar, collectively delivering an average load of 11.44 MW according to the available hydrology. 2. Despite of both Cooling Water Pumps operational with 2.7 Bar pressure, GCC temperature of Unit No. 01 reached at 42.4 degree celcius. It is pertinent to mention that GCC alarm is at 40 degree celcius and trip is at 45 degree celcius. 3. Since 17-Apr-2026, rectification of powerhouse punch list items has remained inactive. The sole activity recorded was motor installation at the intake site by the sub-contractor, without adequate supervision. 4. Motors for weir site gates, being installed by the sub-contractor, are neither tested/commissioned nor have protection from rain/theft. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-05-31 | 2026 | 5 | 31 | Koto HPS | 40.8 | 27.05 | 26.63 | 633500 | 630524 | 174.1 | 81.52 | 64.7 | 8.24 | 95.9 | 58 | 939032.26 | 7737625.81 | 5195517.76 | 2542108.05 | 2976 | Key obstacle preventing full generation are 1) Frequent choking of Intake and Sand Trap Trash Racks 2) Non availability of TRCM 3) Non functional cooling water strainers. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-31 | 2026 | 5 | 31 | Machai HPS | 2.6 | 1.9 | 1.7 | 42888 | 41760 | 0 | 28 | 68.73 | 4.671 | 76.45 | 70 | 47705.81 | 222833.82 | 195060.96 | 27772.86 | 1128 | Unit tripped at 0747 due to 11 KV line tripping from Katlang Grid, Line restored at 0757 while unit synced with system at 0801 | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-05-31 | 2026 | 5 | 31 | Malakand-3 HPS | 81 | 59 | 56.57 | 1357651 | 1347060 | 51 | 38.67 | 69.84 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3856228.66 | 1392670.31 | 10591 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-05-31 | 2026 | 5 | 31 | Pehur HPS | 18 | 6.78 | 6.3 | 153100 | 150000 | 16.35 | 18 | 35.44 | 3.767 | 31.06 | 41 | 134193.55 | 505507.1 | 565050 | -59542.9 | 3100 | Plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-05-31 | 2026 | 5 | 31 | Reshun HPS | 4.2 | 2.22 | 1.66 | 40000 | 39688 | 2.51 | 2.45 | 39.68 | 13.48 | 59.4 | 45 | 59875.2 | 807117.7 | 534994.24 | 272123.46 | 312 | nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-06-01 | 2026 | 6 | 1 | Daral Khwar HPS | 36.6 | 36.6 | 36.6 | 877340 | 874940 | 35.02 | 14.63 | 99.88 | 8.2683 | 72.1 | 48 | 633333.33 | 5236590 | 7234266.4 | -1997676.4 | 2400 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.6 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-06-01 | 2026 | 6 | 1 | Jabori HPS | 10.2 | 8.3 | 8.08 | 181720 | 180225 | 7.1 | 5.94 | 74.23 | 5.7092 | 85.09 | 79.57 | 208300 | 1189226.36 | 1028940.57 | 160285.79 | 1495 | 1: Plant was shutdown at 2234 Hrs due to damaged red phase cable of generator stator and blue phase CT of unit 01 along with associated wiring in generator protection panel. 2: Cooling Water Pump #02 has remained non-functional since 12-10-2025. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-06-01 | 2026 | 6 | 1 | Karora HPS | 11.8 | 11.78 | 11.15 | 267586 | 264759 | 10.82 | 8.9 | 94.49 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 2059825.02 | 118574.98 | 2827 | 1. Unit No. 01 and 02 on bar, collectively delivering an average load of 11.15MW according to the available hydrology. 2. Since 17-Apr-2026, rectification of powerhouse punch list items has remained inactive. The sole activity recorded was motor installation at the intake site by the sub-contractor, without adequate supervision. 3. Motors for weir site gates, being installed by the sub-contractor, are neither tested/commissioned nor have protection from rain/theft. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-06-01 | 2026 | 6 | 1 | Koto HPS | 40.8 | 27.23 | 26.63 | 615500 | 612200 | 171.2 | 79.2 | 62.86 | 8.24 | 97.19 | 58 | 951666.67 | 7841733.33 | 5044528 | 2797205.33 | 3300 | Non functional cooling water strainers and non availability of TRCM are the main bottlenecks. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-01 | 2026 | 6 | 1 | Machai HPS | 2.6 | 1.82 | 1.6 | 40320 | 39376 | 0 | 28 | 64.62 | 4.671 | 83 | 70 | 51792 | 241920.43 | 183925.3 | 57995.14 | 944 | Unit tripped due to tripping of 11 KV line from Katlang Grid line at 1347 restored at 1419while unit was synced at 1432 | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-06-01 | 2026 | 6 | 1 | Malakand-3 HPS | 81 | 61 | 56.53 | 1356779 | 1345010 | 51 | 38.76 | 69.79 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 3850360.13 | 1398877.44 | 11769 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-01 | 2026 | 6 | 1 | Pehur HPS | 18 | 6.82 | 6.75 | 162200 | 157000 | 16.35 | 18 | 37.55 | 3.767 | 29.55 | 41 | 127666.67 | 480920.33 | 591419 | -110498.67 | 5200 | Plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-06-01 | 2026 | 6 | 1 | Reshun HPS | 4.2 | 2.13 | 1.57 | 36000 | 35691 | 2.26 | 2.2 | 35.71 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 481114.68 | 874045.9 | 309 | line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-06-02 | 2026 | 6 | 2 | Daral Khwar HPS | 36.6 | 36.6 | 36.5 | 875450 | 872650 | 35.02 | 14.59 | 99.66 | 8.2683 | 72.1 | 48 | 633333.33 | 5236590 | 7215332 | -1978742 | 2800 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.5 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-06-02 | 2026 | 6 | 2 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 7.1 | 0 | 0 | 5.7092 | 85.09 | 79.57 | 208300 | 1189226.36 | 0 | 1189226.36 | 0 | 1: On 01-06-2026 at 2234 hrs, an incident occurred on Unit-01, resulting in damage to one of the generator stator phase cables, a current transformer (CT), and associated wiring within the generator protection panel. Consequently, the plant, including Unit-02, was shut down as a precautionary measure to ensure personnel and equipment safety pending further inspection and assessment. The Project Authorities and the Management Consultant were promptly informed of the situation. 2: Cooling Water Pump #02 has remained non-functional since 12-10-2025. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-06-02 | 2026 | 6 | 2 | Karora HPS | 11.8 | 11.8 | 10.31 | 247514 | 244822 | 10.82 | 8.08 | 87.4 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1904715.16 | 273684.84 | 2692 | Unit No. 01 and 02 on bar, collectively delivering an average load of 10.31 MW according to the available hydrology. The plant was shutdown for trash rack cleaning at 8:04 Hrs. After completion of trash rack cleaning, the Unit #01 and Unit #02 were synchronized with the system at 09:12 hrs and 09:17 hrs, respectively. Unit # 01 electrically tripped at 21:57 Hrs, after resetting alarm the unit was resynchronized with system at 22:02 Hrs. Since 17-Apr-2026, rectification of powerhouse punch list items has remained inactive. The sole activity recorded was motor installation at the intake site by the sub-contractor, without adequate supervision. Motors for weir site gates, being installed by the sub-contractor, are neither tested/commissioned nor have protection from rain/theft. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-06-02 | 2026 | 6 | 2 | Koto HPS | 40.8 | 27.17 | 22.49 | 539750 | 538443 | 171.2 | 69.45 | 55.12 | 8.24 | 97.19 | 58 | 951666.67 | 7841733.33 | 4436770.32 | 3404963.01 | 1307 | Non availability of TRCM and non functional cooling water strainers are the main bottlenecks. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-02 | 2026 | 6 | 2 | Machai HPS | 2.6 | 1.75 | 1.31 | 31324 | 30710 | 16.6 | 28 | 50.2 | 4.671 | 83 | 70 | 51792 | 241920.43 | 143446.41 | 98474.02 | 614 | No data submitted for this date | engr.atifwazir@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-06-02 | 2026 | 6 | 2 | Malakand-3 HPS | 81 | 64 | 56.21 | 1349123 | 1337220 | 51 | 39.58 | 69.4 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 3828059.69 | 1421177.87 | 11903 | Unit # 01, 02 & 03 tripped at 20:37 Hrs due to tripping of the 132 kV supply lines. The supply was restored at 20:53 Hrs. Subsequently, Unit # 01, 02 & 03 were synchronized back to the system at 21:16 Hrs, 21:20 Hrs, and 21:18 Hrs, respectively. As per the available hydrology provided by the Irrigation Department, all three units are presently on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-02 | 2026 | 6 | 2 | Pehur HPS | 18 | 7.48 | 6.9 | 165800 | 162000 | 16.35 | 18 | 38.38 | 3.767 | 29.55 | 41 | 127666.67 | 480920.33 | 610254 | -129333.67 | 3800 | Plant operational 24 hrs + valve open | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-06-02 | 2026 | 6 | 2 | Reshun HPS | 4.2 | 2.12 | 1.59 | 37000 | 36684 | 2.4 | 2.26 | 36.71 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 494500.32 | 860660.26 | 316 | Line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-06-03 | 2026 | 6 | 3 | Daral Khwar HPS | 36.6 | 36.6 | 36.7 | 879830 | 877430 | 35.02 | 14.67 | 100.16 | 8.2683 | 72.1 | 48 | 633333.33 | 5236590 | 7254854.47 | -2018264.47 | 2400 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.7 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-06-03 | 2026 | 6 | 3 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 7.71 | 0 | 0 | 5.7092 | 85.09 | 79.57 | 208300 | 1189226.36 | 0 | 1189226.36 | 0 | 1: On 01-06-2026 at 2234 hrs, an incident occurred on Unit-01, resulting in damage to one of the generator stator phase cables, a current transformer (CT), and associated wiring within the generator protection panel. Consequently, the plant, including Unit-02, was shut down as a precautionary measure to ensure personnel and equipment safety pending further inspection and assessment. The Project Authorities and the Management Consultant were promptly informed of the situation. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-06-03 | 2026 | 6 | 3 | Karora HPS | 11.8 | 11.83 | 11.65 | 279593 | 276714 | 10.82 | 9.2 | 98.73 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 2152834.92 | 25565.08 | 2879 | Unit No. 01 and 02 on bar, collectively delivering an average load of 11.65 MW according to the available hydrology. Since 17-Apr-2026, rectification of powerhouse punch list items has remained inactive. The only activity partially carried out during this period was the installation of gate hoist motors at the intake site by the subcontractor till 23-May-2026, without supervision. Furthermore, the motors installed for the weir site gates have neither been tested and commissioned nor protected against rain and theft. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-06-03 | 2026 | 6 | 3 | Koto HPS | 40.8 | 27.15 | 26.77 | 642500 | 633621 | 171.2 | 82.67 | 65.61 | 8.24 | 97.19 | 58 | 951666.67 | 7841733.33 | 5221037.04 | 2620696.29 | 8879 | Non availability of TRCM and non functional cooling water strainer are the main bottlenecks. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-03 | 2026 | 6 | 3 | Machai HPS | 2.6 | 1.92 | 0.98 | 22327 | 22044 | 33.2 | 28 | 35.78 | 4.671 | 83 | 70 | 51792 | 241920.43 | 102967.52 | 138952.91 | 283 | 11KV line restored at 1111hrs which was tripped yesterday. and Unit synched at 1134hrs. Unit tripped at 1731 hrs due to line tripping and synched at 1734hrs | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-06-03 | 2026 | 6 | 3 | Malakand-3 HPS | 81 | 64 | 60.86 | 1460523 | 1448360 | 51 | 40.53 | 75.13 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 4146220.17 | 1103017.4 | 12163 | Due to Heavy rainfall and storms in the catchment area, the inflow is muddy with heavy trash accumulation at the Forebay, resulting in reduced load. However, as per the available hydrology from the Irrigation Department, all three units are currently on bar. Load variation is due to fluctuations in the hydrology of River Swat. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-03 | 2026 | 6 | 3 | Pehur HPS | 18 | 7.52 | 6.94 | 166500 | 162000 | 16.35 | 18 | 38.54 | 3.767 | 29.55 | 41 | 127666.67 | 480920.33 | 610254 | -129333.67 | 4500 | Plant remained operational throughout 24 hrs+Irrigation valve open. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-06-03 | 2026 | 6 | 3 | Reshun HPS | 4.2 | 2.05 | 1.58 | 37000 | 36690 | 2.49 | 2.26 | 36.71 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 494581.2 | 860579.38 | 310 | outgoing feeder breaker remained off 0.40hour due to line faults | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-06-04 | 2026 | 6 | 4 | Daral Khwar HPS | 36.6 | 36.6 | 36.5 | 876490 | 873690 | 35.02 | 14.61 | 99.78 | 8.2683 | 72.1 | 48 | 633333.33 | 5236590 | 7223931.03 | -1987341.03 | 2800 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.5 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-06-04 | 2026 | 6 | 4 | Jabori HPS | 10.2 | 5.1 | 5 | 8157 | 7735 | 7.1 | 0.27 | 3.33 | 5.7092 | 85.09 | 79.57 | 208300 | 1189226.36 | 44160.66 | 1145065.7 | 422 | 1: Stator insulation resistance test and its associated cable testing were conducted on Unit-02. In addition, the generator stator was also inspected. The test results and inspection findings were found satisfactory. Accordingly, Unit-02 was synchronized with the grid at 2223 hrs." 2: Cooling Water Pump #02 has remained non-functional since 12-10-2025. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-06-04 | 2026 | 6 | 4 | Karora HPS | 11.8 | 11.77 | 10.48 | 251406 | 248548 | 10.82 | 8.23 | 88.77 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1933703.44 | 244696.56 | 2858 | Unit No. 01 and 02 on bar, collectively delivering an average load of 10.48 MW according to the available hydrology. Since 17-Apr-2026, rectification of powerhouse punch list items has remained inactive. The only activity partially carried out during this period was the installation of gate hoist motors at the intake site by the subcontractor till 23-May-2026, without supervision. Furthermore, the motors installed for the weir site gates have neither been tested and commissioned nor protected against rain and theft. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-06-04 | 2026 | 6 | 4 | Koto HPS | 40.8 | 27.25 | 23.43 | 562250 | 558550 | 171.2 | 72.35 | 57.42 | 8.24 | 97.19 | 58 | 951666.67 | 7841733.33 | 4602452 | 3239281.33 | 3700 | Target power generation is currently constrained by the unavailability of the TRCM and non functional cooling water strainers. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-04 | 2026 | 6 | 4 | Machai HPS | 2.6 | 2.01 | 1.71 | 41228 | 40128 | 33.2 | 28 | 66.07 | 4.671 | 83 | 70 | 51792 | 241920.43 | 187437.89 | 54482.54 | 1100 | Unit tripped at 1526 hrs due to line tripping and synched at 1547 hrs | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-06-04 | 2026 | 6 | 4 | Malakand-3 HPS | 81 | 64 | 60.84 | 1460277 | 1448300 | 51 | 40.82 | 75.12 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 4146048.41 | 1103189.16 | 11977 | Due to heavy rainfall and storms in the catchment area of River Swat, the inflow is muddy with heavy trash accumulation at the Forebay, resulting in reduced load. However, as per the available hydrology from the Irrigation Department, all three units are currently on bar. Load variation is due to fluctuations in the hydrology of River Swat. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-04 | 2026 | 6 | 4 | Pehur HPS | 18 | 7.86 | 7.54 | 180900 | 177000 | 16.35 | 20 | 41.88 | 3.767 | 29.55 | 41 | 127666.67 | 480920.33 | 666759 | -185838.67 | 3900 | Plant remained operational throughout 24 hrs as per available hydrology + Irrigation valve open. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-06-04 | 2026 | 6 | 4 | Reshun HPS | 4.2 | 2.06 | 1.47 | 34000 | 33691 | 2.4 | 2.81 | 33.73 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 454154.68 | 901005.9 | 309 | Outgoing Feeder Breaker tripped 5times due to line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-06-05 | 2026 | 6 | 5 | Daral Khwar HPS | 36.6 | 36.6 | 36.4 | 874630 | 871830 | 35.02 | 14.58 | 99.57 | 8.2683 | 72.1 | 48 | 633333.33 | 5236590 | 7208551.99 | -1971961.99 | 2800 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.4 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-06-05 | 2026 | 6 | 5 | Jabori HPS | 10.2 | 5.1 | 5.1 | 122330 | 120800 | 7.1 | 4 | 49.97 | 5.7092 | 85.09 | 79.57 | 208300 | 1189226.36 | 689671.36 | 499555 | 1530 | 1: Unit-02 on bar delivering an average load equals to 5.10MW to the national grid. Unit-01 remains out of service due to a damaged Red phase stator terminal and is awaiting rectification by the contractor. 2: Cooling Water Pump #02 has remained non-functional since 12-10-2025. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-06-05 | 2026 | 6 | 5 | Karora HPS | 11.8 | 11.8 | 9.63 | 231155 | 228502 | 10.82 | 7.71 | 81.62 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1777745.56 | 400654.44 | 2653 | 1. Unit No. 01 and 02 on bar, collectively delivering an average load of 9.63 MW according to the available hydrology. 2. The plant was shut down for trash rack cleaning at 08:52 hrs. After completion of trash rack cleaning, the Unit #01 and Unit #02 were synchronized with the system at 09:46 hrs and 09:51 hrs, respectively. Total plant load 11.8MW. 3. At 11:49Hrs, the load on Unit No.01, decreased due to less hydrology in the Khan Khwar river, indicating the difference between actual and historical hydrology. Since 17-Apr-2026, rectification of powerhouse punch list items has remained inactive. The only activity partially carried out during this period was the installation of gate hoist motors at the intake site by the subcontractor till 23-May-2026, without supervision. Furthermore, the motors installed for the weir site gates have neither been tested and commissioned nor protected against rain and theft. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-06-05 | 2026 | 6 | 5 | Koto HPS | 40.8 | 27.15 | 25.17 | 604000 | 599038 | 171.2 | 77.72 | 61.68 | 8.24 | 97.19 | 58 | 951666.67 | 7841733.33 | 4936073.12 | 2905660.21 | 4962 | Non-functional strainer and non availability of TRCM are the two primary constraints in full generation. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-05 | 2026 | 6 | 5 | Machai HPS | 2.6 | 1.85 | 1.64 | 41280 | 40216 | 33.2 | 28 | 66.15 | 4.671 | 83 | 70 | 51792 | 241920.43 | 187848.94 | 54071.5 | 1064 | Unit tripped at 0758 hrs due to line tripping and synched at 0827 hrs | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-06-05 | 2026 | 6 | 5 | Malakand-3 HPS | 81 | 64 | 60.43 | 1450266 | 1438850 | 51 | 40.73 | 74.6 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 4118995.9 | 1130241.67 | 11416 | Due to heavy rainfall and storms in the catchment area of River Swat, the inflow is muddy with heavy trash accumulation at the Forebay, resulting in reduced load. However, as per the available hydrology from the Irrigation Department, all three units are currently on bar. Load variation is due to fluctuations in the hydrology of River Swat. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-05 | 2026 | 6 | 5 | Pehur HPS | 18 | 8.03 | 7.79 | 186900 | 182000 | 16.35 | 20 | 43.26 | 3.767 | 29.55 | 41 | 127666.67 | 480920.33 | 685594 | -204673.67 | 4900 | Plant remained operational throughout 24 hrs. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-06-05 | 2026 | 6 | 5 | Reshun HPS | 4.2 | 2.51 | 1.58 | 37000 | 36664 | 2.4 | 2.26 | 36.71 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 494230.72 | 860929.86 | 336 | Outgoing Feeder Breaker remained off 1.09hour due line faults tripping. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-06-06 | 2026 | 6 | 6 | Daral Khwar HPS | 36.6 | 36.6 | 36.3 | 872230 | 869430 | 35.02 | 14.54 | 99.3 | 8.2683 | 72.1 | 48 | 633333.33 | 5236590 | 7188708.07 | -1952118.07 | 2800 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.3 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-06-06 | 2026 | 6 | 6 | Jabori HPS | 10.2 | 9 | 4.83 | 115970 | 114480 | 7.1 | 3.79 | 47.37 | 5.7092 | 85.09 | 79.57 | 208300 | 1189226.36 | 653589.22 | 535637.14 | 1490 | 1: Unit-02 tripped at 1333 hrs during the testing of the Unit-01 generator CTs. Following the successful completion of the CT testing activities on Unit-01, Unit-02 was re-synchronized with the grid at 1504 hrs. 2: Subsequently, all preliminary checks and inspections were carried out on Unit-01 and found satisfactory. Unit-01 was then synchronized with the grid at 2019 hrs. 3: Cooling Water Pump 02 has remained non-functional since 12-10-2025. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-06-06 | 2026 | 6 | 6 | Karora HPS | 11.8 | 11.8 | 9.44 | 226670 | 223863 | 10.82 | 7.52 | 80.04 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1741654.14 | 436745.86 | 2807 | 1) Unit No. 01 and 02 on bar, collectively delivering an average load of 9.44 MW according to the available hydrology. 2) The load on Unit #01 and Unit #02 was reduced at 02:22 hrs and 03:41 hrs, respectively, due to less hydrology. This indicates a difference between the actual and historical hydrology in the Khan Khwar River. 3) Since 17-Apr-2026, rectification of powerhouse punch list items has remained inactive. The only activity partially carried out during this period was the installation of gate hoist motors at the intake site by the subcontractor till 23-May-2026, without supervision. Furthermore, the motors installed for the weir site gates have neither been tested and commissioned nor protected against rain and theft. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-06-06 | 2026 | 6 | 6 | Koto HPS | 40.8 | 26.75 | 22.85 | 548500 | 544745 | 171.2 | 70.58 | 56.02 | 8.24 | 97.19 | 58 | 951666.67 | 7841733.33 | 4488698.8 | 3353034.53 | 3755 | Unit#02&03 on bar and unit#01 on standby due to cooling water strainer issue. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-06 | 2026 | 6 | 6 | Machai HPS | 2.6 | 1.86 | 1.66 | 40468 | 39468 | 33.2 | 28 | 64.85 | 4.671 | 83 | 70 | 51792 | 241920.43 | 184355.03 | 57565.4 | 1000 | Smooth Operation | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-06-06 | 2026 | 6 | 6 | Malakand-3 HPS | 81 | 62 | 59.75 | 1433895 | 1422640 | 51 | 40.23 | 73.76 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 4072591.53 | 1176646.04 | 11255 | Due to heavy rainfall and storms in the catchment area of River Swat, the inflow is muddy with heavy trash accumulation at the Forebay, resulting in reduced load. However, as per the available hydrology from the Irrigation Department, all three units are currently on bar. Load variation is due to fluctuations in the hydrology of River Swat. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-06 | 2026 | 6 | 6 | Pehur HPS | 18 | 8.03 | 7.94 | 190500 | 185000 | 16.35 | 20 | 44.1 | 3.767 | 29.55 | 41 | 127666.67 | 480920.33 | 696895 | -215974.67 | 5500 | Plant operational 24 hours. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-06-06 | 2026 | 6 | 6 | Reshun HPS | 4.2 | 2.06 | 1.62 | 37000 | 36675 | 2.36 | 2.26 | 36.71 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 494379 | 860781.58 | 325 | Outgoing Feeder Breaker remain Off 03times. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-06-07 | 2026 | 6 | 7 | Daral Khwar HPS | 36.6 | 36.6 | 35.4 | 849000 | 846200 | 35.02 | 14.15 | 96.65 | 8.2683 | 72.1 | 48 | 633333.33 | 5236590 | 6996635.46 | -1760045.46 | 2800 | 1. Units No. 01,02 and 03 were on bar delivering an average load equal to 35.4 MW according to the available hydrology. 2. 132 kV line failed at 1537Hrs and was restored at 1603Hrs. 3. Units No. 03, 02 and 01 synchronized with national Grid at 1616Hrs, 1620Hrs and 1622Hrs respectively. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-06-07 | 2026 | 6 | 7 | Jabori HPS | 10.2 | 10 | 7.05 | 169130 | 167520 | 7.1 | 5.53 | 69.09 | 5.7092 | 85.09 | 79.57 | 208300 | 1189226.36 | 956405.18 | 232821.18 | 1610 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 7.05 MW to the national grid according to the available hydrology. 2: Cooling Water Pump #02 has remained non-functional since 12-10-2025. 3: The rectification of the punch list items remains pending. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-06-07 | 2026 | 6 | 7 | Karora HPS | 11.8 | 10.8 | 7.18 | 172378 | 169927 | 10.82 | 5.66 | 60.87 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1322032.06 | 856367.94 | 2451 | 1. Unit No. 01 and 02 on bar, collectively delivering an average load of 7.18 MW according to the available hydrology. 2. Both the units are unable to operate at rated capacity due to frequent choking of the intake trash rack and leakages from the under-sluice gates. 3. Since 17-Apr-2026, rectification of powerhouse punch list items has remained inactive. The only activity partially carried out during this period was the installation of gate hoist motors at the intake site by the subcontractor till 23-May-2026, without supervision. Furthermore, the motors installed for the weir site gates have neither been tested and commissioned nor protected against rain and theft. 4. At 09:22 hrs, Complex Shutdown for trash rack cleaning, Unit # 02 was synchronized with the grid at 10:18 hrs and its load was gradually increased to 5.9 MW. Subsequently, at 11:07 hrs, Unit # 01 synchronized with the grid and its load was also gradually increased to 5.0 MW. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-06-07 | 2026 | 6 | 7 | Koto HPS | 40.8 | 26.83 | 19.95 | 478750 | 477710 | 171.2 | 61.6 | 48.89 | 8.24 | 97.19 | 58 | 951666.67 | 7841733.33 | 3936330.4 | 3905402.93 | 1040 | 1) Unit #02 & Unit #03 were shut down at 14:06 hrs upon EPC Contractor's request to facilitate TRCM modification and installation works. Both units were subsequently restarted and synchronized with the grid at 21:04 hrs (Unit #03) and 21:09 hrs (Unit #02), in accordance with EPC Contractor instructions. 2) Unit#02 and Unit#03 on bar while unit#01 on standby due to cooling water strainer issue. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-07 | 2026 | 6 | 7 | Machai HPS | 2.6 | 1.7 | 1.61 | 39516 | 38588 | 30 | 28 | 63.33 | 4.671 | 83 | 70 | 51792 | 241920.43 | 180244.55 | 61675.88 | 928 | Smoothly Operation | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-06-07 | 2026 | 6 | 7 | Malakand-3 HPS | 81 | 63 | 59.59 | 1430112 | 1418550 | 51 | 40.03 | 73.57 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 4060883.08 | 1188354.48 | 11562 | Due to heavy rainfall and storms in the catchment area of River Swat, the inflow is muddy with heavy trash accumulation at the Forebay, resulting in reduced load. However, as per the available hydrology from the Irrigation Department, all three units are currently on bar. Load variation is due to fluctuations in the hydrology of River Swat. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-07 | 2026 | 6 | 7 | Pehur HPS | 18 | 8.12 | 7.98 | 191600 | 187000 | 16.35 | 20 | 44.35 | 3.767 | 29.55 | 41 | 127666.67 | 480920.33 | 704429 | -223508.67 | 4600 | Plant operational 24 hours. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-06-07 | 2026 | 6 | 7 | Reshun HPS | 4.2 | 2.5 | 1.67 | 35000 | 34645 | 2.2 | 2.14 | 34.72 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 467014.6 | 888145.98 | 355 | Outgoing feeder breaker remained Off for 1.15hours. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-06-08 | 2026 | 6 | 8 | Daral Khwar HPS | 36.6 | 36.6 | 36.6 | 877320 | 874520 | 35.02 | 14.63 | 99.88 | 8.2683 | 72.1 | 48 | 633333.33 | 5236590 | 7230793.72 | -1994203.72 | 2800 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 36.6 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-06-08 | 2026 | 6 | 8 | Jabori HPS | 10.2 | 8.4 | 6.96 | 166944 | 165360 | 7.1 | 5.46 | 68.2 | 5.7092 | 85.09 | 79.57 | 208300 | 1189226.36 | 944073.31 | 245153.05 | 1584 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 6.96 MW to the national grid according to the available hydrology. 2: Cooling Water Pump #02 has remained non-functional since 12-10-2025. 3: The rectification of the punch list items remains pending. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-06-08 | 2026 | 6 | 8 | Karora HPS | 11.8 | 11.7 | 8.02 | 192383 | 189945 | 10.82 | 6.9 | 67.93 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1477772.1 | 700627.9 | 2438 | 1. Unit No. 01 and 02 on bar, collectively delivering an average load of 8.02 MW according to the available hydrology. 2. Both the units are unable to operate at rated capacity due to frequent choking of the intake trash rack and leakages from the under-sluice gates. 3. Since 17-Apr-2026, rectification of powerhouse punch list items has remained inactive. The only activity partially carried out during this period was the installation of gate hoist motors at the intake site by the subcontractor till 23-May-2026, without supervision. Furthermore, the motors installed for the weir site gates have neither been tested and commissioned nor protected against rain and theft. 4 At 08:33 hrs, Complex Shutdown for trash rack cleaning, Unit # 01 was synchronized with the grid at 10:39 hrs and its load was gradually increased to 5.9 MW. Subsequently, at 10:44 hrs, Unit # 02 synchronized with the grid and its load was also gradually increased to 5.9 MW. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-06-08 | 2026 | 6 | 8 | Koto HPS | 40.8 | 26.98 | 26.8 | 643250 | 641250 | 171.2 | 82.77 | 65.69 | 8.24 | 97.19 | 58 | 951666.67 | 7841733.33 | 5283900 | 2557833.33 | 2000 | Unit#02 and unit#03 on bar while unit#01 on standby due to cooling water strainer issue. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-08 | 2026 | 6 | 8 | Machai HPS | 2.6 | 1.88 | 1.57 | 37444 | 36520 | 30.5 | 26 | 60.01 | 4.671 | 83 | 70 | 51792 | 241920.43 | 170584.92 | 71335.51 | 924 | Unit tripped three times due to Machai 11 KV line tripping from Katlang grid. (No operation for total of 100 minutes.) | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-06-08 | 2026 | 6 | 8 | Malakand-3 HPS | 81 | 63 | 58.68 | 1408266 | 1396530 | 51 | 38.7 | 72.44 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 3997846.43 | 1251391.14 | 11736 | As per message of SDO Head Works Malakand Irrigation Department CW NO. 18 dt: 08-06-2026, the water flow was diverted at 05:00Hrs dt: 09-06-2026, for about 06 running hours to facilitate search operation for the dead body in the power channel of jabban MKD-III-HPC. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-08 | 2026 | 6 | 8 | Pehur HPS | 18 | 8.9 | 8 | 192300 | 186000 | 16.35 | 20 | 44.51 | 3.767 | 29.55 | 41 | 127666.67 | 480920.33 | 700662 | -219741.67 | 6300 | Not reported | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-06-08 | 2026 | 6 | 8 | Reshun HPS | 4.2 | 2.44 | 1.62 | 38000 | 37650 | 2.4 | 2.32 | 37.7 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 507522 | 847638.58 | 350 | Line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-06-09 | 2026 | 6 | 9 | Daral Khwar HPS | 36.6 | 36.6 | 36.7 | 880640 | 877840 | 35.02 | 14.68 | 100.26 | 8.2683 | 72.1 | 48 | 633333.33 | 5236590 | 7258244.47 | -2021654.47 | 2800 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 36.7 MW according to the available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-06-09 | 2026 | 6 | 9 | Jabori HPS | 10.2 | 7.8 | 6.59 | 158070 | 156480 | 7.1 | 5.17 | 64.57 | 5.7092 | 85.09 | 79.57 | 208300 | 1189226.36 | 893375.62 | 295850.74 | 1590 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 6.59 MW to the national grid according to the available hydrology. 2: Cooling Water Pump #02 has remained non-functional since 12-10-2025. 3: The rectification of the punch list items remains pending. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-06-09 | 2026 | 6 | 9 | Karora HPS | 11.8 | 11.8 | 11.15 | 267699 | 264756 | 11.32 | 8.7 | 94.53 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 2059801.68 | 118598.32 | 2943 | 1. Unit No. 01 and 02 on bar, collectively delivering an average load of 11.15 MW according to the available hydrology. 2. Since 17-Apr-2026, rectification of powerhouse punch list items has remained inactive. The only activity partially carried out during this period was the installation of gate hoist motors at the intake site by the subcontractor till 23-May-2026, without supervision. Furthermore, the motors installed for the weir site gates have neither been tested and commissioned nor protected against rain and theft. 3. The contractor attempted to stop the leakage from the under-sluice gates by using sandbags. This action resulted in a reduction of the leakage; however, leakages still persists. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-06-09 | 2026 | 6 | 9 | Koto HPS | 40.8 | 37.58 | 26.94 | 637500 | 628894 | 171.2 | 80.6 | 65.1 | 8.24 | 97.19 | 58 | 951666.67 | 7841733.33 | 5182086.56 | 2659646.77 | 8606 | Unit #02 and Unit #03 are on bar , delivering an average load of 26.94 MW. Unit #01 is on standby due to TRCM and cooling water strainer issues.. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-09 | 2026 | 6 | 9 | Machai HPS | 2.6 | 1.66 | 0.74 | 20464 | 19976 | 30.8 | 16 | 32.79 | 4.671 | 83 | 70 | 51792 | 241920.43 | 93307.9 | 148612.54 | 488 | (1) - Unit tripped at 0856 hrs. due to reverse power, while resynched at 1010 hrs.. (2) - Unit stopped at 1157 hrs. due to no inflow - shut down at Malakand-3, for searching of dead body - while resynched at 2029 hrs. | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-06-09 | 2026 | 6 | 9 | Malakand-3 HPS | 81 | 64 | 31.11 | 746716 | 740750 | 51 | 27.07 | 38.41 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 2120545.02 | 3128692.54 | 5966 | As per message of SDO Head Works Malakand Irrigation Department CW NO. 18 dt: 08-06-2026, the water flow was diverted at 05:00Hrs dt: 09-06-2026, for about 06 running hours to facilitate search operation of the dead body in the power channel of jabban MKD-III-HPC, Unit 03, 01 & 02 desynchronized from the system at 06:05hrs, 06:23hrs & 06:42hrs respectively. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-09 | 2026 | 6 | 9 | Pehur HPS | 18 | 8.2 | 7.2 | 174200 | 170000 | 16.35 | 19 | 40.32 | 3.767 | 29.55 | 41 | 127666.67 | 480920.33 | 640390 | -159469.67 | 4200 | The plant remained operational for 24 hours. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-06-09 | 2026 | 6 | 9 | Reshun HPS | 4.2 | 2.16 | 1.55 | 36000 | 35690 | 2.3 | 2.21 | 35.71 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 481101.2 | 874059.38 | 310 | Nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-06-10 | 2026 | 6 | 10 | Daral Khwar HPS | 36.6 | 36.6 | 36.6 | 879160 | 876360 | 35.02 | 14.66 | 100.09 | 8.2683 | 72.1 | 48 | 633333.33 | 5236590 | 7246007.39 | -2009417.39 | 2800 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 36.6 MW according to available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-06-10 | 2026 | 6 | 10 | Jabori HPS | 10.2 | 7.6 | 6.56 | 157350 | 155760 | 7.1 | 5.14 | 64.28 | 5.7092 | 85.09 | 79.57 | 208300 | 1189226.36 | 889264.99 | 299961.37 | 1590 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 6.56 MW to the national grid according to the available hydrology. 2: Cooling Water Pump #02 has remained non-functional since 12-10-2025. 3: The rectification of the punch list items remains pending. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-06-10 | 2026 | 6 | 10 | Karora HPS | 11.8 | 11.5 | 10.59 | 254135 | 251246 | 11.32 | 8.3 | 89.74 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1954693.88 | 223706.12 | 2889 | 1.Unit No. 01 and 02 on bar, collectively delivering an average load of 10.59 MW according to the available hydrology. 2.Since 17-Apr-2026, rectification of powerhouse punch list items has remained inactive. The only activity partially carried out during this period was the installation of gate hoist motors at the intake site by the subcontractor till 23-May-2026, without supervision. Furthermore, the motors installed for the weir site gates have neither been tested and commissioned nor protected against rain and theft. 3.The contractor attempted to stop the leakage from the under sluice gates by using sandbags. This action resulted in a reduction of the leakage; however, leakage still persists. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-06-10 | 2026 | 6 | 10 | Koto HPS | 40.8 | 26.5 | 16.79 | 399250 | 395637 | 171.2 | 71.05 | 40.77 | 8.24 | 97.19 | 58 | 951666.67 | 7841733.33 | 3260048.88 | 4581684.45 | 3613 | Unit #02 and Unit #03 are on bar , delivering an average load of 16.79 MW. Unit #01 is on standby due to TRCM and cooling water strainer issues.. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-10 | 2026 | 6 | 10 | Machai HPS | 2.6 | 2.09 | 1.7 | 40520 | 39556 | 31.04 | 26 | 64.94 | 4.671 | 83 | 70 | 51792 | 241920.43 | 184766.08 | 57154.36 | 964 | Unit tripped at 0207 hrs. due to 132 KV (Mardan) line tripping; 11 KV line restored at 0217 hrs., while unit synched at 0226 hrs.. | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-06-10 | 2026 | 6 | 10 | Malakand-3 HPS | 81 | 66 | 61.35 | 1472444 | 1459010 | 51 | 40.53 | 75.74 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 4176707.93 | 1072529.64 | 13434 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-10 | 2026 | 6 | 10 | Pehur HPS | 18 | 7.29 | 6.86 | 164700 | 160000 | 16.35 | 18 | 38.12 | 3.767 | 29.55 | 41 | 127666.67 | 480920.33 | 602720 | -121799.67 | 4700 | Plant operational 24 hours. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-06-10 | 2026 | 6 | 10 | Reshun HPS | 4.2 | 2.17 | 1.51 | 34000 | 33670 | 2.4 | 2.08 | 33.73 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 453871.6 | 901288.98 | 330 | line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-06-11 | 2026 | 6 | 11 | Daral Khwar HPS | 36.6 | 36.6 | 36.7 | 881580 | 878780 | 35.02 | 14.7 | 100.36 | 8.2683 | 72.1 | 48 | 633333.33 | 5236590 | 7266016.67 | -2029426.67 | 2800 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 36.7 MW according to the available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-06-11 | 2026 | 6 | 11 | Jabori HPS | 10.2 | 7.5 | 6.31 | 151403 | 149790 | 6.49 | 5.22 | 61.85 | 5.7092 | 85.09 | 79.57 | 208300 | 1189226.36 | 855181.07 | 334045.29 | 1613 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 6.31 MW to the national grid according to the available hydrology. 2: Cooling Water Pump #02 has remained non-functional since 12-10-2025. 3: The rectification of the punch list items remains pending. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-06-11 | 2026 | 6 | 11 | Karora HPS | 11.8 | 10.35 | 9.32 | 223785 | 220896 | 10.82 | 7.32 | 79.02 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1718570.88 | 459829.12 | 2889 | Unit No. 01 and 02 on bar, collectively delivering an average load of 9.32 MW according to the available hydrology. Since 17-Apr-2026, rectification of powerhouse punch list items has remained inactive. The only activity partially carried out during this period was the installation of gate hoist motors at the intake site by the subcontractor till 23-May-2026, without supervision. Furthermore, the motors installed for the weir site gates have neither been tested and commissioned nor protected against rain and theft. The contractor attempted to stop the leakage from the under sluice gates by using sandbags.This action resulted in a reduction of the leakage; however, leakage still persists. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-06-11 | 2026 | 6 | 11 | Koto HPS | 40.8 | 39.1 | 31.56 | 764499 | 757088 | 171.2 | 98.07 | 78.07 | 8.24 | 97.19 | 58 | 951666.67 | 7841733.33 | 6238405.12 | 1603328.21 | 7411 | All units are on bar delivering in an average load of 31.56MW | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-11 | 2026 | 6 | 11 | Machai HPS | 2.6 | 1.67 | 1.49 | 38469 | 37444 | 31.04 | 26 | 61.65 | 4.671 | 83 | 70 | 51792 | 241920.43 | 174900.92 | 67019.51 | 1025 | Smooth operation. | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-06-11 | 2026 | 6 | 11 | Malakand-3 HPS | 81 | 67 | 63.24 | 1517825 | 1504180 | 41.67 | 51 | 78.08 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 4306016.09 | 943221.48 | 13645 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-11 | 2026 | 6 | 11 | Pehur HPS | 18 | 7.2 | 6.9 | 166200 | 162000 | 16.35 | 18 | 38.47 | 3.767 | 29.55 | 41 | 127666.67 | 480920.33 | 610254 | -129333.67 | 4200 | plant operation throughout 24 hours + irrigation valve open | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-06-11 | 2026 | 6 | 11 | Reshun HPS | 4.2 | 2 | 1.56 | 38000 | 37690 | 2.4 | 2.32 | 37.7 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 508061.2 | 847099.38 | 310 | Greasing of Unit No.2 and 3. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-06-12 | 2026 | 6 | 12 | Daral Khwar HPS | 36.6 | 36.6 | 36.4 | 873790 | 870990 | 35.02 | 14.57 | 99.48 | 8.2683 | 72.1 | 48 | 633333.33 | 5236590 | 7201606.62 | -1965016.62 | 2800 | 1. Units No. 01,02 and 03 were on bar delivering an average load equal to 36.4 MW according to the available hydrology and existing system constraints. 2. All units tripped due to grid over-frequency at 19:06 Hrs 3. Units No.03,02 and 01 were synchronized with the National grid at 19:14Hrs, 19:16Hrs and 19:18Hrs respectively. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-06-12 | 2026 | 6 | 12 | Jabori HPS | 10.2 | 9.3 | 6.28 | 150615 | 149020 | 6.49 | 5.22 | 61.53 | 5.7092 | 85.09 | 79.57 | 208300 | 1189226.36 | 850784.98 | 338441.38 | 1595 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 6.28 MW to the national grid according to the available hydrology. 2: Cooling Water Pump #02 has remained non-functional since 12-10-2025. 3: The rectification of the punch list items remains pending. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-06-12 | 2026 | 6 | 12 | Karora HPS | 11.8 | 11.75 | 8.2 | 196839 | 194202 | 10.82 | 6.39 | 69.51 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1510891.56 | 667508.44 | 2637 | 1. Unit No. 01 and 02 on bar, collectively delivering an average load of 8.20 MW according to the available hydrology. 2. Since 17-Apr-2026, rectification of powerhouse punch list items has remained inactive. The only activity partially carried out during this period was the installation of gate hoist motors at the intake site by the subcontractor till 23-May-2026, without supervision. Furthermore, the motors installed for the weir site gates have neither been tested and commissioned nor protected against rain and theft. 3. The contractor attempted to stop the leakage from the under sluice gates by using sandbags. This action resulted in a reduction of the leakage; however, leakage still persists. 4. Plant completely shutdown at 06:52 hrs for Trash Rack cleaning at intake site. After cleaning of Track Rack, Unit No. 02 was synchronized to the National Grid at 08:10 hrs and Unit No. 01 synchronized at 08:18 hrs. 5. At 10:43 hrs sand-trap level dropped again with Net Head at 140.9 meter, thereby load gradually decreased. After heavy rainfall after 16:40 hrs, water head dropped again resulting in complete shutdown of Unit No. 02 at 19:44 hrs due to choking of TRCM. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-06-12 | 2026 | 6 | 12 | Koto HPS | 40.8 | 38.38 | 31.56 | 815000 | 810509 | 171.2 | 104.94 | 83.23 | 8.24 | 97.19 | 58 | 951666.67 | 7841733.33 | 6678594.16 | 1163139.17 | 4491 | All units were operated and delivered average power of 31.56 to the system. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-12 | 2026 | 6 | 12 | Machai HPS | 2.6 | 1.8 | 1.45 | 34359 | 33572 | 31.03 | 26 | 55.06 | 4.671 | 83 | 70 | 51792 | 241920.43 | 156814.81 | 85105.62 | 787 | Unit tripped at 2401hrs due to 11kv line tripped because of stormy weather, and 11kv line restored at 0224 from grid, some wait for stable line, unit synched with system at 0329hrs. | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-06-12 | 2026 | 6 | 12 | Malakand-3 HPS | 81 | 67 | 63.25 | 1517889 | 1505100 | 51 | 41.68 | 78.08 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 4308649.77 | 940587.8 | 12789 | As per available hydrology from Irrigation Department all three units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-12 | 2026 | 6 | 12 | Pehur HPS | 18 | 7.6 | 7 | 168200 | 165000 | 16.35 | 18 | 38.94 | 3.767 | 29.55 | 41 | 127666.67 | 480920.33 | 621555 | -140634.67 | 3200 | Not reported | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-06-12 | 2026 | 6 | 12 | Reshun HPS | 4.2 | 2.21 | 1.63 | 38000 | 37645 | 2.4 | 2.32 | 37.7 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 507454.6 | 847705.98 | 355 | Nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-06-13 | 2026 | 6 | 13 | Daral Khwar HPS | 36.6 | 36.6 | 26.8 | 643880 | 641480 | 35.02 | 10.73 | 73.3 | 8.2683 | 72.1 | 48 | 633333.33 | 5236590 | 5303949.08 | -67359.08 | 2400 | 1. Units No. 01,02 and 03 were on bar delivering an average load equal to 26.8 MW according to the available hydrology and existing system constraints. 2. 132KV supply failed at 17:42 hrs.The RCC was informed, and as per RCC, There is a fault in the PESCO Madyan Grid. The breaker's yellow phase blasted on the incoming 132KV line from Khwazakhela Grid to Madyan. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-06-13 | 2026 | 6 | 13 | Jabori HPS | 10.2 | 9.2 | 4.22 | 101214 | 100110 | 6.49 | 3.46 | 41.35 | 5.7092 | 85.09 | 79.57 | 208300 | 1189226.36 | 571548.01 | 617678.35 | 1104 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 4.22 MW to the national grid according to the available hydrology. 2: Cooling Water Pump #02 has remained non-functional since 12-10-2025. 3: The rectification of the punch list items remains pending. 4: Due to heavy rainfall in the catchment area, the river water became highly turbid and contained excessive silt. To protect the turbine and other critical equipment from potential damage, the plant was shut down at 1446 Hrs as a precautionary measure. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-06-13 | 2026 | 6 | 13 | Karora HPS | 11.8 | 5.92 | 3.73 | 89632 | 87982 | 10.82 | 2.8 | 31.65 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 684499.96 | 1493900.04 | 1650 | 1. Unit No. 01 on bar, collectively delivering an average load of 3.73 MW according to the available hydrology. 2. Since 17-Apr-2026, rectification of powerhouse punch list items has remained inactive. The only activity partially carried out during this period was the installation of gate hoist motors at the intake site by the subcontractor till 23-May-2026, without supervision. Furthermore, the motors installed for the weir site gates have neither been tested and commissioned nor protected against rain and theft. 3. The contractor attempted to stop the leakage from the under sluice gates by using sandbags. This action resulted in a reduction of the leakage; however, leakage still persists. 4. At 17:13 hrs, the complex was shut down due to flood conditions caused by heavy rainfall in the upstream area. The excessive inflow resulted in a substantial accumulation of debris, silt, and floating material at the intake, leading to severe choking of the intake trash racks. The plant was safely shut down in a controlled manner until normal operating conditions could be restored. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-06-13 | 2026 | 6 | 13 | Koto HPS | 40.8 | 36.1 | 20.56 | 493500 | 490270 | 171.2 | 63.5 | 50.4 | 8.24 | 97.19 | 58 | 951666.67 | 7841733.33 | 4039824.8 | 3801908.53 | 3230 | All the units were operated according to inflow, average load of 20.56 were delivered to grid. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-13 | 2026 | 6 | 13 | Machai HPS | 2.6 | 1.59 | 1.29 | 32664 | 31768 | 31 | 26 | 52.35 | 4.671 | 83 | 70 | 51792 | 241920.43 | 148388.33 | 93532.1 | 896 | Unit operated normally as per available hydrology | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-06-13 | 2026 | 6 | 13 | Malakand-3 HPS | 81 | 67 | 63.04 | 1512933 | 1501200 | 51 | 41.23 | 77.83 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 4297485.24 | 951752.33 | 11733 | As per available hydrology from Irrigation Department all three units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-13 | 2026 | 6 | 13 | Pehur HPS | 18 | 7.5 | 7.2 | 174000 | 169000 | 16.35 | 18 | 40.28 | 3.767 | 29.55 | 41 | 127666.67 | 480920.33 | 636623 | -155702.67 | 5000 | Not reported | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-06-13 | 2026 | 6 | 13 | Reshun HPS | 4.2 | 2.23 | 1.58 | 37000 | 36675 | 2.36 | 2.26 | 36.71 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 494379 | 860781.58 | 325 | line faults | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-06-14 | 2026 | 6 | 14 | Daral Khwar HPS | 36.6 | 36.6 | 28.4 | 681700 | 679300 | 35.02 | 11.36 | 77.61 | 8.2683 | 72.1 | 48 | 633333.33 | 5236590 | 5616656.19 | -380066.19 | 2400 | 1: Units No. 01,02 and 03 were on bar delivering an average load equal to 28.4 MW according to the available hydrology and existing system constraints. 2: 132KV supply failed at 17:42 Hrs on 13-06-2026 due to a fault on the yellow phase of the MYN-1 breaker (Khwazakhela-Madyan) at Madyan Grid Station,and was restored at 02:30 Hrs on 14-06-2026. 3: During this shutdown window, comprehensive flushing of the intake, gravel trap and the sand trap was carried out as per designer recommendations regarding suspended bed load for month of june, with critical activities extending till 05:17Hrs. 4: Units No.03, 01 and 02 were subsequently synchronized with the national grid at 05:17 Hrs, 05:24 Hrs and 05:26 Hrs respectively. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-06-14 | 2026 | 6 | 14 | Jabori HPS | 10.2 | 8.6 | 6.28 | 94222 | 93130 | 6.49 | 3.46 | 38.49 | 5.7092 | 85.09 | 79.57 | 208300 | 1189226.36 | 531697.8 | 657528.56 | 1092 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 6.28 MW to the national grid according to the available hydrology. 2: Cooling Water Pump #02 has remained non-functional since 12-10-2025. 3: The rectification of the punch list items remains pending. 4: Unit-01 and Unit-02 were synchronized with the National Grid at 0900 hrs and 0945 hrs, respectively, following the improvement in water quality conditions 5: At 2108 hrs, Unit 01 tripped due to mechanical trip and was resynchronized at 0008 Hrs. 6: At 2235 Hrs, unit 02 tripped due to low cooling water pressure and was synchronized at 2355 Hrs. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-06-14 | 2026 | 6 | 14 | Karora HPS | 11.8 | 11.37 | 3.67 | 88108 | 87103 | 10.82 | 3.29 | 31.11 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 677661.34 | 1500738.66 | 1005 | 1. Unit No. 01 & 02 on bar, collectively delivering an average load of 3.67 MW according to the available hydrology. 2. Since 17-Apr-2026, rectification of powerhouse punch list items has remained inactive. The only activity partially carried out during this period was the installation of gate hoist motors at the intake site by the subcontractor till 23-May-2026, without supervision. Furthermore, the motors installed for the weir site gates have neither been tested and commissioned nor protected against rain and theft. 3. The contractor attempted to stop the leakage from the under sluice gates by using sandbags. This action resulted in a reduction of the leakage; however, leakage still persists. Moreover, motors for weir site gates, being installed by the sub-contractor, are neither tested/commissioned nor have protection from rain/theft. 4. Unit No. 02 & 01 synchronized with grid at 10:42 hrs and10:43 hrs respectively after cleaning of trash racks. 5. Despite 3 Bar pressure of both Cooling Water Pumps, GCC temperatures of both units increased and displayed alarms on SCADA resulting in load reduction of both units to drop GCC temperatures and ultimately avoid units' tripping. 6. Due to choking of trash racks head was dropped resulting in complete plant shutdown for trash racks cleaning at 1752 hrs. 7. After cleaning of trash racks for the second time in a single day, Unit No. 01 synchronized with the system at 2015 hrs, load gradually increased to 4MW & Unit No. 02 synchronized with the system at 2018 hrs, load gradually increased to 4MW as per available hydrology. 8. The plant load has been kept below the rated capacity due to reduced hydrological inflow compared to previous month. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-06-14 | 2026 | 6 | 14 | Koto HPS | 40.8 | 27.02 | 26.46 | 635000 | 632515 | 171.2 | 81.71 | 64.85 | 8.24 | 97.19 | 58 | 951666.67 | 7841733.33 | 5211923.6 | 2629809.73 | 2485 | Unit No.2 and 3 were operated while unit No.1 remain standby due to Head loss. Main bottlenecks are non availability of TRCM and non functional cooling water strainers. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-14 | 2026 | 6 | 14 | Machai HPS | 2.6 | 1.91 | 1.43 | 33160 | 32384 | 30.7 | 26 | 53.14 | 4.671 | 83 | 70 | 51792 | 241920.43 | 151265.66 | 90654.77 | 776 | Unit stopped at 1210 due to choking and spillway gate was opened at 1215 and was closed at 1330 while unit was synced with system at 1342 | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-06-14 | 2026 | 6 | 14 | Malakand-3 HPS | 81 | 65 | 62.53 | 1500824 | 1489430 | 51 | 41.06 | 77.2 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 4263791.26 | 985446.31 | 11394 | As per available hydrology from Irrigation Department all three units are in bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-14 | 2026 | 6 | 14 | Pehur HPS | 18 | 7.45 | 6.85 | 164500 | 160000 | 16.35 | 18 | 38.08 | 3.767 | 29.55 | 41 | 127666.67 | 480920.33 | 602720 | -121799.67 | 4500 | Plant remained operational throughout 24 hrs + Irrigation valve open. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-06-14 | 2026 | 6 | 14 | Reshun HPS | 4.2 | 2.25 | 1.72 | 40000 | 39634 | 2.51 | 2.44 | 39.68 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 534266.32 | 820894.26 | 366 | NIl | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-06-15 | 2026 | 6 | 15 | Daral Khwar HPS | 36.6 | 36.6 | 36.6 | 879090 | 876290 | 35.02 | 14.65 | 100.08 | 8.2683 | 72.1 | 48 | 633333.33 | 5236590 | 7245428.61 | -2008838.61 | 2800 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 36.6 MW according to available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-06-15 | 2026 | 6 | 15 | Jabori HPS | 10.2 | 8.4 | 7.13 | 171152 | 169400 | 6.49 | 3.46 | 69.92 | 5.7092 | 85.09 | 79.57 | 208300 | 1189226.36 | 967138.48 | 222087.88 | 1752 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 7.13 MW to the national grid according to the available hydrology. 2: Cooling Water Pump #02 has remained non-functional since 12-10-2025. 3: The rectification of the punch list items remains pending. 4: Both generating units were shut down at 2230 hrs to facilitate testing of cooling water pump 02. Both units were re-synchronized with the national grid at 2300 hrs | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-06-15 | 2026 | 6 | 15 | Karora HPS | 11.8 | 11.81 | 6.25 | 150097 | 147991 | 10.82 | 6.11 | 53 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1151369.98 | 1027030.02 | 2106 | 1. Unit No. 01 & 02 on bar, collectively delivering an average load of 6.25 MW according to the available hydrology. 2. Since 17-Apr-2026, rectification of powerhouse punch list items has remained inactive. The only activity partially carried out during this period was the installation of gate's hoist motors at the intake site by the subcontractor till 23-May-2026, without supervision. Furthermore, the motors installed for the weir site gates have neither been tested & commissioned nor protected against rain & theft. 3. The contractor attempted to stop the leakage from the under sluice gates by using sandbags. This action resulted in a reduction of the leakage; however, leakage still persists. 4. Unit No. 02 shutdown twice, at 08:29 hrs due to choking of trash racks and at 10:39 hrs for trash racks cleaning. Accordingly, Unit No. 02 synchronized with the system at 08:57 hrs and 15:03 hrs respectively after the cleaning of trash racks at intake site. 5. Water leakage from Shaft Seal of Unit No. 01 been observed at 08:35 hrs, therefore, immediately reported PMU, Consultant & Contractor vide TR # 56/2026. Also, Unit No. 01 tripped at 08:52 hrs due to choking of Shaft Seal which was ultimately rectified by the contractor at 12:45 hrs. 6. Unit No. 01 synchronized with the National Grid at 15:08 hrs but unfortunately was shutdown again at 15:16 hrs due to leakage from its Shaft Seal. After rectification works by the contractor, Unit No. 01 was synchronized again at 15:50 hrs. 7. Despite Cooling Water Pumps' combine pressure of 2.8 Bar, GCC temperatures of both units reached 43C whereas at 45C plant will trip. 8. Standby pump was operated to maintain oil flow & bearings temperature as TRB of Unit No. 02 reached at 63C. At 70C, plant will trip. 9. The plant load has been kept below the rated capacity due to reduced hydrological inflow compared to previous month. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-06-15 | 2026 | 6 | 15 | Koto HPS | 40.8 | 27.67 | 26.82 | 643750 | 637544 | 171.2 | 82.84 | 65.74 | 8.24 | 97.19 | 58 | 951666.67 | 7841733.33 | 5253362.56 | 2588370.77 | 6206 | Non available TRCM, Non functional cooling water strainers are the main bottlenecks. 2 out of 3 units were operated with average load of 26.82 MW. However with the operation of 3rd unit, Head suddenly drops. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-15 | 2026 | 6 | 15 | Machai HPS | 2.6 | 1.92 | 1.65 | 39264 | 38104 | 30.7 | 26 | 62.92 | 4.671 | 83 | 70 | 51792 | 241920.43 | 177983.78 | 63936.65 | 1160 | Unit tripped at 0446hrs due to reveres power, while unit synched at 0542hrs. unit tripped at 0843hrs due to line tripped, back restored at 0845hrs and unit synched at 0857hrs . unit tripped at 1104hrs due to issued PTW #695. line restored at 1130hrs. unit synched at 1140hrs | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-06-15 | 2026 | 6 | 15 | Malakand-3 HPS | 81 | 66 | 62.04 | 1489060 | 1476760 | 51 | 40.83 | 76.6 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 4227520.85 | 1021716.72 | 12300 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-15 | 2026 | 6 | 15 | Pehur HPS | 18 | 7.32 | 6.96 | 167100 | 162000 | 16.35 | 18 | 38.68 | 3.767 | 29.55 | 41 | 127666.67 | 480920.33 | 610254 | -129333.67 | 5100 | Plant remained operational throughout 24 hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-06-15 | 2026 | 6 | 15 | Reshun HPS | 4.2 | 2.39 | 1.46 | 35000 | 34480 | 2.22 | 2.14 | 34.72 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 464790.4 | 890370.18 | 520 | outgoing feeder breaker remained off 1.45hours due to line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-06-16 | 2026 | 6 | 16 | Daral Khwar HPS | 36.6 | 36.6 | 35.7 | 855910 | 853510 | 35.02 | 14.27 | 97.44 | 8.2683 | 72.1 | 48 | 633333.33 | 5236590 | 7057076.73 | -1820486.73 | 2400 | 1. Units No. 01,02 and 03 were on bar delivering an average load equal to 35.7 MW according to the available hydrology and existing system constraints. 2. 132 kV line tripped at 1508 Hrs. The line restored at 1527 Hrs. 3. Unit No. 02, 01 and 03 synchronized at 1545 Hrs, 1546 Hrs and 1547 Hrs respectively. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-06-16 | 2026 | 6 | 16 | Jabori HPS | 10.2 | 8.4 | 6.66 | 159784 | 158060 | 6.49 | 5.4 | 65.27 | 5.7092 | 85.09 | 79.57 | 208300 | 1189226.36 | 902396.15 | 286830.21 | 1724 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 6.66 MW to the national grid according to the available hydrology. 2: Cooling Water Pump #02 has remained non-functional since 12-10-2025. 3: The rectification of the punch list items remains pending. 4: Both units were shut down at 1100 hrs to facilitate testing of cooling water pump 02. Unit 01 and 02 were re-synchronized with the national grid at 1220 hrs and 1230 hrs respectively. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-06-16 | 2026 | 6 | 16 | Karora HPS | 11.8 | 10.71 | 9.68 | 232341 | 229466 | 10.82 | 7.64 | 82.04 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1785245.48 | 393154.52 | 2875 | 1. Unit No. 01 & 02 on bar, collectively delivering an average load of 9.68 MW according to the available hydrology. 2. Since 17-Apr-2026, rectification of powerhouse punch list items has remained inactive. The only activity partially carried out during this period was the installation of gate's hoist motors at the intake site by the subcontractor till 23-May-2026, without supervision. Furthermore, the motors installed for the weir site gates have neither been tested & commissioned nor protected against rain & theft. 3. The contractor attempted to stop the leakage from the under sluice gates by using sandbags. This action resulted in a reduction of the leakage; however, leakage still persists. 4. Oil leakage from TRB & TTB inlet pipe of Unit No. 01 been observed, therefore, immediately reported PMU, Consultant & Contractor vide TR# 57/2026. 5. Despite Cooling Water Pumps' combine pressure of 2.8 Bar, GCC temperatures of both units reached 44.8C whereas at 45C plant will trip. 6. Standby pump was operated to maintain oil flow & bearings temperatures which went above 60C of both Units. At 70C, plant will trip. 7. The plant load has been kept below the rated capacity due to high GCC temperatures & reduced hydrological inflow compared to previous month. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-06-16 | 2026 | 6 | 16 | Koto HPS | 40.8 | 27.35 | 26.14 | 627250 | 621952 | 171.2 | 80.71 | 64.06 | 8.24 | 97.19 | 58 | 951666.67 | 7841733.33 | 5124884.48 | 2716848.85 | 5298 | Two out of three units were operated during the day, with the generation load regulated according to the available Head. Mean load of 26.14 MW delivered to the National Grid. However, operations remain constrained by critical bottlenecks, specifically the unavailability of the Trash Rack Cleaning Machine (TRCM) and non-functional strainers. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-16 | 2026 | 6 | 16 | Machai HPS | 2.6 | 2.02 | 1.7 | 43140 | 42108 | 30.7 | 28 | 69.13 | 4.671 | 83 | 70 | 51792 | 241920.43 | 196686.47 | 45233.96 | 1032 | Unit tripped at 0101,0902hrs due to 11kv line tripped, 11kv line restored at 0140,0906hrs, and Unit synchronized with the system at 0154,0912hrs | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-06-16 | 2026 | 6 | 16 | Malakand-3 HPS | 81 | 68 | 63.27 | 1518542 | 1505850 | 51 | 41.46 | 78.11 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 4310796.8 | 938440.77 | 12692 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-16 | 2026 | 6 | 16 | Pehur HPS | 18 | 7.32 | 6.79 | 162900 | 159000 | 16.35 | 18 | 37.71 | 3.767 | 29.55 | 41 | 127666.67 | 480920.33 | 598953 | -118032.67 | 3900 | Plant operational 24 hrs along with irrigation valve open. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-06-16 | 2026 | 6 | 16 | Reshun HPS | 4.2 | 2.32 | 1.68 | 41000 | 40470 | 2.57 | 2.51 | 40.67 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 545535.6 | 809624.98 | 530 | Nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-06-17 | 2026 | 6 | 17 | Daral Khwar HPS | 36.6 | 36.6 | 34.7 | 833610 | 830810 | 35.02 | 13.89 | 94.9 | 8.2683 | 72.1 | 48 | 633333.33 | 5236590 | 6869386.32 | -1632796.32 | 2800 | 1: Units No. 01,02 and 03 were on bar delivering an average load equal to 34.7 MW according to the available hydrology and existing system constraints. 2: 132 kV line tripped at 1345 Hrs. The line restored at 1435 Hrs. 3: Unit No. 03, 02 and 01 synchronized at 1450 Hrs, 1455 Hrs and 1505 Hrs respectively. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-06-17 | 2026 | 6 | 17 | Jabori HPS | 10.2 | 9 | 6.49 | 155675 | 153980 | 6.49 | 5.4 | 63.59 | 5.7092 | 85.09 | 79.57 | 208300 | 1189226.36 | 879102.62 | 310123.74 | 1695 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 7.13 MW to the national grid according to the available hydrology. 2: Cooling Water Pump #02 has remained non-functional since 12-10-2025. 3: The rectification of the punch list items remains pending. 4: Both units were shut down at 2010 hrs to facilitate testing of cooling water pump 02. Unit 01 and 02 were re-synchronized with the national grid at 2110 hrs and 2125 hrs respectively. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-06-17 | 2026 | 6 | 17 | Karora HPS | 11.8 | 10.08 | 9.68 | 228409 | 225400 | 10.82 | 7.56 | 80.65 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1753612 | 424788 | 3009 | Unit No. 01 & 02 on bar, collectively delivering an average load of 9.68 MW according to the available hydrology. Since 17-Apr-2026, rectification of powerhouse punch list items has remained inactive. The only activity partially carried out during this period was the installation of gate's hoist motors at the intake site by the subcontractor till 23-May-2026, without supervision. Furthermore, the motors installed for the weir site gates have neither been tested & commissioned nor protected against rain & theft. The contractor attempted to stop the leakage from the under sluice gates by using sandbags. This action resulted in a reduction of the leakage; however, leakage still persists. Despite both cooling water pumps operating with a combined discharge pressure of 2.8 bar, the GCC temperatures of both units remained above 44.0°C. Considering that the unit trip set point is 45.0°C Upon the contractor's recommendation, the standby oil pump was started and kept in continuous operation to maintain adequate oil flow to the bearings, as the temperature of one of Unit #02's bearings had exceeded 60°C. Operation of the plant at its rated capacity was constrained by elevated GCC temperatures and reduced hydrological inflow relative to the previous month | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-06-17 | 2026 | 6 | 17 | Koto HPS | 40.8 | 27.58 | 21.54 | 517000 | 512159 | 171.2 | 66.53 | 52.8 | 8.24 | 97.19 | 58 | 951666.67 | 7841733.33 | 4220190.16 | 3621543.17 | 4841 | All three units were operated at different times based on availability; however, simultaneous operation of all three units is not feasible under current conditions, as it causes a drop in head. The main bottlenecks remain the non-availability of the Trash Rack Cleaning Machine (TRCM) and non-functional strainers. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-17 | 2026 | 6 | 17 | Machai HPS | 2.6 | 2.18 | 1.4 | 33464 | 32560 | 31 | 28.5 | 53.63 | 4.671 | 83 | 70 | 51792 | 241920.43 | 152087.76 | 89832.67 | 904 | unit tripped at 1040hrs due to reverse power, while unit synched at 1059hrs, unit tripped at 1550hrs due to 11kv line tripped because of stormy weather and line fault, 11kv line restored at 1840hrs, while unit synched at 1852hrs. unit normally stopped at 2125hrs due to turbine bearing head cover not,bolt losed, and damaged. | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-06-17 | 2026 | 6 | 17 | Malakand-3 HPS | 81 | 68.33 | 62.91 | 1509729 | 1497190 | 51 | 41.48 | 77.66 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 4286005.81 | 963231.75 | 12539 | No data submitted for this date | malakand03hpc@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-06-17 | 2026 | 6 | 17 | Pehur HPS | 18 | 7.21 | 6.78 | 162800 | 159000 | 16.35 | 19 | 37.69 | 3.767 | 29.55 | 41 | 127666.67 | 480920.33 | 598953 | -118032.67 | 3800 | Plant remained operational throughout 24 hrs and irrigation valve is open. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-06-17 | 2026 | 6 | 17 | Reshun HPS | 4.2 | 2.2 | 1.6 | 37000 | 36490 | 2.34 | 2.27 | 36.71 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 491885.2 | 863275.38 | 510 | Line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-06-18 | 2026 | 6 | 18 | Daral Khwar HPS | 36.6 | 36.6 | 36.6 | 877540 | 874740 | 35.02 | 14.63 | 99.9 | 8.2683 | 72.1 | 48 | 633333.33 | 5236590 | 7232612.74 | -1996022.74 | 2800 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 36.6 MW according to available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-06-18 | 2026 | 6 | 18 | Jabori HPS | 10.2 | 7.9 | 6.49 | 155676 | 153840 | 6.49 | 5.33 | 63.59 | 5.7092 | 85.09 | 79.57 | 208300 | 1189226.36 | 878303.33 | 310923.03 | 1836 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 6.49 MW to the national grid according to the available hydrology. 2: The rectification of the punch list items remains pending. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-06-18 | 2026 | 6 | 18 | Karora HPS | 11.8 | 9.08 | 7.11 | 170710 | 168275 | 10.82 | 5.51 | 60.28 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1309179.5 | 869220.5 | 2435 | Unit No. 01 & 02 on bar, collectively delivering an average load of 7.11 MW according to the available hydrology. Since 17-Apr-2026, rectification of powerhouse punch list items has remained inactive. The only activity partially carried out during this period was the installation of gate's hoist motors at the intake site by the subcontractor till 23-May-2026, without supervision. Furthermore, the motors installed for the weir site gates have neither been tested & commissioned nor protected against rain & theft. The plant was shut down at 08:47 hrs upon the request of the contractor to carry out the necessary rectification work on the lube oil system to mitigate the observed leakages. The required rectification work was completed by the contractor, and Unit #02 was synchronized with the system at 11:16 hrs. Subsequently, Unit #01 was started at 11:20 hrs; however, it failed to indicate RPM. Consequently, an emergency shutdown was initiated. After carrying out the necessary troubleshooting, Unit #01 was restarted and successfully synchronized with the system at 12:06 hrs Despite both cooling water pumps operating with a combined discharge pressure of 2.8 bar, the GCC temperatures of both units remained above 44.0°C. Considering that the unit trip setpoint is 45.0°C The standby oil pump was started and kept in continuous operation to maintain adequate oil flow to the bearings, as the temperature of one of Unit #02 bearings had exceeded 60°C. Operation of the plant at its rated capacity was constrained by elevated GCC temperatures and reduced hydrological inflow relative to the previous month | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-06-18 | 2026 | 6 | 18 | Koto HPS | 40.8 | 26.58 | 16.64 | 399250 | 391170 | 171.2 | 51.37 | 40.77 | 8.24 | 97.19 | 58 | 951666.67 | 7841733.33 | 3223240.8 | 4618492.53 | 8080 | Unit#02 and 01 were shutdown at 05:38hrs and 11:07 hrs for Trash Racks cleaning and after cleaning unit#01 and 02 were started and synchronized with grid at 14:49hrs and 15:10hrs respectively. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-18 | 2026 | 6 | 18 | Machai HPS | 2.6 | 1.79 | 0.48 | 12400 | 12188 | 33.2 | 28 | 19.87 | 4.671 | 83 | 70 | 51792 | 241920.43 | 56930.15 | 184990.28 | 212 | Unit synched at 1706 hrs after Turbine guide bearing Mechanical work was done | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-06-18 | 2026 | 6 | 18 | Malakand-3 HPS | 81 | 65 | 62.54 | 1500916 | 1488530 | 51 | 41.51 | 77.21 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 4261214.83 | 988022.74 | 12386 | Due to heavy rainfall in the catchment area of River Swat, the inflow is muddy with heavy trash accumulation at the Forebay, resulting in reduced load. However, as per the available hydrology from the Irrigation Department, all three units are currently on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-18 | 2026 | 6 | 18 | Pehur HPS | 18 | 7.16 | 6.85 | 164300 | 158000 | 16.35 | 18 | 38.03 | 3.767 | 29.55 | 41 | 127666.67 | 480920.33 | 595186 | -114265.67 | 6300 | Plant Operational 24 hours. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-06-18 | 2026 | 6 | 18 | Reshun HPS | 4.2 | 2.43 | 1.32 | 31000 | 30520 | 2.96 | 2.89 | 30.75 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 411409.6 | 943750.98 | 480 | Line faults due to heavy winds. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-06-19 | 2026 | 6 | 19 | Daral Khwar HPS | 36.6 | 36.6 | 36.6 | 879300 | 876500 | 35.02 | 14.66 | 100.1 | 8.2683 | 72.1 | 48 | 633333.33 | 5236590 | 7247164.95 | -2010574.95 | 2800 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 36.6 MW according to available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-06-19 | 2026 | 6 | 19 | Jabori HPS | 10.2 | 9.7 | 5.76 | 138186 | 136750 | 6.49 | 5.33 | 56.45 | 5.7092 | 85.09 | 79.57 | 208300 | 1189226.36 | 780733.1 | 408493.26 | 1436 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 5.76 MW to the national grid according to the available hydrology. 2: Cooling Water Pump-02 was operating satisfactorily on 18-06-2026. However, on 19-06-2026, the pump was taken out of service due to low discharge pressure, and abnormal noise was observed during its operation. 3: Both units were shut down at 1100 hrs due to heavy rainfall in the catchment area, which resulted in extremely muddy water conditions. After the muddy inflow subsided and water quality improved, Unit-01 and Unit-02 were resynchronized with the system at 1720 hrs and 1655 hrs, respectively. 4: The rectification of the punch list items remains pending. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-06-19 | 2026 | 6 | 19 | Karora HPS | 11.8 | 9.05 | 7.8 | 187248 | 184519 | 10.82 | 6.44 | 66.12 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1435557.82 | 742842.18 | 2729 | Unit No. 01 & 02 on bar, collectively delivering an average load of 7.80 MW according to the available hydrology. Since 17-Apr-2026, rectification of powerhouse punch list items has remained inactive. The only activity partially carried out during this period was the installation of gate's hoist motors at the intake site by the subcontractor till 23-May-2026, without supervision. Furthermore, the motors installed for the weir site gates have neither been tested & commissioned nor protected against rain & theft. Unit #01 on bar delivering 4.0 MW, tripped at 14:02 hrs due to high GCC temperature (>45°C). The unit was synchronized at 14:19 hrs and restored to 4.0 MW. Subsequently, it tripped again at 14:54 hrs on the same alarm and was resynchronized at 15:30 hrs. To mitigate the issue, the unit load was reduced to 2.85 MW; however, Unit #01 tripped again at 17:07 hrs due to high GCC temperature. The unit#1 was resynchronized at 17:34 hrs and loaded to 2.85 MW. Despite operating at the minimum allowable load, the GCC temperature remained close to the permissible limit. The standby oil pump was started and kept in continuous operation to maintain adequate oil flow to the bearings, as the temperature of one of Unit #02 bearings had exceeded 60°C. Operation of the plant at its rated capacity was constrained by elevated GCC temperatures and reduced hydrological inflow relative to the previous month | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-06-19 | 2026 | 6 | 19 | Koto HPS | 40.8 | 27.3 | 24.38 | 585000 | 583642 | 171.2 | 75.28 | 59.74 | 8.24 | 97.19 | 58 | 951666.67 | 7841733.33 | 4809210.08 | 3032523.25 | 1358 | Unit#01 and 02 on bar while unit#03 on standby due to cooling water strainer issue. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-19 | 2026 | 6 | 19 | Machai HPS | 2.6 | 2.14 | 1.64 | 41884 | 40876 | 33.2 | 28 | 67.12 | 4.671 | 83 | 70 | 51792 | 241920.43 | 190931.8 | 50988.64 | 1008 | Unit tripped at 1639 & 1758 hrs due to 11KV line tripping and Unit synchronised with the system at 1703 & 1818hrs respectively. | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-06-19 | 2026 | 6 | 19 | Malakand-3 HPS | 81 | 65 | 61.58 | 1477818 | 1465550 | 51 | 41.03 | 76.02 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 4195429.99 | 1053807.58 | 12268 | Due to heavy rainfall in the catchment area of River Swat, the inflow is muddy with heavy trash accumulation at the Forebay, resulting in reduced load. However, as per the available hydrology from the Irrigation Department, all three units are currently on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-19 | 2026 | 6 | 19 | Pehur HPS | 18 | 7.13 | 6.8 | 162300 | 158000 | 16.35 | 18 | 37.57 | 3.767 | 29.55 | 41 | 127666.67 | 480920.33 | 595186 | -114265.67 | 4300 | Plant operational 24 hours. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-06-19 | 2026 | 6 | 19 | Reshun HPS | 4.2 | 2.44 | 1.63 | 39000 | 38550 | 2.55 | 2.49 | 38.69 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 519654 | 835506.58 | 450 | Not reported | zafar.src@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days; Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-06-20 | 2026 | 6 | 20 | Daral Khwar HPS | 36.6 | 36.6 | 32.6 | 782600 | 780200 | 35.02 | 13.05 | 89.09 | 8.2683 | 72.1 | 48 | 633333.33 | 5236590 | 6450927.66 | -1214337.66 | 2400 | 1: Units No. 01,02 and 03 were on bar delivering an average load equal to 32.6 MW according to the available hydrology and existing system constraints. 2: Plant was shutdown at 0906Hrs under NOC No. 401/PEDO/RE(O&M)/DKHPC Dated 20-06-2026 issued against NOC request from PESCO, request No. 77-79/KWK-4, to remove hotspot on 132KV Yellow phase isolator (iso-102) affecting 132KV GSS Matta, Khwazakhela, Madyan, Shangla and Daral Khwar HPC.. 3: 132KV supply was restored after completion of said works at 1130hrs. 4: Units No.03,02 and 01 synchronized with the national grid at 1146Hrs, 1155Hrs and 1202Hrs respectively. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-06-20 | 2026 | 6 | 20 | Jabori HPS | 10.2 | 10.2 | 8.18 | 196438 | 194640 | 6.49 | 6.42 | 80.24 | 5.7092 | 85.09 | 79.57 | 208300 | 1189226.36 | 1111238.69 | 77987.67 | 1798 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 8.18 MW to the national grid according to the available hydrology. 2: Cooling water pump-02 experienced pressure drop at 1420 Hrs; therefore it was shutdown and Cooling water pump 01 was started. 3: Unit-01 tripped at 1707 Hrs and again at 1913 Hrs due to a Temperature Circuit Test Meter high-trip indication and was resynchronized at 1757 Hrs and 2032 Hrs respectively. The absence of heavy-duty exhaust fans in the generator hall results in elevated stator temperatures during the summer season (already mentioned in the punch list). 4: The rectification of the punch list items remains pending. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-06-20 | 2026 | 6 | 20 | Karora HPS | 11.8 | 8.8 | 5.6 | 134338 | 131954 | 10.82 | 4.58 | 47.44 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1026602.12 | 1151797.88 | 2384 | Unit No. 01 & 02 on bar, collectively delivering an average load of 5.60 MW according to the available hydrology. Since 17-Apr-2026, rectification of powerhouse punch list items has remained inactive. The only activity partially carried out during this period was the installation of gate's hoist motors at the intake site by the subcontractor till 23-May-2026, without supervision. Furthermore, the motors installed for the weir site gates have neither been tested & commissioned nor protected against rain & theft. "At 10:08 hrs, Unit #2 was shut down upon the request of the contractor to carry out an inspection of the Turbine Radial Bearing (TRB). At 18:02 hrs, following the completion of the necessary rectification works on the TRB by the contractor, Unit #2 was started and synchronized with the system. Subsequently, the unit load was gradually increased to 5.9 MW. later At 18:49Hrs unit#2 was shutdown due to chocking of intake trash rack." At 12:18 hrs., Unit #01 tripped due to high GCC temperature. After resetting the alarms, a start command was initiated from SCADA at 12:30 hrs. During the start-up sequence, the MIV opened, the brakes were released, and the governor system became operational. However, the lube oil system failed to operate automatically while the unit was in Auto mode. Consequently, as the unit started rolling, an emergency shutdown was applied. Representatives of the Contractor and Consultant were also present during the event. Accordingly, TR#60/2026 was issued regarding the malfunction of the lube oil system in Auto mode. After filling the upper oil tank and operate the lube oil pump manually , the unit#1 was started and synchronize with grid at 13:30 Hrs. Operation of the plant at its rated capacity was constrained by elevated GCC temperatures and reduced hydrological inflow relative to the previous month | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-06-20 | 2026 | 6 | 20 | Koto HPS | 40.8 | 27.25 | 25.66 | 615750 | 613465 | 171.2 | 79.23 | 62.88 | 8.24 | 97.19 | 58 | 951666.67 | 7841733.33 | 5054951.6 | 2786781.73 | 2285 | Unit no 1 and 2 were operated and delivering power to system while unit no 03 is standby due to the cooling water strainer issue. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-20 | 2026 | 6 | 20 | Machai HPS | 2.6 | 2 | 1.81 | 43392 | 42324 | 33.2 | 28 | 69.54 | 4.671 | 83 | 70 | 51792 | 241920.43 | 197695.4 | 44225.03 | 1068 | Smooth Operation | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-06-20 | 2026 | 6 | 20 | Malakand-3 HPS | 81 | 65 | 61.53 | 1476613 | 1464680 | 51 | 40.81 | 75.96 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 4192939.44 | 1056298.13 | 11933 | Due to heavy rainfall in the catchment area of River Swat, the inflow is muddy with heavy trash accumulation at the Forebay, resulting in reduced load. However, as per the available hydrology from the Irrigation Department, all three units are currently on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-20 | 2026 | 6 | 20 | Pehur HPS | 18 | 7.3 | 6.7 | 161100 | 157000 | 16.35 | 18 | 37.29 | 3.767 | 29.55 | 41 | 127666.67 | 480920.33 | 591419 | -110498.67 | 4100 | Not reported | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-06-20 | 2026 | 6 | 20 | Reshun HPS | 4.2 | 2.31 | 1.36 | 34000 | 33520 | 2.14 | 2.08 | 33.73 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 451849.6 | 903310.98 | 480 | Trees trimming campaign was held. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-06-21 | 2026 | 6 | 21 | Daral Khwar HPS | 36.6 | 36.6 | 35.8 | 858970 | 856170 | 35.02 | 14.32 | 97.79 | 8.2683 | 72.1 | 48 | 633333.33 | 5236590 | 7079070.41 | -1842480.41 | 2800 | 1: Units No. 01,02 and 03 were on bar delivering an average load equal to 35.8 MW according to the available hydrology and existing system constraints. 2: 132kV supply failed at 14:24Hrs and restored at 14:40Hrs. 3: Unit NO.03,02 and 01 synchronized with national grid at 14:47 Hrs, 14:54Hfrs and 14:54Hrs respectively. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-06-21 | 2026 | 6 | 21 | Jabori HPS | 10.2 | 9.2 | 8.4 | 201932 | 199680 | 6.7 | 6.6 | 82.49 | 5.7092 | 85.09 | 79.57 | 208300 | 1189226.36 | 1140013.06 | 49213.3 | 2252 | Unit 01 and 02 were on the bar delivering an average load equals to 8.41 MW to the national grid according to the available hydrology. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-06-21 | 2026 | 6 | 21 | Karora HPS | 11.8 | 10.18 | 6.32 | 151638 | 149087 | 10.82 | 5.05 | 53.54 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1159896.86 | 1018503.14 | 2551 | Unit No. 01 & 02 on bar, collectively delivering an average load of 6.32 MW according to the available hydrology. Since 17-Apr-2026, rectification of powerhouse punch list items has remained inactive. The only activity partially carried out during this period was the installation of gate's hoist motors at the intake site by the subcontractor till 23-May-2026, without supervision. Furthermore, the motors installed for the weir site gates have neither been tested & commissioned nor protected against rain & theft. "At 09:48 hrs, the plant complex was shut down to facilitate the cleaning of the intake trash rack, both cooling water pumps, and their respective strainers. Upon completion of the cleaning activities, Unit #01 was synchronized with the grid at 11:33 hrs, followed by Unit #02 at 11:41 hrs. It is pertinent to mention that during the start-up of both units, the lube oil system did not start automatically as part of the normal start sequence while the units were in Auto mode. Consequently, the lube oil system was started manually. " While Unit #02 was on bar and delivering 4.0 MW to the system, it was observed at 15:01 hrs that the wicket gate lock had engaged automatically. The representatives of the Contractor and Consultant were immediately informed and physically verified the condition at site. Following verification, the wicket gate lock was disengaged. This anomaly has been formally reported to the Contractor and Consultant vide TR#61/2026 for necessary corrective action. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-06-21 | 2026 | 6 | 21 | Koto HPS | 40.8 | 26.9 | 25.9 | 620000 | 617904 | 171.2 | 77.7 | 63.32 | 8.24 | 97.19 | 58 | 951666.67 | 7841733.33 | 5091528.96 | 2750204.37 | 2096 | Unit#01 and Unit#02 are on bar, delivering an average load of 25.90MW. Unit#03 on standby due to TRCM and cooling water strainer issues. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-21 | 2026 | 6 | 21 | Machai HPS | 2.6 | 1.87 | 1.5 | 41380 | 40308 | 33.2 | 27 | 66.31 | 4.671 | 83 | 70 | 51792 | 241920.43 | 188278.67 | 53641.76 | 1072 | Smooth Operation as per available inflow | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-06-21 | 2026 | 6 | 21 | Malakand-3 HPS | 81 | 64 | 61.06 | 1465322 | 1453200 | 51 | 40.78 | 75.38 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 4160075.64 | 1089161.93 | 12122 | Due to heavy rainfall in the catchment area of River Swat, the inflow is muddy with heavy trash accumulation at the Forebay, resulting in reduced load. However, as per the available hydrology from the Irrigation Department, all three units are currently on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-21 | 2026 | 6 | 21 | Pehur HPS | 18 | 6.5 | 5.5 | 132200 | 130000 | 16.35 | 16 | 30.6 | 3.767 | 29.55 | 41 | 127666.67 | 480920.33 | 489710 | -8789.67 | 2200 | Generation is less because unit # 03 and 01 tripped due to isolation of the Gadoon grid from national grid at 1716 Hrs and taken on bar at 1950 Hrs and 2040 hrs, respectively. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-06-21 | 2026 | 6 | 21 | Reshun HPS | 4.2 | 3.16 | 1.18 | 23000 | 22570 | 2 | 1.49 | 22.82 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 304243.6 | 1050916.98 | 430 | outgoing feeder breaker remained Off for for 9hours due to trees trimming campaign. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-06-22 | 2026 | 6 | 22 | Daral Khwar HPS | 36.6 | 36.6 | 36.7 | 881320 | 878520 | 35.02 | 14.69 | 100.33 | 8.2683 | 72.1 | 48 | 633333.33 | 5236590 | 7263866.92 | -2027276.92 | 2800 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 36.7 MW according to available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-06-22 | 2026 | 6 | 22 | Jabori HPS | 10.2 | 9 | 8.3 | 199272 | 197520 | 6.7 | 6.51 | 81.4 | 5.7092 | 85.09 | 79.57 | 208300 | 1189226.36 | 1127681.18 | 61545.18 | 1752 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 8.3 MW to the national grid according to the available hydrology. 2: The unavailability of mandatory maintenance tools is adversely affecting the plant's monthly preventive maintenance activities. The O&M staff are unable to carry out proper maintenance due to the lack of the required tools. 3: The rectification of the punch list items remains pending. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-06-22 | 2026 | 6 | 22 | Karora HPS | 11.8 | 10.49 | 9.09 | 216151 | 212967 | 11.01 | 7.12 | 76.32 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1656883.26 | 521516.74 | 3184 | 1. Unit No. 01 & 02 on bar, collectively delivering an average load of 9.01 MW according to the available hydrology. 2. All three lube oil pumps and both cooling water pumps are in operation to maintain the required temperatures and cooling water flow/ Pressure with in prescribed limits. No standby pump is available, as all pumps are currently in service. 3. The plant load has been kept below the rated capacity due to low hydrology. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-06-22 | 2026 | 6 | 22 | Koto HPS | 40.8 | 26.27 | 21.67 | 518500 | 513752 | 171.2 | 69.04 | 52.95 | 8.24 | 97.19 | 58 | 951666.67 | 7841733.33 | 4233316.48 | 3608416.85 | 4748 | Unit #01 and Unit #02 are on bar , delivering an average load of 21.67 MW. Unit #03 is on standby due to TRCM and cooling water strainer issues.. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-22 | 2026 | 6 | 22 | Machai HPS | 2.6 | 1.88 | 1.75 | 42940 | 41844 | 30 | 28.5 | 68.81 | 4.671 | 83 | 70 | 51792 | 241920.43 | 195453.32 | 46467.11 | 1096 | Smooth Operation | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-06-22 | 2026 | 6 | 22 | Malakand-3 HPS | 81 | 68 | 64.32 | 1543695 | 1531250 | 51 | 42.75 | 79.41 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 4383509.38 | 865728.19 | 12445 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-22 | 2026 | 6 | 22 | Pehur HPS | 18 | 6.68 | 5.88 | 141200 | 137000 | 16.35 | 16 | 32.69 | 3.767 | 29.55 | 41 | 127666.67 | 480920.33 | 516079 | -35158.67 | 4200 | plant operation throughout 24 hours + irrigation valve open | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-06-22 | 2026 | 6 | 22 | Reshun HPS | 4.2 | 2.45 | 1.8 | 41000 | 40470 | 2.6 | 2.51 | 40.67 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 545535.6 | 809624.98 | 530 | nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-06-23 | 2026 | 6 | 23 | Daral Khwar HPS | 36.6 | 36.6 | 36.6 | 879470 | 877070 | 35.02 | 14.67 | 100.12 | 8.2683 | 72.1 | 48 | 633333.33 | 5236590 | 7251877.88 | -2015287.88 | 2400 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 36.6 MW according to available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-06-23 | 2026 | 6 | 23 | Jabori HPS | 10.2 | 8.3 | 7.37 | 176989 | 175160 | 6.7 | 5.78 | 72.3 | 5.7092 | 85.09 | 79.57 | 208300 | 1189226.36 | 1000023.47 | 189202.89 | 1829 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 7.37 MW to the national grid according to the available hydrology. 2: The unavailability of mandatory maintenance tools is adversely affecting the plant's monthly preventive maintenance activities. The O&M staff are unable to carry out proper maintenance due to the lack of the required tools. 3: The rectification of the punch list items remains pending. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-06-23 | 2026 | 6 | 23 | Karora HPS | 11.8 | 10.5 | 9.06 | 217325 | 214153 | 11.01 | 7.09 | 76.74 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1666110.34 | 512289.66 | 3172 | 1. Unit No. 01 & 02 on bar, collectively delivering an average load of 9.06 MW according to the available hydrology. 2. All three lube oil pumps and both cooling water pumps are in operation to maintain the required temperatures and cooling water flow/ Pressure with in prescribed limits. No standby pump is available, as all pumps are currently in service. 3. The plant load has been kept below the rated capacity due to low hydrology. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-06-23 | 2026 | 6 | 23 | Koto HPS | 40.8 | 26.42 | 26.69 | 404500 | 400741 | 171.2 | 54.11 | 41.31 | 8.24 | 97.19 | 58 | 951666.67 | 7841733.33 | 3302105.84 | 4539627.49 | 3759 | Unit #01 and Unit #02 are on bar, delivering an average load of 16.69MW.Unit#03 is on standby due to TRCM and cooling water strainer issues. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-23 | 2026 | 6 | 23 | Machai HPS | 2.6 | 1.99 | 1.78 | 43040 | 42064 | 30 | 28.5 | 68.97 | 4.671 | 83 | 70 | 51792 | 241920.43 | 196480.94 | 45439.49 | 976 | Unit tripped at 0305 & 0733 hrs. due to 11 KV line tripping from Katlang grid; 11 KV line restored at 0308 & 0738 hrs., while unit resynched at 0312 & 0743 hrs., respectively. | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-06-23 | 2026 | 6 | 23 | Malakand-3 HPS | 81 | 67 | 64.26 | 1542348 | 1529880 | 51 | 42.6 | 79.34 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 4379587.48 | 869650.09 | 12468 | As per available hydrology from the Irrigation Department all the three Units are on bar. Load variation is due to variation in the hydrology of River Swat. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-23 | 2026 | 6 | 23 | Pehur HPS | 18 | 6.06 | 5.8 | 139300 | 136000 | 16.35 | 15 | 32.25 | 3.767 | 29.55 | 41 | 127666.67 | 480920.33 | 512312 | -31391.67 | 3300 | Operating head for unit # 01 drooped to minimum therefore, Unit # 01 taken off the bar at 1120 hours. Unit # 03 running on 5.8 MW load + irrigation valve open. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-06-23 | 2026 | 6 | 23 | Reshun HPS | 4.2 | 2.3 | 1.71 | 40000 | 39490 | 2.54 | 2.44 | 39.68 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 532325.2 | 822835.38 | 510 | nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-06-24 | 2026 | 6 | 24 | Daral Khwar HPS | 36.6 | 36.6 | 36.6 | 879020 | 876220 | 35.02 | 14.65 | 100.07 | 8.2683 | 72.1 | 48 | 633333.33 | 5236590 | 7244849.83 | -2008259.83 | 2800 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 36.6 MW according to available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-06-24 | 2026 | 6 | 24 | Jabori HPS | 10.2 | 7.3 | 6.57 | 157765 | 156000 | 6.7 | 5.16 | 64.45 | 5.7092 | 85.09 | 79.57 | 208300 | 1189226.36 | 890635.2 | 298591.16 | 1765 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 8.18 MW to the national grid according to the available hydrology. 2: Unit-01 was shut down at 1210 Hrs for scheduled monthly preventive maintenance and was resynchronized with the system at 1350 Hrs. However, the maintenance activities were carried out with limited tools. The unavailability of mandatory maintenance tools is adversely affecting the plant's maintenance program. Consequently, the O&M staff are unable to execute maintenance activities effectively due to the lack of the required tools. 3: The rectification of the punch list items remains pending. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-06-24 | 2026 | 6 | 24 | Karora HPS | 11.8 | 10.26 | 8.82 | 211590 | 208407 | 10.82 | 7.04 | 74.71 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1621406.46 | 556993.54 | 3183 | 1. Unit No. 01 & 02 on bar, collectively delivering an average load of 8.82 MW according to the available hydrology. 2. All three lube oil pumps and both cooling water pumps are in operation to maintain the required temperatures and cooling water flow/ Pressure with in prescribed limits. No standby pump is available, as all pumps are currently in service. 3. The plant load has been kept below the rated capacity due to low hydrology. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-06-24 | 2026 | 6 | 24 | Koto HPS | 40.8 | 26.7 | 25.58 | 614000 | 611893 | 171.02 | 79.01 | 62.7 | 8.24 | 97.19 | 58 | 951666.67 | 7841733.33 | 5041998.32 | 2799735.01 | 2107 | Unit 01 and Unit 02 were opreated and delievering power to he system, while Unit 03 sandby due to cooling water strainer issue. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-24 | 2026 | 6 | 24 | Machai HPS | 2.6 | 2.03 | 1.69 | 41984 | 40920 | 30 | 29 | 67.28 | 4.671 | 83 | 70 | 51792 | 241920.43 | 191137.32 | 50783.11 | 1064 | Unit tripped at 0501, 1201 & 1301 hrs. due to 11 KV line tripping; 11 KV line restored at 0515, 1211 & 1339 hrs.; while unit resynched at 0605, 1216 & 1401 hrs. respectively. | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-06-24 | 2026 | 6 | 24 | Malakand-3 HPS | 81 | 68 | 63.7 | 1528770 | 1516440 | 51 | 42.24 | 78.64 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 4341112.79 | 908124.78 | 12330 | As per available hydrology from Irrigation Department all three units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-24 | 2026 | 6 | 24 | Pehur HPS | 18 | 5.8 | 5.76 | 138400 | 135000 | 16.35 | 15 | 32.04 | 3.767 | 29.55 | 41 | 127666.67 | 480920.33 | 508545 | -27624.67 | 3400 | Not reported | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-06-24 | 2026 | 6 | 24 | Reshun HPS | 4.2 | 2.14 | 1.59 | 40000 | 39480 | 2.54 | 2.44 | 39.68 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 532190.4 | 822970.18 | 520 | Nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-06-25 | 2026 | 6 | 25 | Daral Khwar HPS | 36.6 | 36.6 | 36.6 | 879590 | 876790 | 35.02 | 14.66 | 100.14 | 8.2683 | 72.1 | 48 | 633333.33 | 5236590 | 7249562.76 | -2012972.76 | 2800 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 36.6 MW according to available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-06-25 | 2026 | 6 | 25 | Jabori HPS | 10.2 | 7.4 | 6.32 | 151686 | 150000 | 6.7 | 4.96 | 61.96 | 5.7092 | 85.09 | 79.57 | 208300 | 1189226.36 | 856380 | 332846.36 | 1686 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 6.32 MW to the national grid according to the available hydrology. 2: plant was shut down at 1419 Hrs for scheduled monthly preventive maintenance of unit 02 and cleaning of cooling water strainers and was subsequently resynchronized with the system at 1521 Hrs. However, the maintenance activities were carried out with limited tools. The unavailability of mandatory maintenance tools is adversely affecting the plant's monthly preventive maintenance program. Consequently, the O&M staff are unable to execute maintenance activities effectively due to the lack of the required tools. 3: The rectification of the punch list items remains pending. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-06-25 | 2026 | 6 | 25 | Karora HPS | 11.8 | 11.12 | 7.11 | 170701 | 168081 | 10.82 | 5.67 | 60.28 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1307670.18 | 870729.82 | 2620 | 1.Unit No. 01 & 02 on bar, collectively delivering an average load of 7.11 MW according to the available hydrology. 2.All three lube oil pumps and both cooling water pumps are in operation to maintain the required temperatures and cooling water flow/ Pressure with in prescribed limits. No standby pump is available, as all pumps are currently in service. 3.The plant load has been kept below the rated capacity due to low hydrology. 4.Unit No. 02 was shutdown at 04:33 hrs. due to sudden drop in head caused by muddy water and trash rack choking. 5.Unit No. 01 Mechanically tripped at 06:38 hrs. following a rise in GCC temperature to 45℃. 6.Complex shutdown from 06:38 hrs. to 10:21 hrs. due to a failure in SCADA start sequence. The motorized heat exchanger cooling water valve and lube oil motorized valve failed to open, resulting in both units being unavailable for operation. 7.At 11:42 hrs., Complex Shutdown for trash rack cleaning, Unit # 02 was synchronized with the grid at 13:20 hrs. and its load was gradually increased to 5.7MW. Subsequently, at 13:24 hrs., Unit # 01 synchronized with the grid and its load was also gradually increased to 5.0 MW, as per available hydrology. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-06-25 | 2026 | 6 | 25 | Koto HPS | 40.8 | 26.25 | 24.22 | 581250 | 578416 | 171.2 | 74.79 | 59.36 | 8.24 | 97.19 | 58 | 951666.67 | 7841733.33 | 4766147.84 | 3075585.49 | 2834 | Unit No. 01 and 02 were operated and delevring power to system ,while unit No .03 is standby due to cooling water strainers issue. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-25 | 2026 | 6 | 25 | Machai HPS | 2.6 | 2.12 | 1.85 | 45056 | 44000 | 30 | 29 | 72.21 | 4.671 | 83 | 70 | 51792 | 241920.43 | 205524 | 36396.43 | 1056 | (1) - Unit tripped at 0637 hrs., due to reverse power, while resynched at 0701 hrs. (2) - Unit tripped at 1531 hrs. due to 11 KV line tripping; 11 KV line restored at 1535 hrs., while unit synched at 1547 hrs. | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-06-25 | 2026 | 6 | 25 | Malakand-3 HPS | 81 | 68 | 64.69 | 1552676 | 1541150 | 51 | 43 | 79.87 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 4411850.11 | 837387.46 | 11526 | As per available hydrology from Irrigation Department all three units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-25 | 2026 | 6 | 25 | Pehur HPS | 18 | 6 | 5.6 | 135300 | 132000 | 16.35 | 15 | 31.32 | 3.767 | 29.55 | 41 | 127666.67 | 480920.33 | 497244 | -16323.67 | 3300 | Not reported | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-06-25 | 2026 | 6 | 25 | Reshun HPS | 4.2 | 2.15 | 1.69 | 39000 | 38688 | 2.48 | 2.38 | 38.69 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 521514.24 | 833646.34 | 312 | Nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-06-26 | 2026 | 6 | 26 | Daral Khwar HPS | 36.6 | 36.6 | 23.6 | 566090 | 563740 | 35.02 | 9.43 | 64.45 | 8.2683 | 72.1 | 48 | 633333.33 | 5236590 | 4661171.44 | 575418.56 | 2350 | 1: Units No. 01,02 and 03 were on bar delivering an average load equal to 23.6 MW according to the available hydrology and existing system constraints. 2: At 1402 hrs, a fault on the generation busbar resulted in the shutdown of all generating units for inspection. Preliminary investigations identified damage to the outer insulation and cable guard ground wire of 11 kV Red Phase Cable of Main Transformer No. 1, generation busbar PT, and possible damage to the isolation transformer. 3: The 132 kV Main Transformer No.2 SF6 circuit breaker trip coil was replaced and the 11 kV cable was successfully tested using a Megger and re-insulated with heat-shrink insulation. 4: The transformer has been isolated from service as a precautionary measure and will remain out of operation pending detailed diagnostic testing, assessment, and confirmation of its condition scheduled for the morning. 5: As an interim restoration measure, the damaged PT was replaced with the PT from Unit No. 1, While this arrangement necessitated keeping Unit No.1 out of service until a replacement PT is installed, it enabled the safe restoration and synchronization of Units No.2 and No.3, thereby restoring plant generation to 30.6 MW and significantly mitigating generation losses. Following successful replacement and system checks: 6: Unit No. 2 was synchronized to the grid at 2200 hours. Unit No. 3 was synchronized to the grid at 2204 hours. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-06-26 | 2026 | 6 | 26 | Jabori HPS | 10.2 | 7.4 | 6.23 | 149554 | 147600 | 6.7 | 4.89 | 61.09 | 5.7092 | 85.09 | 79.57 | 208300 | 1189226.36 | 842677.92 | 346548.44 | 1954 | Unit 01 and 02 were on the bar delivering an average load equals to 6.23 MW to the national grid according to the available hydrology. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-06-26 | 2026 | 6 | 26 | Karora HPS | 11.8 | 11.1 | 7.11 | 170701 | 168081 | 10.82 | 7.2 | 60.28 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1307670.18 | 870729.82 | 2620 | 1.Unit No. 01 & 02 on bar, collectively delivering an average load of 7.11 MW according to the available hydrology. 2.All three lube oil pumps and both cooling water pumps are in operation to maintain the required temperatures and cooling water flow/ Pressure with in prescribed limits for both units. No standby pump is available, as all pumps are currently in service. 3.The plant load has been kept below the rated capacity due to low hydrology. 4.Unit No. 01 was safely shutdown at 20:11Hrs due to a rapid head drop resulting from adverse weather conditions, rainfall, and subsequent trash rack choking. The shutdown was carried out as a precautionary measure to safeguard the unit and ensure safe plant operation under the prevailing abnormal conditions | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-06-26 | 2026 | 6 | 26 | Koto HPS | 40.8 | 27.02 | 24.99 | 599750 | 597746 | 171.2 | 77.17 | 61.25 | 8.24 | 97.19 | 58 | 951666.67 | 7841733.33 | 4925427.04 | 2916306.29 | 2004 | Unit No. 01 and 02 were operated and delevring power to system ,while unit No .03 is standby due to cooling water strainers issue. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-26 | 2026 | 6 | 26 | Machai HPS | 2.6 | 2.16 | 1.91 | 45464 | 44440 | 30 | 29 | 72.86 | 4.671 | 83 | 70 | 51792 | 241920.43 | 207579.24 | 34341.19 | 1024 | Unit remained on bar delivering power to national grid as per available hydrology. | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-06-26 | 2026 | 6 | 26 | Malakand-3 HPS | 81 | 69 | 65.06 | 1561392 | 1550000 | 51 | 43.21 | 80.32 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 4437185 | 812052.57 | 11392 | As per available hydrology from Irrigation Department all three units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-26 | 2026 | 6 | 26 | Pehur HPS | 18 | 6.05 | 5.7 | 136600 | 134000 | 16.35 | 15 | 31.62 | 3.767 | 29.55 | 41 | 127666.67 | 480920.33 | 504778 | -23857.67 | 2600 | plant operational 24 hrs + irrigation valve open. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-06-26 | 2026 | 6 | 26 | Reshun HPS | 4.2 | 2.52 | 1.71 | 37000 | 36684 | 2.34 | 2.27 | 36.71 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 494500.32 | 860660.26 | 316 | outgoing feeder breaker remained Off 1.10hours due to line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-06-27 | 2026 | 6 | 27 | Daral Khwar HPS | 36.6 | 30.6 | 30.7 | 734890 | 734890 | 35.02 | 12.29 | 83.66 | 8.2683 | 72.1 | 48 | 633333.33 | 5236590 | 6076290.99 | -839700.99 | 0 | 1: Units No. 02 and 03 were on bar delivering an average load equal to 30.7 MW according to the available hydrology and existing system constraints. 2: On 26 June, 2026 at 1402 Hrs, a fault was recorded on the generation busbar. Subsequent inspection revealed that the Yellow Phase (Phase B) of Potential Transformer (PT) had experienced catastrophic failure, rendering it irreparable and unserviceable. To facilitate the earlier possible restoration of generation, the damaged busbar PT was temporarily replaced with the corresponding PT from Unit No. 1 as an interim operational measure. Consequently, Unit No. 1 was retained out of service pending until procurement and installation of a replacement PT. This arrangement enabled the safe energization, synchronization and commercial operation of Unit No. 2 and No. 3, restoring the plant's available generation capacity to 30.6 MW and substantially minimizing the generation losses while maintain operational safety and system reliability. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-06-27 | 2026 | 6 | 27 | Jabori HPS | 10.2 | 9.5 | 7.6 | 182508 | 179760 | 6.7 | 5.96 | 74.55 | 5.7092 | 85.09 | 79.57 | 208300 | 1189226.36 | 1026285.79 | 162940.57 | 2748 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 7.6 MW to the national grid. 2: Both Cooling Water Pumps are in operation to keep the temperatures within permissible limits, as the absence of a ventilation system in the generator hall has caused the stator and bearing temperatures of both units to exceed the threshold limits and remain in an alarm state. Moreover, full load cannot be imposed on the generators, as it results in a further rise in temperatures despite the improved hydrological conditions following recent rainfall. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-06-27 | 2026 | 6 | 27 | Karora HPS | 11.8 | 10 | 2.62 | 62946 | 61489 | 10.82 | 2.23 | 22.23 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 478384.42 | 1700015.58 | 1457 | Unit No. 01 & 02 on bar, collectively delivering an average load of 2.62 MW according to the available hydrology. All three lube oil pumps and both cooling water pumps are in operation to maintain the required temperatures and cooling water flow/ Pressure with in prescribed limits for both units. No standby pump is available, as all pumps are currently in service. As Unit #01 had already been shut down due to the choking of the intake trash rack, PTW No. 43/2026 was issued upon request of the GRC representative for maintenance of the Generator Air Cooler (GCC) and shaft seal of both units. Subsequently, Unit #02 was shut down at 09:24 hrs to execute the maintenance work under the issued PTW, resulting in the complete shutdown of the Complex. While the plant was under PTW, cleaning of the intake trash rack was carried out. The under-sluice gates were opened to flush out river-borne material and accumulated debris from the intake structure. Following the completion of maintenance work on the Generator Air Cooler (GCC) of Unit #02.The unit was successfully started and synchronized with the national grid at 19:21 hrs and the load was gradually increased to 5.9 MW, in accordance with the available hydrology. Following the completion of maintenance work on the Generator Air Cooler (GCC) and Shaft Seal of Unit #01. The unit was successfully started and synchronized with the national grid at 23:12 hrs and the load was gradually increased to 4.3 MW, in accordance with the available hydrology. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-06-27 | 2026 | 6 | 27 | Koto HPS | 40.8 | 26.05 | 20.71 | 497000 | 489547 | 171.2 | 63.95 | 50.76 | 8.24 | 97.19 | 58 | 951666.67 | 7841733.33 | 4033867.28 | 3807866.05 | 7453 | The required generation from the Kotu Power House was affected due to two reasons: first, trash rack cleaning when all the units were shut down, and second, a shear pin failure in Unit No. 1; meanwhile, Unit No. 3 is already facing a failure-to-start issue. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-27 | 2026 | 6 | 27 | Machai HPS | 2.6 | 1.93 | 1.72 | 42840 | 41800 | 26 | 29 | 68.65 | 4.671 | 83 | 70 | 51792 | 241920.43 | 195247.8 | 46672.63 | 1040 | unit tripped at 1456 due to reverse power and synced back with system at 1511 | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-06-27 | 2026 | 6 | 27 | Malakand-3 HPS | 81 | 68 | 64.23 | 1541595 | 1529960 | 51 | 42.54 | 79.3 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 4379816.49 | 869421.07 | 11635 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-27 | 2026 | 6 | 27 | Pehur HPS | 18 | 6.09 | 5.72 | 137300 | 134000 | 16.35 | 15 | 31.78 | 3.767 | 29.55 | 41 | 127666.67 | 480920.33 | 504778 | -23857.67 | 3300 | Plant remained off the bar for 1 hour due to isolation of Gadoon grid due to fault on Wah-8 line. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-06-27 | 2026 | 6 | 27 | Reshun HPS | 4.2 | 2.17 | 1.72 | 40000 | 39682 | 2.54 | 2.44 | 39.68 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 534913.36 | 820247.22 | 318 | Nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-06-28 | 2026 | 6 | 28 | Daral Khwar HPS | 36.6 | 30.6 | 30.2 | 722060 | 722060 | 35.02 | 12.08 | 82.2 | 8.2683 | 72.1 | 48 | 633333.33 | 5236590 | 5970208.7 | -733618.7 | 0 | 1: Units No. 02 and 03 were on bar delivering an average load equal to 30.2 MW according to the available hydrology and existing system constraints. 2: 132 kV line tripped at 1031 Hrs and restored at 1042 Hrs. Units No. 03 and 02 synchronized at 1051 Hrs and 1052 Hrs respectively. 3: Unit No. 1 was retained out of service pending until procurement and installation of a replacement PT. 4. Total units Genrated are equal to Net Generation because the Auxillary is switched from 11KV busbar to 132KV busbar as an interim arrangement. Daily Aux. Consumption = 2200kWH | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-06-28 | 2026 | 6 | 28 | Jabori HPS | 10.2 | 7.9 | 7.25 | 174110 | 171360 | 6.7 | 5.69 | 71.12 | 5.7092 | 85.09 | 79.57 | 208300 | 1189226.36 | 978328.51 | 210897.85 | 2750 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 7.25 MW to the national grid. 2: Unit-01 tripped at 1144 Hrs and 1306 Hrs due to a Temperature Circuit Test Meter high-trip indication, as RTD No. 05 exceeded its set limit of 70°C. The unit was subsequently resynchronized at 1238 Hrs and 1436 Hrs, respectively. 3: Both Cooling Water Pumps are currently in operation to maintain temperatures within permissible limits. However, due to the absence of a ventilation system in the generator hall, the stator and bearing temperatures of both units continue to exceed the threshold limits (65°C) and remain in an alarm state. 4: Full load cannot be imposed on the generators, as it causes a further increase in temperatures despite the availability of adequate hydrology in the Siran River. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-06-28 | 2026 | 6 | 28 | Karora HPS | 11.8 | 11.2 | 10.18 | 244402 | 241211 | 10.82 | 7.92 | 86.3 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1876621.58 | 301778.42 | 3191 | 1. Unit No. 01 & 02 on bar, collectively delivering an average load of 10.18 MW according to the available hydrology. 2. All three lube oil pumps and both cooling water pumps are in operation to maintain the required temperatures and cooling water flow/ Pressure with in prescribed limits for both units. No standby pump is available, as all pumps are currently in service. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-06-28 | 2026 | 6 | 28 | Koto HPS | 40.8 | 26.67 | 23.55 | 565250 | 562117 | 171.2 | 72.73 | 57.73 | 8.24 | 97.19 | 58 | 951666.67 | 7841733.33 | 4631844.08 | 3209889.25 | 3133 | 1) Non Availability of TRCM 2) Non functional cooling water Strainers 3) Starting problem of unit No.3 | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-28 | 2026 | 6 | 28 | Machai HPS | 2.6 | 2.23 | 1.8 | 43396 | 42372 | 24 | 29 | 69.54 | 4.671 | 83 | 70 | 51792 | 241920.43 | 197919.61 | 44000.82 | 1024 | Unit tripped due to Governor fault at 1045,1524,1701 and 1803 while synced back to system at 1057,1537,1706 and 1813. Unit tripped due to high temperature at 1301 and 1425 while synced to the system at 1307 and 1438. Unit tripped due to line tripping from katlang grid at 1115 and 2140 line restored at 1120 and 2146 while unit was synced to system at 1122 and 2150 | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-06-28 | 2026 | 6 | 28 | Malakand-3 HPS | 81 | 67 | 64.18 | 1540425 | 1528450 | 51 | 42.71 | 79.24 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 4375493.82 | 873743.75 | 11975 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-28 | 2026 | 6 | 28 | Pehur HPS | 18 | 5.98 | 5.8 | 139200 | 136000 | 16.35 | 15 | 32.22 | 3.767 | 29.55 | 41 | 127666.67 | 480920.33 | 512312 | -31391.67 | 3200 | Plant remained operational throughout 24 hrs as per available hydrology and irrigation valve is open | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-06-28 | 2026 | 6 | 28 | Reshun HPS | 4.2 | 2.62 | 1.9 | 47000 | 46679 | 2.93 | 2.87 | 46.63 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 629232.92 | 725927.66 | 321 | nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-06-29 | 2026 | 6 | 29 | Daral Khwar HPS | 36.6 | 30.6 | 29.7 | 710260 | 710260 | 35.02 | 11.88 | 80.86 | 8.2683 | 72.1 | 48 | 633333.33 | 5236590 | 5872642.76 | -636052.76 | 0 | 1: Units No. 02 and 03 were on bar delivering an average load equal to 29.7 MW according to the available hydrology and existing system constraints. 2: 132 kV T-Line tripped at 1023 Hrs and restored at 1033 Hrs. The T-Line tripped again at 1044 Hrs and restored at 1055 Hrs. 3: Units No. 03 and 02 synchronized at 1107 Hrs and 1113 Hrs respectively. 4: Unit No. 1 was retained out of service pending until procurement and installation of a replacement PT. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-06-29 | 2026 | 6 | 29 | Jabori HPS | 10.2 | 7.8 | 6.88 | 165220 | 162480 | 6.7 | 5.4 | 67.49 | 5.7092 | 85.09 | 79.57 | 208300 | 1189226.36 | 927630.82 | 261595.54 | 2740 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 6.88 MW to the national grid according to the available hydrology and prevailing system constraints. 2: Both Cooling Water Pumps and all lube oil pumps are currently in operation to maintain temperatures within permissible limits. However, due to the absence of a ventilation system in the generator hall, the stator and bearing temperatures of both units continue to exceed the threshold limits (65°C) and remain in an alarm state. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-06-29 | 2026 | 6 | 29 | Karora HPS | 11.8 | 11.2 | 9.31 | 223391 | 220163 | 10.82 | 7.49 | 78.88 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1712868.14 | 465531.86 | 3228 | 1. Unit No. 01 & 02 on bar, collectively delivering an average load of 9.31 MW according to the available hydrology. 2. All three lube oil pumps and both cooling water pumps are in operation to maintain the required temperatures and cooling water flow/ Pressure with in prescribed limits for both units. No standby pump is available, as all pumps are currently in service. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-06-29 | 2026 | 6 | 29 | Koto HPS | 40.8 | 27.25 | 24.85 | 596500 | 592476 | 171.2 | 76.76 | 60.92 | 8.24 | 97.19 | 58 | 951666.67 | 7841733.33 | 4882002.24 | 2959731.09 | 4024 | 1) Non Availability of TRCM 2) Non functional cooling water strainers 3) Starting problem of Unit No.3 | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-29 | 2026 | 6 | 29 | Machai HPS | 2.6 | 2.11 | 1.81 | 47020 | 45892 | 0 | 29 | 75.35 | 4.671 | 83 | 70 | 51792 | 241920.43 | 214361.53 | 27558.9 | 1128 | Unit tripped due to governor fault at 1249 and 2150 while unit synced back with system at 1301 and 2203 | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-06-29 | 2026 | 6 | 29 | Malakand-3 HPS | 81 | 66 | 63.7 | 1528798 | 1515970 | 51 | 42.38 | 78.64 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 4339767.32 | 909470.25 | 12828 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-29 | 2026 | 6 | 29 | Pehur HPS | 18 | 6.41 | 5.95 | 142900 | 139000 | 16.35 | 18 | 33.08 | 3.767 | 29.55 | 41 | 127666.67 | 480920.33 | 523613 | -42692.67 | 3900 | Plant remained operational throughout 24 hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-06-29 | 2026 | 6 | 29 | Reshun HPS | 4.2 | 2.62 | 1.54 | 36000 | 35682 | 2.3 | 2.2 | 35.71 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 480993.36 | 874167.22 | 318 | Works in Line. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-06-30 | 2026 | 6 | 30 | Daral Khwar HPS | 36.6 | 30.6 | 25.5 | 609730 | 609730 | 35.02 | 10.2 | 69.41 | 8.2683 | 72.1 | 48 | 633333.33 | 5236590 | 5041430.56 | 195159.44 | 0 | 1: Units No. 02 and 03 were on bar delivering an average load equal to 25.5 MW according to the available hydrology and existing system constraints. 2: NOC for shut down issued to PESCO at 0845Hrs against their request for emergency maintenance on 132 KV Barikot-Swat T/L. Unit # 03 and Unit #2 were shutdown at 0907Hrs and 0909Hrs respectively under NOC-416/PEDO/RE(O&M)/DKHPC. 132kV supply line. 3: 132kV supply line restored at 0923 HRS and failed again at 0938Hrs and restored at 0949Hrs. 4: Unit #2 Synchronized with national Grid at 1001 Hrs. 5: 132kV supply line failed again at 1007Hrs and restored at 1018Hrs. However, RCC instructed to keep units on standby. 6: 132kV supply line failed at 1041Hrs and restored at 1102Hrs. 7: Unit #03 and Unit #2 synchronized with national Grid at 1115Hrs and 1121Hrs respectively. 8: 132 KV supply line failed at 22:05 HRS due to bad weather and restored at 22:.28 HRS. The tripping event caused damage to outer PVC insulation of red phase cable of MTR 1. Hence plant restored with MTR 2 while rectification works on MTR 1 cable are under process. 9: Unit No. 1 is retained out of service pending until procurement and installation of a replacement PT. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-06-30 | 2026 | 6 | 30 | Jabori HPS | 10.2 | 6.8 | 6.25 | 149998 | 147290 | 6.7 | 4.9 | 61.27 | 5.7092 | 85.09 | 79.57 | 208300 | 1189226.36 | 840908.07 | 348318.29 | 2708 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 6.28 MW to the national grid according to the prevailing system constraints. 2: Due to inadequate ventilation in the generator hall, the bearing temperatures of both generating units are approaching their maximum permissible operating limits at a load of 3 MW. Despite the improvement in hydrological conditions during the afternoon, further loading of the units could not be undertaken, as any increase in generation would result in bearing temperatures exceeding the allowable operating limits. Consequently, the available hydropower potential could not be fully utilized, leading to generation loss. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-06-30 | 2026 | 6 | 30 | Karora HPS | 11.8 | 11.29 | 7.72 | 185386 | 183081 | 10.82 | 6.28 | 65.46 | 7.78 | 98.87 | 0.69 | 280000 | 2178400 | 1424370.18 | 754029.82 | 2305 | 1. Unit No. 01 & 02 on bar, collectively delivering an average load of 7.72 MW according to the available hydrology. 2. All three lube oil pumps and both cooling water pumps are in operation to maintain the required temperatures and cooling water flow/ Pressure with in prescribed limits for both units. No standby pump is available, as all pumps are currently in service. 3 PTW No. 44/2026 was issued upon the request of the GRC representative for maintenance of the cooling water pumps, strainers, and lube oil heat exchanger. Accordingly, Unit No. 1 was shut down at 15:07 hrs, followed by Unit No. 2 at 15:11 hrs, to carry out the maintenance work under the issued PTW, resulting in the complete shutdown of the Power Complex. 4 Following the completion of maintenance work on the cooling water pumps, strainers, and lube oil heat exchanger, Unit No.2 and Unit No.1 were successfully started and synchronized with the National Grid at 20:38 hrs and 20:47 hrs, respectively. Subsequently, the load on each unit was gradually increased to 4 MW in accordance with the available hydrological conditions. | 11.8mwkarorahps@gmail.com | Original |  | Generation_Data.xlsx
2026-06-30 | 2026 | 6 | 30 | Koto HPS | 40.8 | 26.63 | 16.85 | 404500 | 401622 | 171.2 | 52.05 | 41.31 | 8.24 | 97.19 | 58 | 951666.67 | 7841733.33 | 3309365.28 | 4532368.05 | 2878 | Unit#01 and 02 on bar delivering average load 16.85. Unit#02 and 01 shutdown due to Intake Trash Racks cleaning at 08:50hrs and 08:54hrs while restarted after cleaning activity at 17:03hrs and 17:37hrs respectively. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-30 | 2026 | 6 | 30 | Machai HPS | 2.6 | 2.17 | 1.67 | 41076 | 40084 | 0 | 29 | 65.83 | 4.671 | 83 | 70 | 51792 | 241920.43 | 187232.36 | 54688.07 | 992 | Unit tripped due to line tripping from katlang grid because of tree falling on 11 kv machai line, after tree removal line was restored at 1933 while unit was synced at 2203. Unit tripped at 2124 due to line tripping from katlang grid line was restored at 2130 while unit was synced with system at 2136 | machai.12333@gmail.com | Original |  | Generation_Data.xlsx
2026-06-30 | 2026 | 6 | 30 | Malakand-3 HPS | 81 | 68 | 63.86 | 1532638 | 1518960 | 51 | 42.41 | 78.84 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 4348326.79 | 900910.77 | 13678 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-06-30 | 2026 | 6 | 30 | Pehur HPS | 18 | 6.87 | 6.6 | 158300 | 154000 | 16.35 | 19 | 36.64 | 3.767 | 29.55 | 41 | 127666.67 | 480920.33 | 580118 | -99197.67 | 4300 | Plant operational 24 hrs + irrigation valve open | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-06-30 | 2026 | 6 | 30 | Reshun HPS | 4.2 | 2.49 | 1.9 | 45000 | 44685 | 2.81 | 2.75 | 44.64 | 13.48 | 99.73 | 45 | 100531.2 | 1355160.58 | 602353.8 | 752806.78 | 315 | Nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-07-01 | 2026 | 7 | 1 | Daral Khwar HPS | 36.6 | 30.6 | 20.2 | 482350 | 482350 | 28.25 | 8.07 | 54.91 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 3988214.5 | 1879611.3 | 0 | 1: Units No. 02 and 03 were on bar delivering an average load equal to 20.2 MW according to the available hydrology and existing system constraints. 2: NOC for Emergency shutdown for rectification of Hotspot on yellow phase dropper clamp on main busbar at SWT-2 (Swat- Chakdara) Line. Issued to PESCO at 03:20 Hrs against their request for emergency maintenance on 132 KV Swat-Chakdara T/L. Unit No.03 and Unit No.2 were shutdown at 03:25Hrs and 03:26Hrs respectively under NOC-419/PEDO/RE(O&M)/DKHPC. 3: 132kV supply line restored at 05:31Hrs. 4: Unit No.03 and Unit No.02 were Synchronized with the National Grid at 05:56Hrs and 06:00Hrs respectively. 5: 132kV supply line failed again at 14:26Hrs and restored at 15:09Hrs. 6: Unit No.03 and Unit No.02 were Synchronized with the National Grid at 15:18Hrs and 15:39Hrs respectively. 7: 132kV supply line failed again at 16:28Hrs. Upon inquery from RCC they informed that there is fault in Chakdara Grid (CKD-10). The line restored at 20:03Hrs. 8: Unit No.03 and Unit No.02 were Synchronized with the National Grid at 20:12Hrs and 20:13Hrs respectively. 9: Unit No. 1 is retained out of service pending until procurement and installation of a replacement PT. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-01 | 2026 | 7 | 1 | Jabori HPS | 10.2 | 7.1 | 5.86 | 140600 | 138170 | 7.62 | 4.59 | 57.43 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 788840.16 | 590105.84 | 2430 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 5.86 MW according to available hydrology 2: Unit-01 tripped at 0125 hrs and 0911 hrs due to a Temperature Circuit Test Meter High Trip indication. The unit was resynchronized at 0936 hrs and 1013 hrs, respectively. During trip event, the Governor PLC cache memory was cleared. Additionally, Unit-02 tripped at 0114 hrs due to a mechanical trip and was resynchronized at 0130 hrs. 3: The 132 kV transmission line tripped at 1830 hrs and was restored at 2030 hrs. Following restoration of the transmission line, Unit-01 and Unit-02 were synchronized with the national grid at 2050 hrs and 2056 hrs, respectively.y and system conditions. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-07-01 | 2026 | 7 | 1 | Karora HPS | 11.8 | 10.85 | 7.07 | 169651 | 167042 | 11.29 | 5.58 | 59.91 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 1299586.76 | 861245.5 | 2609 | 1. Unit No. 01 & 02 on bar, collectively delivering an average load of 7.07 MW according to the available hydrology. 2. All three lube oil pumps and both cooling water pumps are in operation to maintain the required temperatures and cooling water flow/ Pressure with in prescribed limits for both units. No standby pump is available, as all pumps are currently in service. 3. At 14:08 hrs, The circuit breaker (E1Q1) of the 132 kV transmission line at the Dubair Khwar HPP side tripped due to adverse weather conditions. The RCC was informed accordingly and they instructed to wait until weather conditions improved. Upon restoration of normal weather conditions, RCC granted permission at 14:56 hrs to close the breaker, and the line was successfully energized at 14:57 hrs. Subsequently, Unit #01 and Unit #02 were synchronized with the system at 15:46 hrs and 16:21 hrs, respectively. 4. Unit No. 02 was safely shut down at 16:50 hrs due to a rapid reduction in net head and water inflow resulting from intake trash rack choking caused by heavy rainfall. The shutdown was carried out to ensure safe and reliable plant operation under the prevailing conditions. 5. At 18:30 hrs, a 132 kV transmission line supply failure occurred. Following the restoration of the supply at 20:44 hrs, Unit #01 was synchronized with the system at 21:19 hrs. The unit load was then gradually increased to 5.9 MW in accordance with the available water inflow. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-07-01 | 2026 | 7 | 1 | Koto HPS | 40.8 | 27.4 | 20.79 | 499000 | 493709 | 98.8 | 64.21 | 50.96 | 8.24 | 96 | 58 | 940000 | 7745600 | 4068162.16 | 3677437.84 | 5291 | DOD Comment: Both 132 kV transmission lines tripped at 16:35 hrs due to adverse weather conditions, resulting in the tripping of Unit #01 and Unit #02. The 132 kV supply was successfully restored at 17:35 hrs. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-01 | 2026 | 7 | 1 | Machai HPS | 2.6 | 2.16 | 1.38 | 33668 | 32868 | 11.15 | 29 | 53.96 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 153526.43 | 55203.99 | 800 | Unit tripped due to governor fault at 10:22 hours and 2147 hours while synced back with system at 10:33 and 2213. Unitript due to line tripping from Katlang Grid due to tree falling on 11 KV line at 16:30, after tree removal line was restored at 2047 while unit synced back at 21:10. Unit tripped due to 11 kv line tripping from Katlang Grid due to obstructions on 11 KV line due to storm at 2309 | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-07-01 | 2026 | 7 | 1 | Malakand-3 HPS | 81 | 66 | 57.27 | 1374372 | 1361690 | 51 | 41.42 | 70.7 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3898109.96 | 1350789 | 12682 | 132kV lines supply failed at 16:30Hrs and restored at 17:40Hrs, Unit 02, 03 & 01 synchronized with the system at 18:13, 18:15 & 18:17Hrs. Due to heavy rainfall in the catchment area of River Swat, the inflow is muddy with heavy trash accumulation at the Forebay, resulting in reduced load. However, as per the available hydrology from the Irrigation Department, all three units are currently on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-01 | 2026 | 7 | 1 | Pehur HPS | 18 | 7.84 | 5.79 | 139000 | 134000 | 21.22 | 14 | 32.18 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 504778 | 486793.61 | 5000 | Plant remained shut down for more than 3 hours due to tripping of 132 KV supply. After availability of 132 KV supply Unit 1 put on bar at 3.6 MW, while unit 3 off the bar due to high head restrictions. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-01 | 2026 | 7 | 1 | Reshun HPS | 4.2 | 2.65 | 1.75 | 41000 | 40649 | 2.6 | 2.51 | 40.67 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 547948.52 | 720249.88 | 351 | Nil. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-07-02 | 2026 | 7 | 2 | Daral Khwar HPS | 36.6 | 30.6 | 30.4 | 727060 | 727060 | 28.25 | 12.16 | 82.77 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 6011550.2 | -143724.39 | 0 | 1: Unit No. 02 and 03 were on bar delivering an average load equal to 30.4 MW according to available hydrology and existing system constraints. 2: Unit No. 01 is retained out of service until procurement and installation of replacement PT. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-02 | 2026 | 7 | 2 | Jabori HPS | 10.2 | 7.8 | 2.54 | 60929 | 59440 | 7.62 | 1.99 | 24.89 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 339354.85 | 1039591.15 | 1489 | 1: Unit 01 ans 02 were on the bar delivering an average load equals to 2.54 MW to the national grid according to the available hydrology and system conditions. 2: Upon the contractor's request, a Permit to Work (PTW) was issued, and the plant was shut down at 0910 Hrs. During the shutdown, the O&M staff, in coordination with the contractor's team, carried out the following maintenance activities: ○ Thorough cleaning of both surface air coolers. ○ Opening and cleaning of the lube oil heat exchanger. ○ Cleaning of both cooling water strainers. Upon successful completion of the maintenance activities, both generating units were synchronized with the national grid at 2350 Hrs. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-07-02 | 2026 | 7 | 2 | Karora HPS | 11.8 | 10.87 | 7.6 | 182348 | 179469 | 11.29 | 5.3 | 64.39 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 1396268.82 | 764563.44 | 2879 | Unit No. 01 & 02 on bar, collectively delivering an average load of 7.60 MW according to the available hydrology. All three lube oil pumps and both cooling water pumps are in operation to maintain the required temperatures and cooling water flow/ Pressure with in prescribed limits for both units. No standby pump is available, as all pumps are currently in service. At 16:13 hrs, the complex was shutdown for cleaning of intake trash rack. Following the completion of the intake trash rack cleaning, Unit #01 was synchronized with the grid at 17:03 hrs, followed by Unit #02 at 17:09 hrs. The unit loads were then gradually increased in accordance with the available hydrology. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-07-02 | 2026 | 7 | 2 | Koto HPS | 40.8 | 26.63 | 16.17 | 388000 | 387723 | 98.8 | 49.93 | 39.62 | 8.24 | 96 | 58 | 940000 | 7745600 | 3194837.52 | 4550762.48 | 277 | Unit 01 and 02 on bar and delivering power to the system, unit no 03 is standby due to cooling water strainer issue | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-02 | 2026 | 7 | 2 | Machai HPS | 2.6 | 2.08 | 0.25 | 4536 | 4356 | 11.15 | 29 | 7.27 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 20346.88 | 188383.54 | 180 | Unit was stand still from 01-07-2026 due to obstruction on 11 KV Katlang line. Line restored after removal of obstructions at 2143 while unit was synced with system at 2150 | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-07-02 | 2026 | 7 | 2 | Malakand-3 HPS | 81 | 66 | 59.91 | 1437902 | 1425390 | 51 | 40.37 | 73.97 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 4080463.95 | 1168435.01 | 12512 | As per available hydrology from irrigation department all the units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-02 | 2026 | 7 | 2 | Pehur HPS | 18 | 6.7 | 5.2 | 125800 | 121000 | 21.22 | 14 | 29.12 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 455807 | 535764.61 | 4800 | As per increase inTarbela reservoir level minimum operating head for u#02 is achived therefore, Unit#02 taken on bar at 1125 Hrs dt.03-07-2026. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-02 | 2026 | 7 | 2 | Reshun HPS | 4.2 | 2.38 | 1.42 | 33000 | 32685 | 2.2 | 2.02 | 32.74 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 440593.8 | 827604.6 | 315 | Outgoing feeder breaker remained off for 2.2hours and Mastuj Section remained off for off due to line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-07-03 | 2026 | 7 | 3 | Daral Khwar HPS | 36.6 | 30.6 | 30.8 | 736070 | 736070 | 28.25 | 12.31 | 83.8 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 6086047.58 | -218221.77 | 0 | 1: Unit No. 02 and 03 were on bar delivering an average load equal to 30.8 MW according to the available hydrology and existing system constraints. 2: Unit No. 01 is retained out of service pending until procurement and installation of a replacement PT. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-03 | 2026 | 7 | 3 | Jabori HPS | 10.2 | 9.2 | 6.07 | 145740 | 143550 | 7.62 | 4.76 | 59.53 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 819555.66 | 559390.34 | 2190 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 6.07 MW to the national grid according to the available hydrology and system conditions. 2: Both units experienced a total of seven mechanical trips due to inadequate cooling water pressure. Cooling Water Pump-02 is out of service as it is unable to develop the required flow and discharge pressure. Although Cooling Water Pump-01 is operational, its discharge pressure is insufficient to adequately supply cooling water to both units simultaneously. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-07-03 | 2026 | 7 | 3 | Karora HPS | 11.8 | 10.98 | 8.55 | 205207 | 202012 | 11.29 | 7.4 | 72.46 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 1571653.36 | 589178.9 | 3195 | Unit No. 01 & 02 on bar, collectively delivering an average load of 8.55 MW according to the available hydrology. All three lube oil pumps and both cooling water pumps are in operation to maintain the required temperatures and cooling water flow/ Pressure with in prescribed limits for both units. No standby pump is available, as all pumps are currently in service. At 22:15 hrs, PTW No. 45/2026 was issued to the contractor for the testing of both generating units. The PTW was cancelled at 23:00 hrs with the following remarks recorded by the contractor: "Unit #02 was started and stopped three times under FSNL conditions to verify its smooth operation. Unit #02 successfully executed all start and stop commands. However, Unit #01 remained untested." | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-07-03 | 2026 | 7 | 3 | Koto HPS | 40.8 | 27 | 26.47 | 636000 | 630136 | 98.8 | 76.65 | 64.95 | 8.24 | 96 | 58 | 940000 | 7745600 | 5192320.64 | 2553279.36 | 5864 | Unit #01 and Unit #02 are on bar , delivering an average load of 26.47 MW. Unit #03 is on standby due to TRCM and cooling water strainer issues.. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-03 | 2026 | 7 | 3 | Machai HPS | 2.6 | 2 | 1.76 | 44000 | 42812 | 29.6 | 30 | 70.51 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 199974.85 | 8755.56 | 1188 | Unit tripped at 0115 & 0950 hrs due to 11KV line tripping and Unit synchronised with the system at 0205 & 1001 hrs respectively. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-07-03 | 2026 | 7 | 3 | Malakand-3 HPS | 81 | 66 | 62.16 | 1491815 | 1479890 | 51 | 42.39 | 76.74 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 4236481.1 | 1012417.86 | 11925 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-03 | 2026 | 7 | 3 | Pehur HPS | 18 | 7.27 | 6.93 | 166500 | 161000 | 21.21 | 16 | 38.54 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 606487 | 385084.61 | 5500 | The plant remained operational throughout 24 hours as per available hydrology. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-03 | 2026 | 7 | 3 | Reshun HPS | 4.2 | 2.54 | 1.51 | 33000 | 32688 | 2.2 | 2.02 | 32.74 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 440634.24 | 827564.16 | 312 | outgoing feeder breaker tripped 6times due to line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-07-04 | 2026 | 7 | 4 | Daral Khwar HPS | 36.6 | 30.6 | 30.7 | 734680 | 734680 | 28.25 | 12.29 | 83.64 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 6074554.64 | -206728.84 | 0 | 1: Unit No. 02 and 03 were on bar delivering an average load equal to 30.7 MW according to the available hydrology and existing system constraints. 2: Unit No. 01 is retained out of service pending until procurement and installation of a replacement PT. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-04 | 2026 | 7 | 4 | Jabori HPS | 10.2 | 8.1 | 6.52 | 156362 | 154220 | 7.62 | 5.1 | 63.87 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 880472.82 | 498473.18 | 2142 | Plant was shutdown at 1245 hrs due to low cooling water pressure. After cleaning of both cooling water strainers, unit 01 and 02 were resynchronized at 1315 hrs. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-07-04 | 2026 | 7 | 4 | Karora HPS | 11.8 | 10.6 | 8.57 | 205629 | 202715 | 11.29 | 6.9 | 72.61 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 1577122.7 | 583709.56 | 2914 | Unit No. 01 & 02 on bar, collectively delivering an average load of 8.57 MW according to the available hydrology. All three lube oil pumps and both cooling water pumps are in operation to maintain the required temperatures and cooling water flow/ Pressure with in prescribed limits for both units. No standby pump is available, as all pumps are currently in service. At 11:25 hrs, PTW No. 46/2026 was issued to the contractor for the testing of both generating units. Unit #01 was stopped and started under FSNL conditions three times, and its operation was found to be normal during all test runs. Subsequently, Unit #01 was synchronized with the grid, loaded up to 3.0 MW, and then tripped to verify its operational performance. The unit responded satisfactorily, and no abnormalities were observed. For Unit #02, the load was gradually reduced from 5.9 MW to 3.0 MW, after which the unit was tripped to verify its operational performance. During the subsequent start-up sequence, the unit accelerated to 863 rpm. A stop command was immediately applied, following which the Governor PLC was reset. The start command was then executed again, and Unit #02 started successfully and operated smoothly. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-07-04 | 2026 | 7 | 4 | Koto HPS | 40.8 | 26.52 | 25.56 | 613250 | 609791 | 98.8 | 76.44 | 62.63 | 8.24 | 96 | 58 | 940000 | 7745600 | 5024677.84 | 2720922.16 | 3459 | Unit #01 and Unit #02 are on bar , delivering an average load of 25.56MW. Unit #03 is on standby due to TRCM and cooling water strainer issues | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-04 | 2026 | 7 | 4 | Machai HPS | 2.6 | 2.09 | 1.63 | 40620 | 39600 | 29.2 | 30 | 65.1 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 184971.6 | 23758.82 | 1020 | Unit tripped at 2245 hrs due to 11KV line tripping and Unit synchronised with the system at 2258 hrs. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-07-04 | 2026 | 7 | 4 | Malakand-3 HPS | 81 | 66 | 63.04 | 1513058 | 1500980 | 51 | 41.22 | 77.83 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 4296855.45 | 952043.52 | 12078 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-04 | 2026 | 7 | 4 | Pehur HPS | 18 | 7.65 | 6.31 | 151600 | 147000 | 21.21 | 15 | 35.09 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 553749 | 437822.61 | 4600 | At 2211 hrs Unit # 01 & 02 tripped on "loss voltage pro" due to isolation of gadoon grid from national grid. Unit # 02 & 01 again taken on bar at 2340 hrs and 2350 hrs respectivel | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-04 | 2026 | 7 | 4 | Reshun HPS | 4.2 | 2.58 | 1.48 | 35000 | 34685 | 2.28 | 2.08 | 34.72 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 467553.8 | 800644.6 | 315 | Outgoing feeder breaker remained off 3times due to line faults | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-07-05 | 2026 | 7 | 5 | Daral Khwar HPS | 36.6 | 30.6 | 30.6 | 731760 | 731760 | 28.25 | 12.24 | 83.31 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 6050411.21 | -182585.4 | 0 | 1: Unit No. 02 and 03 were on bar delivering an average load equal to 30.6 MW according to the available hydrology and existing system constraints. 2: Unit No. 01 is retained out of service pending until procurement and installation of a replacement PT. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-05 | 2026 | 7 | 5 | Jabori HPS | 10.2 | 7.5 | 5.48 | 259900 | 129950 | 7.62 | 4.3 | 106.17 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 741910.54 | 637035.46 | 129950 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 5.48 MW to the national grid according to the available hydrology and system conditions. 2: plant was shutdown at 1800 Hrs on the request of contractor to resolve the issues in SCADA, cooling water pump 01. PTW # 31/2026 issued to contractor in this regard. Plant was resynchronized at 2110 Hrs after completing these activities. | faizanbabar5@gmail.com | Original | Units = Net + Aux; Plant factor recalculated; CHECK: units > installed capacity x 24h (source me verify karein) | Generation_Data.xlsx
2026-07-05 | 2026 | 7 | 5 | Karora HPS | 11.8 | 9.05 | 7.82 | 187592 | 184646 | 11.29 | 6.28 | 66.24 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 1436545.88 | 724286.38 | 2946 | Unit No. 01 & 02 on bar, collectively delivering an average load of 7.82 MW according to the available hydrology. All three lube oil pumps and both cooling water pumps are in operation to maintain the required temperatures and cooling water flow/ Pressure with in prescribed limits for both units. No standby pump is available, as all pumps are currently in service. At 13:23 hrs, Unit #01 electrically tripped. Upon inspection, the F60 and F512 protection relays were found to have operated. Both relays were reset , and Unit was successfully synchronized with the system at 13:28 hrs. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-07-05 | 2026 | 7 | 5 | Koto HPS | 40.8 | 24.58 | 22.28 | 533250 | 529900 | 98.9 | 71.12 | 54.46 | 8.24 | 96 | 58 | 940000 | 7745600 | 4366376 | 3379224 | 3350 | Unit #01 and Unit #02 are on bar , delivering an average load of 22.28 MW. Unit #03 is on standby due to TRCM and cooling water strainer issues | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-05 | 2026 | 7 | 5 | Machai HPS | 2.6 | 1.95 | 1.82 | 42740 | 41756 | 29.6 | 30 | 68.49 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 195042.28 | 13688.14 | 984 | Unit tripped at 0205, 0658 & 1143 hrs due to 11KV line tripping and Unit synchronised with the system at 0235, 0736 & 1155 hrs respectively. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-07-05 | 2026 | 7 | 5 | Malakand-3 HPS | 81 | 66 | 62.3 | 1495193 | 1483460 | 51 | 41.22 | 76.91 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 4246700.94 | 1002198.03 | 11733 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-05 | 2026 | 7 | 5 | Pehur HPS | 18 | 6.5 | 5.93 | 142400 | 137000 | 21.21 | 14 | 32.96 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 516079 | 475492.61 | 5400 | At 1615 hrs Unit # 01 & 02 tripped on "loss voltage pro" due to isolation of gadoon grid from national grid. Unit # 01 & 02 again taken on bar at 1645 hrs and 1647 hrs respectively | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-05 | 2026 | 7 | 5 | Reshun HPS | 4.2 | 2.55 | 1.69 | 39000 | 38680 | 2.43 | 2.38 | 38.69 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 521406.4 | 746792 | 320 | outgoing feeder breaker remained off 2hours due to line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-07-06 | 2026 | 7 | 6 | Daral Khwar HPS | 36.6 | 30.6 | 28.3 | 677990 | 677990 | 28.25 | 11.34 | 77.18 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 5605824.72 | 262001.09 | 0 | 1: Units No. 02 and 03 were on bar delivering an average load equal to 28.3 MW according to the available hydrology and existing constraints. 2: 132KV supply line failed at 18:08 Hrs and restored at 19:16 Hrs, Unit No.03 and Unit No.02 synchronized with the national Grid at 19:25 Hrs and 19:30 Hrs respectively. 3: Unit No. 1 is retained out of service pending until procurement and installation of a replacement PT. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-06 | 2026 | 7 | 6 | Jabori HPS | 10.2 | 7.1 | 5.12 | 122908 | 120900 | 7.62 | 4.02 | 50.21 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 690242.28 | 688703.72 | 2008 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 5.12 MW to the national grid according to the available hydrology. 2: plant was shutdown at 2230 Hrs due heavy rainfall and muddy flood water in siren river | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-07-06 | 2026 | 7 | 6 | Karora HPS | 11.8 | 9.9 | 6.25 | 149958 | 147566 | 11.29 | 4.71 | 52.95 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 1148063.48 | 1012768.78 | 2392 | Unit No. 01 & 02 on bar, collectively delivering an average load of 6.25 MW according to the available hydrology. All three lube oil pumps and both cooling water pumps are in operation to maintain the required temperatures and cooling water flow/ Pressure with in prescribed limits for both units. No standby pump is available, as all pumps are currently in service. At 21:34 hrs, Unit #01 was de-synchronized from the system followed by Unit #02 at 21:35 hrs. A controlled shutdown of the Power Complex was subsequently carried out due to heavy rainfall resulting in excessive sediment-laden (muddy) river water. The shutdown was executed in accordance with the plant's operational procedures to safeguard the generating units and associated equipment from potential damage caused by high sediment concentration. The Power Complex shall remain under shutdown until river flow conditions stabilize and the sediment concentration returns to within permissible operating limits. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-07-06 | 2026 | 7 | 6 | Koto HPS | 40.8 | 26.17 | 18.25 | 437880 | 436620 | 98.8 | 56.34 | 44.72 | 8.24 | 96 | 58 | 940000 | 7745600 | 3597748.8 | 4147851.2 | 1260 | Units 1 and 2 remained on-bar, sustaining an average load of 18.25 MW, while Unit 3 was placed on standby due to the unavailability of the Trash Rack Cleaning Machine (TRCM). Total generation was temporarily reduced following a far-end system supply failure, which triggered the forced tripping of the Koto HPC generators for a duration of two hours, specifically from 17:53 hrs to 19:53 hrs. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-06 | 2026 | 7 | 6 | Machai HPS | 2.6 | 1.98 | 1.4 | 35936 | 34936 | 19 | 30 | 57.59 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 163186.06 | 45544.36 | 1000 | 1) Unit tripped at 1145hrs due to Earth fault, line restored at 1158hrs,while unit synched at 1202hrs, 2) Unit tripped at 1722hrs due to 11kv line tripped, because of stormy weather, and some wait for stable to line, 11kv line restored at 1905hrs, and unit synched at 1920hrs. 3) Unit tripped at 2115hrs due to 11kv line tripped because of issued PTW#706 in katlang grid, 11kv line restored at 2225hrs, while unit synched at 2233hrs | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-07-06 | 2026 | 7 | 6 | Malakand-3 HPS | 81 | 66 | 61.69 | 1480640 | 1468020 | 51 | 40.55 | 76.16 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 4202500.85 | 1046398.11 | 12620 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-06 | 2026 | 7 | 6 | Pehur HPS | 18 | 8.19 | 6.98 | 167500 | 164000 | 21.22 | 15 | 38.77 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 617788 | 373783.61 | 3500 | Plant operational 24 hrs. + valve open | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-06 | 2026 | 7 | 6 | Reshun HPS | 4.2 | 2.53 | 1.94 | 45000 | 44638 | 2.81 | 2.75 | 44.64 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 601720.24 | 666478.16 | 362 | NIl | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-07-07 | 2026 | 7 | 7 | Daral Khwar HPS | 36.6 | 30.6 | 30.4 | 727620 | 727620 | 28.25 | 12.17 | 82.83 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 6016180.45 | -148354.64 | 0 | 1: Unit. 02 and 03 were on bar delivering an average load equal to 30.4 MW according to the available hydrology and existing system constraints. 2: Unit No. 01 is retained out of service pending until procurement and installation of a replacement PT. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-07 | 2026 | 7 | 7 | Jabori HPS | 10.2 | 6.2 | 0.9 | 21566 | 20760 | 7.62 | 0.7 | 8.81 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 118522.99 | 1260423.01 | 806 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 0.9 MW to the national grid according to the available hydrology and prevailing system constraints. 2: The main trash rack became choked due to floodwater, resulting in a plant shutdown on dated 07-07-2026. After partial cleaning of the trash rack, the plant was synchronized with the grid at 2010 Hrs. During the shutdown, two PTWs were issued to the contractor for the following activities: PTW-33/2026: Checking the operation of the SF6 circuit breaker from the SCADA system. PTW-34/2026: Checking the functionality of the drainage pump. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-07-07 | 2026 | 7 | 7 | Karora HPS | 11.8 | 11.71 | 5.8 | 139115 | 137643 | 11.29 | 4.78 | 49.12 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 1070862.54 | 1089969.72 | 1472 | Unit No. 01 & 02 on bar, collectively delivering an average load of 5.80 MW according to the available hydrology. All three lube oil pumps and both cooling water pumps are in operation to maintain the required temperatures and cooling water flow/ Pressure with in prescribed limits for both units. No standby pump is available, as all pumps are currently in service. "At 09:30 hrs, the intake trash rack cleaning activity was commenced by the Weir Site team. Following the completion of the intake trash rack cleaning, Unit #01 was synchronized with the grid at 11:22 hrs, and its load was gradually increased to 5.0 MW. Subsequently, Unit #02 was synchronized with the grid at 11:26 hrs, and its load was gradually increased to 4.0 MW." | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-07-07 | 2026 | 7 | 7 | Koto HPS | 40.8 | 26.1 | 19.75 | 474073 | 472753 | 98.8 | 61 | 48.41 | 8.24 | 96 | 58 | 940000 | 7745600 | 3895484.72 | 3850115.28 | 1320 | Units 1 and 2 remained on-bar, sustaining an average load of 19.75 MW, while Unit 3 was placed on standby due to PLC related commissioning issues. unit 1and 2 have been shutdown for 1 hr (17:00 to 18:00)to facilitate the ongoing rescue operation at the intake site . | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-07 | 2026 | 7 | 7 | Machai HPS | 2.6 | 1.98 | 1.75 | 39816 | 38764 | 15 | 30 | 63.81 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 181066.64 | 27663.77 | 1052 | 01) Unit normally stopped at 0510hrs due to choking fault, while Unit synched at 0554hrs. 02) Unit tripped at 0622, 2044hrs due to 11kv line tripped, Earth fault, Line restored at 0629,2048hrs, while Unit synched at 0635,2054hrs 03) Unit emergency stopped at 0922hrs due to Governor Motor fault, while Unit synched at 1053hrs. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-07-07 | 2026 | 7 | 7 | Malakand-3 HPS | 81 | 66 | 61.08 | 1465971 | 1453360 | 51 | 40.61 | 75.41 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 4160533.67 | 1088365.3 | 12611 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-07 | 2026 | 7 | 7 | Pehur HPS | 18 | 8.1 | 7 | 167400 | 161000 | 21.22 | 16 | 38.75 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 606487 | 385084.61 | 6400 | Not reported | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-07 | 2026 | 7 | 7 | Reshun HPS | 4.2 | 2.49 | 1.92 | 44000 | 43665 | 2.8 | 2.69 | 43.65 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 588604.2 | 679594.2 | 335 | line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-07-08 | 2026 | 7 | 8 | Daral Khwar HPS | 36.6 | 30.6 | 29.6 | 708160 | 708160 | 28.25 | 11.84 | 80.62 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 5855279.33 | 12546.48 | 0 | 1: Units No. 02 and 03 were on bar delivering an average load equal to 29.6 MW according to the available hydrology and existing system constraints. 2: 132KV Supply line failed at 19:59Hrs and restored at 20:05Hrs, Units No.03 and 02 ware synchronized with the national Grid at 20:10Hrs and 20:14Hrs respectively. 3: Unit No. 1 is retained out of service pending until procurement and installation of a replacement PT. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-08 | 2026 | 7 | 8 | Jabori HPS | 10.2 | 8.5 | 3.09 | 74200 | 72820 | 7.62 | 2.42 | 30.31 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 415743.94 | 963202.06 | 1380 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 3.09 MW to the national grid according to the available hydrology. 2: plant was shutdown at 1915 Hrs due to heavy rainfall and flood situation in catchment area. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-07-08 | 2026 | 7 | 8 | Karora HPS | 11.8 | 11.14 | 7.64 | 183468 | 181059 | 11.29 | 6.25 | 64.78 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 1408639.02 | 752193.24 | 2409 | Unit No. 01 & 02 on bar, collectively delivering an average load of 7.64 MW according to the available hydrology. All three lube oil pumps and both cooling water pumps are in operation to maintain the required temperatures and cooling water flow/ Pressure with in prescribed limits for both units. No standby pump is available, as all pumps are currently in service. "At 20:12 hrs, the head dropped sharply due to severe choking of the intake trash rack following heavy rainfall. Consequently, Unit #02 was shut down in a controlled manner. Subsequently, Unit #01 was shut down in a controlled manner at 20:31 hrs, resulting in the complete shutdown of the Power Complex. The shutdown was executed in accordance with the plant's operational procedures due to excessive sediment-laden river water. The Power Complex shall remain under shutdown until river flow conditions stabilize and the sediment concentration returns to acceptable operating limits." | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-07-08 | 2026 | 7 | 8 | Koto HPS | 40.8 | 26.15 | 19.15 | 459572 | 458192 | 98.8 | 59.14 | 46.93 | 8.24 | 96 | 58 | 940000 | 7745600 | 3775502.08 | 3970097.92 | 1380 | Unit No. 01 and 02 were operated and delevring avrage power 19.15 MW to system ,while unit No .03 is standby due to PLC related commissioning issues. the plant was shutdown for trash rack cleaning from 9:25 am to 12:40 pm | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-08 | 2026 | 7 | 8 | Machai HPS | 2.6 | 2.03 | 1.74 | 40972 | 39864 | 15 | 28 | 65.66 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 186204.74 | 22525.67 | 1108 | Unit tripped at 0138, 0505 & 2145 hrs. due to 11 KV line tripping from Katlang grid; 11 KV line restored at 0201, 0517 & 2215, while unit synched at 0211, 0525 & 2237 hrs. respectively. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-07-08 | 2026 | 7 | 8 | Malakand-3 HPS | 81 | 64 | 61.04 | 1465037 | 1453120 | 51 | 40.47 | 75.36 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 4159846.62 | 1089052.34 | 11917 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-08 | 2026 | 7 | 8 | Pehur HPS | 18 | 8.71 | 7.71 | 185100 | 179000 | 21.22 | 17 | 42.85 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 674293 | 317278.61 | 6100 | Plant operational 24 hrs | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-08 | 2026 | 7 | 8 | Reshun HPS | 4.2 | 2.52 | 1.78 | 40000 | 39675 | 2.51 | 2.44 | 39.68 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 534819 | 733379.4 | 325 | line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-07-09 | 2026 | 7 | 9 | Daral Khwar HPS | 36.6 | 30.6 | 29.6 | 707640 | 707640 | 28.25 | 11.83 | 80.56 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 5850979.81 | 16845.99 | 0 | 1: Units No. 02 and 03 were on bar delivering an average load equal to 29.6 MW according to the available hydrology and existing system constraints. 2: Unit No. 3 tripped at 1256 Hrs due to an RTD (Cooled Air from Air Cooler TEMP 2) malfunctioned. The unit synchronized at 1307 Hrs. 3: Unit No. 1 is retained out of service pending until procurement and installation of a replacement PT. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-09 | 2026 | 7 | 9 | Jabori HPS | 10.2 | 8.5 | 1.28 | 30712 | 29680 | 7.62 | 1 | 12.55 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 169449.06 | 1209496.94 | 1032 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 1.28 MW to the national grid according to the available hydrology and prevailing system constraints. 2: Flushing of the sand trap was carried out to remove accumulated silt after the floodwater level receded. Subsequently, Unit-01 was synchronized. Cooling Water Pump-02 is out of service as it is unable to develop the required flow and discharge pressure. Although Cooling Water Pump-01 is operational, its discharge pressure is insufficient to adequately supply cooling water to both units simultaneously. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-07-09 | 2026 | 7 | 9 | Karora HPS | 11.8 | 9.52 | 2.45 | 58815 | 58161 | 11.29 | 2.19 | 20.77 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 452492.58 | 1708339.68 | 654 | 1. Unit No. 01 & 02 on bar, collectively delivering an average load of 2.45 MW according to the available hydrology. 2. All three lube oil pumps and both cooling water pumps are in operation to maintain the required temperatures and cooling water flow/ Pressure within prescribed limits for both units. No standby pump is available, as of all the pumps are currently in service. 3 "Powerhouse was completely shutdown since 20:31 hrs, 08-07-2026 due to severe choking of trash racks at intake site following heavy rain & medium-level flood. " 4. Cleaning of intake trash rack, both cooling water pumps and strainers been carried out by the O&M team. 5. After cleaning activities, Unit No. 01 was smoothly synchronized with the grid at 16:46 hrs. 6. Unit No. 02 was synchronized with the grid at 18:43 hrs after rectification of its governor system. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-07-09 | 2026 | 7 | 9 | Koto HPS | 40.8 | 25.52 | 20.24 | 485823 | 484403 | 98.8 | 62.51 | 49.61 | 8.24 | 96 | 58 | 940000 | 7745600 | 3991480.72 | 3754119.28 | 1420 | Units No.1 and 2 remained operational, while Unit No.3 was kept on standby due to PLC-related starting issue. Overall station generation and average load remained low, constrained by reduced hydrological inflow. The non-availability of TRCM and non-functional cooling water strainers are prevailing issues. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-09 | 2026 | 7 | 9 | Machai HPS | 2.6 | 2.08 | 1.74 | 42744 | 41620 | 15 | 28 | 68.5 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 194407.02 | 14323.4 | 1124 | Smooth operation as per available hydrology. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-07-09 | 2026 | 7 | 9 | Malakand-3 HPS | 81 | 65 | 61.11 | 1466712 | 1454070 | 51 | 40.57 | 75.45 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 4162566.19 | 1086332.78 | 12642 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-09 | 2026 | 7 | 9 | Pehur HPS | 18 | 8.78 | 7.53 | 180700 | 175000 | 21.22 | 16 | 41.83 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 659225 | 332346.61 | 5700 | Plant remained operational throughout 24 hrs as per available hydrology and irrigation valve open. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-09 | 2026 | 7 | 9 | Reshun HPS | 4.2 | 2.42 | 1.96 | 46000 | 45670 | 2.89 | 2.81 | 45.63 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 615631.6 | 652566.8 | 330 | nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-07-10 | 2026 | 7 | 10 | Daral Khwar HPS | 36.6 | 30.6 | 29.8 | 712760 | 712760 | 28.25 | 11.92 | 81.14 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 5893313.51 | -25487.7 | 0 | 1: Unit No. 02 and 03 were on bar delivering an average load equal to 29.8 MW according to the available hydrology and existing system constraints. 2. Unit No. 01 is retained out of service pending until procurement and installation of a replacement PT. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-10 | 2026 | 7 | 10 | Jabori HPS | 10.2 | 5.1 | 4.92 | 118010 | 116400 | 7.62 | 3.86 | 48.21 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 664550.88 | 714395.12 | 1610 | 1: Unit 01 was on the bar delivering an average load equals to 4.92 MW to the national grid according to the available hydrology and prevailing system constraints. 2: Cooling Water Pump-02 is out of service as it is unable to develop the required flow and discharge pressure. Although Cooling Water Pump-01 is operational, its discharge pressure is insufficient to adequately supply cooling water to both units simultaneously. Therefore only one unit is operating at full load | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-07-10 | 2026 | 7 | 10 | Karora HPS | 11.8 | 9.06 | 7.27 | 174422 | 171307 | 11.29 | 5.78 | 61.59 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 1332768.46 | 828063.8 | 3115 | 1. Unit No. 01 & 02 on bar, collectively delivering an average load of 7.27 MW according to the available hydrology. 2. All three lube oil pumps and two cooling water pumps are in operation to maintain the units' temperatures and cooling water flow/pressure within the prescribed limits for both units. No standby pump is available, as all of the pumps are currently in service. 3 Unit No. 01 electrically tripped at 18:19 hrs, following the operation of generator protection relays. The unit was resynced with the National Grid at 18:27 hrs. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-07-10 | 2026 | 7 | 10 | Koto HPS | 40.8 | 22.45 | 18.03 | 432814 | 431374 | 98.8 | 55.69 | 44.2 | 8.24 | 96 | 58 | 940000 | 7745600 | 3554521.76 | 4191078.24 | 1440 | Historical daily hydrology for the month of July averages 98.80 cumecs; however, the actual average hydrology recorded on July 10, 2026, was 55.69 cumecs. Consequently, the average load of the plant was limited to 18.03 MW. Units 1 and 2 were operated for power generation, while Unit 3 remained on standby due to the existing low hydrology and an ongoing PLC-related starting issue. Furthermore, Unit 2 was shut down for a period of 2 hours and 15 minutes to facilitate the manual cleaning of trashes from the intake trash racks, a task intensified by the current non-availability of the TRCM. Non-functional cooling water strainers is also another prevailing issue. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-10 | 2026 | 7 | 10 | Machai HPS | 2.6 | 1.91 | 1.48 | 39008 | 37976 | 15 | 27 | 62.51 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 177385.9 | 31344.52 | 1032 | (1) - Unit tripped at 0345 hrs. with line tripping. 11 KV line restored at 0357 hrs., while unit resynched at 0406 hrs. (2) - Unit stopped at 2307 hrs. for flushing and remained still, till 0020 hrs., next day. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-07-10 | 2026 | 7 | 10 | Malakand-3 HPS | 81 | 64 | 60.39 | 1449304 | 1436780 | 51 | 40.51 | 74.55 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 4113070.11 | 1135828.86 | 12524 | Due to heavy rainfall and thunder storm in the catchment area of River Swat, the inflow is muddy with heavy trash accumulation at the Forebay, resulting in reduced load. However, the inflow was reduced by the irrigation department and as per the available hydrology, all three units are currently on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-10 | 2026 | 7 | 10 | Pehur HPS | 18 | 8.92 | 7.62 | 183000 | 178000 | 21.22 | 16 | 42.36 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 670526 | 321045.61 | 5000 | Plant remained operational throughout 24 hrs + irrigation valve open. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-10 | 2026 | 7 | 10 | Reshun HPS | 4.2 | 2.66 | 2.07 | 46000 | 45684 | 2.9 | 2.81 | 45.63 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 615820.32 | 652378.08 | 316 | nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-07-11 | 2026 | 7 | 11 | Daral Khwar HPS | 36.6 | 36.6 | 30.9 | 741460 | 738630 | 28.25 | 12.35 | 84.41 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 6107214.43 | -239388.62 | 2830 | 1: Unit No. 01, 02 and 03 were on bar delivering an average load equal to 30.9 MW according to the available hydrology and existing system constraints. 2: Unit No. 01 put on bar at 00:40 Hrs after replacement damaged PT with new set. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-11 | 2026 | 7 | 11 | Jabori HPS | 10.2 | 7.5 | 3.37 | 80777 | 79440 | 8.69 | 2.64 | 33 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 453538.85 | 925407.15 | 1337 | 1: Unit 01 was on the bar delivering an average load equals to 3.37 MW to the national grid according to the available hydrology and prevailing system constraints. 2: The plant was shut down at 1025 Hrs due to extremely muddy water and choking of the main trash rack. The trash rack was partially cleaned; however, complete cleaning was not possible due to the high water flow. During the shutdown, the generator surface air cooler of Unit 01 was opened and cleaned. Unit 02 and Unit 01 were synchronized at 1834 Hrs and 1841 Hrs, respectively. However, at 2000 Hrs, the available head dropped, and Unit 01 was shut down. 3: Cooling Water Pump-02 is out of service as it is unable to develop the required flow and pressure. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-07-11 | 2026 | 7 | 11 | Karora HPS | 11.8 | 8.35 | 6.08 | 145807 | 143218 | 11.29 | 4.64 | 51.49 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 1114236.04 | 1046596.22 | 2589 | 1. Unit No. 01 & 02 on bar, collectively delivering an average load of 6.08 MW according to the available hydrology. 2. All three lube oil pumps and two cooling water pumps are in operation to maintain the units' temperatures and cooling water flow/pressure within the prescribed limits for both units. No standby pump is available, as all of the pumps are currently in service. 3. The Powerplant electrically tripped at 19:51 hrs, 21:20 hrs & 21:59 hrs following the de-energization of 132kV line due to fault at Allai Khwar which was finally energized at 22:24 hrs but plant remained shutdown to monitor quality of hydrology at intake site. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-07-11 | 2026 | 7 | 11 | Koto HPS | 40.8 | 25.52 | 22.35 | 536412 | 535092 | 98.8 | 69.02 | 54.78 | 8.24 | 96 | 58 | 940000 | 7745600 | 4409158.08 | 3336441.92 | 1320 | The actual daily inflow was recorded at 69.02 cumecs, significantly below the historical average of 98.80 cumecs. Due to this low hydrology, only Units 1 and 2 were operated at an average load of 22.35 MW, with a maximum capacity of 25.52 MW. Unit 3 remained on standby because of the water deficit and an unresolved starting issue. In addition to these unit constraints, the intake Trash Rack Cleaning Machine (TRCM) is not yet operational, and issues with the powerhouse cooling water strainers also persist. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-11 | 2026 | 7 | 11 | Machai HPS | 2.6 | 1.89 | 1.24 | 31248 | 30404 | 15 | 27 | 50.08 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 142017.08 | 66713.33 | 844 | (1) - Unit remained on load low load due to maintenance of spillway inlet gate. (2) - Unit tripped at 0200 & 2305 hrs. due to 11 KV line tripping; 11 KV line restored at 0215 & 2338 hrs., while unit synched at 0233 & (0006, next day) hrs. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-07-11 | 2026 | 7 | 11 | Malakand-3 HPS | 81 | 64 | 59.79 | 1434879 | 1423410 | 51 | 40.13 | 73.81 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 4074795.81 | 1174103.16 | 11469 | Due to heavy rainfall and thunder storm in the catchment area of River Swat, the inflow is muddy with heavy trash accumulation at the Forebay, resulting in reduced load. However, the inflow was reduced by the irrigation department and as per the available hydrology, all three units are currently on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-11 | 2026 | 7 | 11 | Pehur HPS | 18 | 9.68 | 4.27 | 102500 | 98000 | 21.22 | 8 | 23.73 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 369166 | 622405.61 | 4500 | Unit # 01 and 02 made stop at 1120 Hrs and 1125 hrs, respectively, due to nil irrigation demand because of heavy rainfall at downstream | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-11 | 2026 | 7 | 11 | Reshun HPS | 4.2 | 2.52 | 1.91 | 46000 | 45655 | 2.9 | 2.81 | 45.63 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 615429.4 | 652769 | 345 | nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-07-12 | 2026 | 7 | 12 | Daral Khwar HPS | 36.6 | 36.6 | 34.3 | 823900 | 820920 | 28.25 | 13.73 | 93.8 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 6787612.84 | -919787.03 | 2980 | 1: Unit No 01, 02 and 03 were on bar delivering an average load equal to 34.3 MW according to the available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-12 | 2026 | 7 | 12 | Jabori HPS | 10.2 | 6.6 | 5.24 | 125749 | 124080 | 8.69 | 4.11 | 51.37 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 708397.54 | 670548.47 | 1669 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 5.24 MW to the national grid according to the available hydrology and prevailing system constraints. 2: At 1215 Hrs, the O&M team moved to the weir site for cleaning of the main trash rack. However, only partial cleaning could be carried out due to the high water flow. Following the partial cleaning of the trash rack, Unit 02 was synchronized at 1833 Hrs. 3: Cooling Water Pump-02 is out of service as it is unable to develop the required flow and pressure. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-07-12 | 2026 | 7 | 12 | Karora HPS | 11.8 | 5.9 | 3.48 | 83414 | 81352 | 11.29 | 2.82 | 29.45 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 632918.56 | 1527913.7 | 2062 | 1. Unit No. 01 is on bar delivering an average load of 3.48 MW according to the available inflow. 2. Unit #01 lube oil pump, standby lube oil pump and both cooling water pumps are in operation to maintain the units' temperatures and cooling water flow/pressure within the prescribed limits for Unit No.1. No standby pump is available, as all of the pumps are currently in service. 3. Following the normalization of weather and water condition at the intake site, Unit #01 was synchronized with the system at 00:34 hrs, while Unit #02 remained at standstill due to intake trash rack choking. 4 Unit No. 01 was safely shut down at 4:05 hrs due to a rapid reduction in net head and water inflow caused by intake trash rack choking resulting from muddy water. The shutdown was carried out to ensure safe and reliable plant operation under the prevailing conditions. Following the improvement in river water condition, Unit #01 was restarted and synchronized with the system at 09:02 hrs. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-07-12 | 2026 | 7 | 12 | Koto HPS | 40.8 | 26.27 | 20.54 | 492934 | 491814 | 98.8 | 63.43 | 50.34 | 8.24 | 96 | 58 | 940000 | 7745600 | 4052547.36 | 3693052.64 | 1120 | The actual daily inflow was recorded at 63.43 cumecs, significantly below the historical average of 98.80 cumecs. Due to the low hydrology, only Units 1 and 2 were operated at an average load of 20.54 MW, with a maximum capacity of 26.27 MW. Unit 3 remained on standby because of the water deficit and an unresolved starting issue. In addition, the Intake Trash Rack Cleaning Machine (TRCM) is not yet operational, and issues with the powerhouse cooling water strainers also persist. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-12 | 2026 | 7 | 12 | Machai HPS | 2.6 | 2.02 | 1.54 | 38960 | 38152 | 16 | 26 | 62.44 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 178207.99 | 30522.42 | 808 | Unit tripped at 1000, 1133, 1230 and 1244 hrs. due to 11 KV line tripping; 11 KV line restored at 1002, 1134, 1232 and 1255 hrs., while unit synched at 1004, 1135, 1237 and 1307 hrs. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-07-12 | 2026 | 7 | 12 | Malakand-3 HPS | 81 | 65 | 60.57 | 1453593 | 1442490 | 51 | 40.58 | 74.77 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 4129416.12 | 1119482.84 | 11103 | Due to heavy rainfall and thunder storm in the catchment area of River Swat, the inflow is muddy with heavy trash accumulation at the Forebay, resulting in reduced load. However, the inflow was reduced by the irrigation department and as per the available hydrology, all three units are currently on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-12 | 2026 | 7 | 12 | Pehur HPS | 18 | 0 | 0 | 0 | 0 | 21.22 | 0 | 0 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 0 | 991571.61 | 0 | Plant shut down 24 hrs because of nil irrigation demand. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-12 | 2026 | 7 | 12 | Reshun HPS | 4.2 | 2.42 | 1.8 | 41000 | 40690 | 2.6 | 2.51 | 40.67 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 548501.2 | 719697.2 | 310 | Line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-07-13 | 2026 | 7 | 13 | Daral Khwar HPS | 36.6 | 36.6 | 35.6 | 854090 | 851110 | 28.25 | 14.23 | 97.23 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 7037232.81 | -1169407.01 | 2980 | 1: Unit No. 01, 02 and 03 were on bar delivering an average load equal to 35.6 MW according to the available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-13 | 2026 | 7 | 13 | Jabori HPS | 10.2 | 5.3 | 3.71 | 89064 | 87950 | 8.69 | 2.91 | 36.38 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 502124.14 | 876821.86 | 1114 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 3.71 MW to the national grid according to the available hydrology and prevailing system constraints. 2: The plant was shut down at 1641 Hrs due to heavy rainfall and extremely muddy inflow from the catchment area, making plant operation unsafe. 3: Cooling Water Pump-02 is out of service as it is unable to develop the required flow and pressure. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-07-13 | 2026 | 7 | 13 | Karora HPS | 11.8 | 9.92 | 5.33 | 127809 | 125300 | 11.29 | 3.97 | 45.13 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 974834 | 1185998.26 | 2509 | 1. Units No.1 and 02 are on bar collectively delivering an average load of 5.33 MW according to the available inflow. 2. All three lube oil pumps and both cooling water pumps are in operation to maintain the units' temperatures and cooling water flow/pressure within the prescribed limits for both units. No standby pump is available, as all of the pumps are currently in service. 3. The Plant was completely shut down for the cleaning of the intake trash rack at 09:47 hrs. After the completion of the cleaning, Unit # 01 was started and synchronized with the system at 12:45 hrs, and the load gradually increased to 5.9 MW. Similarly, unit 02 was synchronized with the grid at 13:17 hrs, and the load was gradually increased to 4 MW as per the available hydrology 4. At 19:40hrs. Unit 01 was mechanically tripped due to the malfunction of the shaft seal cooling water pressure transmitter. Following the inspection and rectification of the fault, the unit was restarted and synchronized with the system at 20:11 hrs. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-07-13 | 2026 | 7 | 13 | Koto HPS | 40.8 | 26.55 | 19.42 | 466056 | 464876 | 98.8 | 59.97 | 47.6 | 8.24 | 96 | 58 | 940000 | 7745600 | 3830578.24 | 3915021.76 | 1180 | 1) The actual daily inflow was recorded at 59.97 cumecs, significantly below the historical average of 98.80 cumecs. Due to the low hydrology, only Units 1 and 2 were operated at an average load of 19.42 MW, with a maximum capacity of 26.55 MW. Unit 3 remained on standby because of the water deficit and an unresolved starting issue. In addition, the Intake Trash Rack Cleaning Machine (TRCM) is not yet operational, and issues with the powerhouse cooling water strainers also persist. 2)Unit#02 shutdown for Intake Trash Racks cleaning at 09:55Hrs and restarted at 11:29Hrs after cleaning activity. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-13 | 2026 | 7 | 13 | Machai HPS | 2.6 | 1.91 | 1.71 | 41428 | 40168 | 16 | 26 | 66.39 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 187624.73 | 21105.69 | 1260 | Unit remained on bar delivering power to National Grid as per available inflow and system conditions. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-07-13 | 2026 | 7 | 13 | Malakand-3 HPS | 81 | 64 | 61.01 | 1464291 | 1452120 | 51 | 41.95 | 75.32 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 4156983.92 | 1091915.04 | 12171 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-13 | 2026 | 7 | 13 | Pehur HPS | 18 | 5.77 | 2.95 | 70800 | 61000 | 21.22 | 5.5 | 16.39 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 229787 | 761784.61 | 9800 | Plant shut down due to nil irrigation demand. At 1230 Hrs only Unit # 1 started with 5.5 MW load. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-13 | 2026 | 7 | 13 | Reshun HPS | 4.2 | 2.52 | 1.82 | 41000 | 40645 | 2.6 | 2.51 | 40.67 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 547894.6 | 720303.8 | 355 | nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-07-14 | 2026 | 7 | 14 | Daral Khwar HPS | 36.6 | 36.6 | 32.5 | 779270 | 776300 | 28.25 | 12.98 | 88.71 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 6418681.29 | -550855.48 | 2970 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 32.5 MW according to the available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-14 | 2026 | 7 | 14 | Jabori HPS | 10.2 | 8.5 | 3.32 | 79718 | 78240 | 8.69 | 2.61 | 32.56 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 446687.81 | 932258.19 | 1478 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 3.32 MW to the national grid according to the available hydrology and prevailing system constraints. 2: The main trash rack was heavily choked following last night's heavy rainfall. At 0700 Hrs, the O&M team moved to the weir site to clean the trash rack. After partial cleaning, Unit 01 was synchronized at 1004 Hrs. Upon completion of the trash rack cleaning, Unit 02 was synchronized at 1428 Hrs. 3: Cleaning of the trash rack is extremely difficult during the monsoon season due to heavy water flow, resulting in prolonged cleaning time and delays the restoration of normal plant operation. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-07-14 | 2026 | 7 | 14 | Karora HPS | 11.8 | 8.01 | 7.7 | 184780 | 181658 | 11.29 | 6.09 | 65.25 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 1413299.24 | 747533.02 | 3122 | 1. Unit No. 01 and 02 are on bar, collectively delivering an average load of 7.70 MW according to the available inflow. 2. All three lube oil pump and both cooling water pumps are in operation to maintain the units' temperatures and cooling water flow/pressure within the prescribed limits for both units. No standby pump is available, as all of the pumps are currently in service. 3 Energy generation remained below the target due to low hydrology and the requirement to maintain the prescribed environmental flow in the river. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-07-14 | 2026 | 7 | 14 | Koto HPS | 40.8 | 26.35 | 19.76 | 474227 | 472927 | 98.8 | 61.02 | 48.43 | 8.24 | 96 | 58 | 940000 | 7745600 | 3896918.48 | 3848681.52 | 1300 | 1) The actual daily inflow was recorded at 61.02 cumecs, significantly below the historical average of 98.80 cumecs. Due to the low hydrology, only Units 1 and 2 were operated at an average load of 19.76 MW, with a maximum capacity of 26.35 MW. Unit 3 remained on standby because of the water deficit and an unresolved starting issue. In addition, the Intake Trash Rack Cleaning Machine (TRCM) is not yet operational, and issues with the powerhouse cooling water strainers also persist. 2)Plant was shut down at 09:40 hrs for Intake Trash Racks cleaning. After completion of the cleaning, Unit #02 was restarted and synchronized with the grid at 11:49 hrs. The startup of Unit #01 was delayed due to two shear pins being broken. After rectification of the broken shear pins, Unit #01 was successfully started and synchronized with the grid at 16:16 hrs. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-14 | 2026 | 7 | 14 | Machai HPS | 2.6 | 1.89 | 1.6 | 38856 | 37796 | 16 | 26 | 62.27 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 176545.12 | 32185.3 | 1060 | Unit tripped at 1145,1159,1227 & 1334 hrs. due to 11 KV line tripping; 11 KV line restored at 1146,1204,1242 &1439 hrs., while unit synched at 1151,1210,1249&1446 hrs. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-07-14 | 2026 | 7 | 14 | Malakand-3 HPS | 81 | 63 | 59.66 | 1431730 | 1418990 | 51 | 40.51 | 73.65 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 4062142.67 | 1186756.3 | 12740 | As per available hydrology from the Irrigation Department all the three Units are on bar. Load variation is due to fluctuations in the hydrology of River Swat, due to weather condition. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-14 | 2026 | 7 | 14 | Pehur HPS | 18 | 8.7 | 7.2 | 173000 | 167000 | 21.22 | 14 | 40.05 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 629089 | 362482.61 | 6000 | As per increase in irrigation demand unit #02 taken on bar at 1140 Hrs dt. 14-07-2016 with 4.3mw load instructed by SDO irrigation. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-14 | 2026 | 7 | 14 | Reshun HPS | 4.2 | 2.55 | 1.8 | 42000 | 42640 | 2.57 | 2.65 | 41.67 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 574787.2 | 693411.2 | 640 | Line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor; CHECK: Net > Units (source me verify karein) | Generation_Data.xlsx
2026-07-15 | 2026 | 7 | 15 | Daral Khwar HPS | 36.6 | 32.8 | 29.7 | 712760 | 709780 | 28.25 | 11.87 | 81.14 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 5868673.97 | -848.17 | 2980 | Unit No 01, 02 and 03 were on bar delivering an average load equal to 29.7 MW according to the available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-15 | 2026 | 7 | 15 | Jabori HPS | 10.2 | 8.4 | 6.08 | 145802 | 143760 | 8.69 | 4.76 | 59.56 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 820754.59 | 558191.41 | 2042 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 6.08 MW to the national grid according to the available hydrology and prevailing system constraints. 2: The plant was shut down at 1040 Hrs for cleaning of both cooling water strainers. Following completion of the cleaning, Unit 02 and Unit 01 were synchronized at 1152 Hrs and 1340 Hrs, respectively. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-07-15 | 2026 | 7 | 15 | Karora HPS | 11.8 | 7.7 | 6.49 | 155641 | 152764 | 11.29 | 6.5 | 54.96 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 1188503.92 | 972328.34 | 2877 | 1. Unit No. 02 is on bar, delivering an average load of 6.49 MW according to the available inflow. 2 Unit No.2 Lube oil pump, standby lube oil pump and both cooling water pumps are in operation to maintain the units' temperatures and cooling water flow/pressure within the prescribed limits for both units .No standby pump is available, as all of the pumps are currently in service. 3 At 13:53 hrs, Unit No. 01 was electrically tripped due to negative sequence protection operation. After resetting the protection alarms, Unit No. 01 was resynchronized with the grid at 13:55 hrs. 4 Muddy river water caused choking of the intake trash rack, resulting in an abrupt reduction in the available inflow and net head. Consequently, Unit No. 02 was shut down at 14:32 hrs due to intake trash rack choking. 5 Unit No. 01 was mechanically tripped at 17:06 hrs, 18:43 hrs, and 21:13 hrs. Following inspection and preliminary root cause analysis of tripping, the unit was resynchronized with the grid at 17:22 hrs and 18:55 hrs. Due to the repeated mechanical tripping of Unit No. 01, Unit No. 02 was started and synchronized with the grid at 21:49 hrs to maintain generation. TR No. 62/2026 was issued to investigate the repeated mechanical tripping of Unit No. 01 | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-07-15 | 2026 | 7 | 15 | Koto HPS | 40.8 | 26.9 | 21.6 | 518488 | 515878 | 98.8 | 66.63 | 52.95 | 8.24 | 96 | 58 | 940000 | 7745600 | 4250834.72 | 3494765.28 | 2610 | No data submitted for this date | rekotohpc@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-07-15 | 2026 | 7 | 15 | Machai HPS | 2.6 | 1.92 | 1.68 | 40524 | 39424 | 18 | 26 | 64.94 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 184149.5 | 24580.91 | 1100 | Unit tripped at 0550&1105 hrs. due to 11 KV line tripping; 11 KV line restored at 0552&1116 hrs., while unit synched at 0645&1123 hrs. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-07-15 | 2026 | 7 | 15 | Malakand-3 HPS | 81 | 60 | 57.18 | 1372413 | 1359250 | 51 | 39.23 | 70.6 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3891124.98 | 1357773.99 | 13163 | As per available hydrology from the Irrigation Department all the three Units are on bar. Load variation is due to fluctuations in the hydrology of River Swat. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-15 | 2026 | 7 | 15 | Pehur HPS | 18 | 9.73 | 8.7 | 209000 | 203000 | 21.22 | 16 | 48.38 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 764701 | 226870.61 | 6000 | Plant remained operational throughout 24 hrs as per available hydrology | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-15 | 2026 | 7 | 15 | Reshun HPS | 4.2 | 2.68 | 1.92 | 42000 | 41490 | 2.65 | 2.57 | 41.67 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 559285.2 | 708913.2 | 510 | outgoing feeder breaker tripped 7times due to line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-07-16 | 2026 | 7 | 16 | Daral Khwar HPS | 36.6 | 29.3 | 27.8 | 665330 | 665330 | 28.25 | 11.13 | 75.74 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 5501148.04 | 366677.77 | 0 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 27.8 MW according to the available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-16 | 2026 | 7 | 16 | Jabori HPS | 10.2 | 7.5 | 6.98 | 167490 | 165840 | 8.69 | 5.47 | 68.42 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 946813.73 | 432132.27 | 1650 | 1: Unit 01 and 02 were on the bar delivering an average load equals to 6.98 MW to the national grid according to the available hydrology and prevailing system constraints. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-07-16 | 2026 | 7 | 16 | Karora HPS | 11.8 | 7.88 | 5.46 | 131158 | 128467 | 11.29 | 4.37 | 46.31 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 999473.26 | 1161359 | 2691 | 1. Unit No.1 and 02 are on bar, collectively delivering an average load of 5.46 MW according to the available inflow. 2 All three Lube oil pumps and both cooling water pumps are in operation to maintain the units' temperatures and cooling water flow/pressure within the prescribed limits for both units. No standby pump is available, as all of the pumps are currently in service. 3 The Plant was completely shut down for the cleaning of Intake trash rack at 09:42 hrs. After completion of the cleaning, Unit # 02 was started and synchronized with system at 12:07 hrs and load gradually increased to 3 MW, similarly unit 01 was synchronized with grid at12:25 hrs and load was gradually increased to 5.9 MW as per available hydrology 4 At 12:28 hrs, the low-voltage side circuit breakers (K1Q1 and K2Q1) of both main transformers tripped, resulting in the shutdown of both units. After resetting the associated protection relay alarms, K1Q1 was closed at 12:33 hrs, and Unit #01 was synchronized with the system at 12:53 hrs. Subsequently, K2Q1 was closed, and Unit #02 was synchronized with the system at 13:31 hrs. 5 Energy generation remained below the target due to low hydrology and the requirement to maintain the prescribed environmental flow in the river. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-07-16 | 2026 | 7 | 16 | Koto HPS | 40.8 | 26.52 | 23.26 | 562750 | 558830 | 98.8 | 72.24 | 57.47 | 8.24 | 96 | 58 | 940000 | 7745600 | 4604759.2 | 3140840.8 | 3920 | Unit #01 and Unit #02 are on bar , delivering an average load of 23.26MW. Unit #03 is on standby due to starting issue | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-16 | 2026 | 7 | 16 | Machai HPS | 2.6 | 2 | 1.7 | 40520 | 39424 | 20 | 28 | 64.94 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 184149.5 | 24580.91 | 1096 | Unit tripped at 0508hrs due to revers power, while unit synched at 0640hrs. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-07-16 | 2026 | 7 | 16 | Malakand-3 HPS | 81 | 61 | 56.59 | 1358211 | 1345230 | 51 | 39.06 | 69.87 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3850989.92 | 1397909.05 | 12981 | As per available hydrology from the Irrigation Department all the three Units are on bar. Load variation is due to fluctuations in the hydrology of River Swat. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-16 | 2026 | 7 | 16 | Pehur HPS | 18 | 8.88 | 8.15 | 195600 | 189000 | 21.22 | 17 | 45.28 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 711963 | 279608.61 | 6600 | Plant remained operational throughout 24 hrs and irrigation valve open. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-16 | 2026 | 7 | 16 | Reshun HPS | 4.2 | 2.58 | 1.94 | 47000 | 46740 | 2.95 | 2.87 | 46.63 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 630055.2 | 638143.2 | 260 | Nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-07-17 | 2026 | 7 | 17 | Daral Khwar HPS | 36.6 | 27.6 | 26 | 620540 | 620540 | 28.25 | 10.38 | 70.64 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 5130810.88 | 737014.92 | 0 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 26 MW according to the available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-17 | 2026 | 7 | 17 | Jabori HPS | 10.2 | 7 | 6.24 | 149795 | 148080 | 8.69 | 4.9 | 61.19 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 845418.34 | 533527.67 | 1715 | Unit 01 and unit 02 were on the bar delivering an average load equals to 6.24 MW to the national grid according to the available hydrology and prevailing system constraints. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-07-17 | 2026 | 7 | 17 | Karora HPS | 11.8 | 7.22 | 6.61 | 158704 | 155433 | 11.29 | 5.25 | 56.04 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 1209268.74 | 951563.52 | 3271 | 1. Unit No.1 and 02 are on bar, collectively delivering an average load of 6.61 MW according to the available inflow. 2. All three Lube oil pumps and both cooling water pumps are in operation to maintain the units' temperatures and cooling water flow/pressure within the prescribed limits for both units. No standby pump is available, as all of the pumps are currently in service. 3. Emergency trip active on unit 01 at 22:38 hrs due to shaft seal pressure sensor malfunctioning. 4. Energy generation remained below the target due to low hydrology. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-07-17 | 2026 | 7 | 17 | Koto HPS | 40.8 | 24.75 | 19.43 | 470000 | 465282 | 98.8 | 60.58 | 48 | 8.24 | 96 | 58 | 940000 | 7745600 | 3833923.68 | 3911676.32 | 4718 | Unit #01 and Unit #02 are on bar , delivering an average load of 19.43MW. Unit #03 is on standby due to starting point.station load maintain according to available hydrology | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-17 | 2026 | 7 | 17 | Machai HPS | 2.6 | 2.05 | 1.83 | 44956 | 43780 | 29.6 | 28 | 72.04 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 204496.38 | 4234.04 | 1176 | Unit tripped at 0752 & 2039 hrs due to 11KV line tripping and Unit synchronised with the system at 0801 & 2048 hrs respectively. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-07-17 | 2026 | 7 | 17 | Malakand-3 HPS | 81 | 61 | 56.11 | 1346599 | 1333630 | 51 | 38.04 | 69.27 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3817782.6 | 1431116.37 | 12969 | As per available hydrology from the Irrigation Department all the three Units are on bar. Load variation is due to fluctuations in the hydrology of River Swat. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-17 | 2026 | 7 | 17 | Pehur HPS | 18 | 9.08 | 8.72 | 209400 | 204000 | 21.22 | 17 | 48.47 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 768468 | 223103.61 | 5400 | Plant operational 24 hours + irrigation valve open. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-17 | 2026 | 7 | 17 | Reshun HPS | 4.2 | 2.83 | 1.84 | 43000 | 42760 | 2.7 | 2.63 | 42.66 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 576404.8 | 691793.6 | 240 | line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-07-18 | 2026 | 7 | 18 | Daral Khwar HPS | 36.6 | 26.6 | 25.4 | 605910 | 605910 | 28.25 | 10.13 | 68.98 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 5009845.65 | 857980.15 | 0 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 25.4 MW according to the available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-18 | 2026 | 7 | 18 | Jabori HPS | 10.2 | 6.5 | 5.86 | 140670 | 138960 | 8.69 | 4.6 | 57.46 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 793350.43 | 585595.57 | 1710 | Unit 01 and 02 were on the bar delivering an average load equals to 5.86 MW to the national grid according to the available hydrology and prevailing system constraints. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-07-18 | 2026 | 7 | 18 | Karora HPS | 11.8 | 5.92 | 5.8 | 139112 | 135931 | 11.29 | 4.79 | 49.12 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 1057543.18 | 1103289.08 | 3181 | 1. Unit No. 02 is on bar, delivering an average load of 5.80 MW according to the available inflow. 2. Energy generation remained below the target due to low hydrology. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-07-18 | 2026 | 7 | 18 | Koto HPS | 40.8 | 24.75 | 19.6 | 470478 | 469198 | 98.8 | 60.54 | 48.05 | 8.24 | 96 | 58 | 940000 | 7745600 | 3866191.52 | 3879408.48 | 1280 | Unit #01 and Unit #02 are synchronized to the grid and operating with Average load of 19.60 MW , while Unit #03 is on standby due to low hydrology and a communication system issue. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-18 | 2026 | 7 | 18 | Machai HPS | 2.6 | 2.06 | 1.81 | 42640 | 41624 | 29.6 | 28 | 68.33 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 194425.7 | 14304.71 | 1016 | Unit tripped at 0401 hrs due to 11KV line tripping and Unit synchronised with the system at 0410 hrs. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-07-18 | 2026 | 7 | 18 | Malakand-3 HPS | 81 | 63 | 58.22 | 1397306 | 1384400 | 51 | 39.24 | 71.88 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3963121.88 | 1285777.09 | 12906 | As per available hydrology from Irrigation Department all three units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-18 | 2026 | 7 | 18 | Pehur HPS | 18 | 9.9 | 9.1 | 219200 | 212000 | 20.21 | 16 | 50.74 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 798604 | 192967.61 | 7200 | Not reported | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-18 | 2026 | 7 | 18 | Reshun HPS | 4.2 | 2.49 | 1.86 | 43000 | 42770 | 2.7 | 2.63 | 42.66 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 576539.6 | 691658.8 | 230 | Line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-07-19 | 2026 | 7 | 19 | Daral Khwar HPS | 36.6 | 29.1 | 26 | 621550 | 621550 | 28.25 | 10.27 | 70.76 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 5139161.86 | 728663.94 | 0 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 26 MW according to the available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-19 | 2026 | 7 | 19 | Jabori HPS | 10.2 | 7 | 1.66 | 39740 | 38880 | 8.69 | 1.3 | 16.23 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 221973.7 | 1156972.3 | 860 | 1- Unit 01 and 02 were on the bar delivering an average load equals to 1.66 MW to the national grid according to the available hydrology and prevailing system constraints. 2- The plant was shut down at 0702 Hrs due to extremely muddy water and flood conditions in Siren river. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-07-19 | 2026 | 7 | 19 | Karora HPS | 11.8 | 5.93 | 5.74 | 137796 | 134656 | 11.29 | 4.85 | 48.66 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 1047623.68 | 1113208.58 | 3140 | 1. Unit No.02 is on bar, delivering an average load of 5.74 MW according to the available inflow, while Unit 01 remains on standby. 2 At 19:53 hrs, Unit 02 experienced an Emergency Trip, resulting in the operation of E3Q1, E4Q1 and K2Q1 breakers. After resetting the operated protection relays and confirming normal operating conditions, the opened breakers were successfully reclosed at 20:02hrs. Unit 02 was subsequently synchronized with the sytem at 20:13 hrs. 3. Energy generation remained below the target due to low hydrology. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-07-19 | 2026 | 7 | 19 | Koto HPS | 40.8 | 24 | 20.24 | 485825 | 484485 | 98.8 | 62.51 | 49.61 | 8.24 | 96 | 58 | 940000 | 7745600 | 3992156.4 | 3753443.6 | 1340 | Unit #01 and Unit #02 are synchronized to the grid and operating with Average load of 20.24 MW ,while Unit #03 is on standby due to low hydrology and a communication system issue. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-19 | 2026 | 7 | 19 | Machai HPS | 2.6 | 1.93 | 0.87 | 21724 | 21120 | 29.6 | 28 | 34.81 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 98651.52 | 110078.9 | 604 | Unit stopped normally at 1205 hrs due to governor system malfunction. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-07-19 | 2026 | 7 | 19 | Malakand-3 HPS | 81 | 62 | 59.12 | 1418921 | 1406060 | 51 | 39.64 | 72.99 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 4025127.96 | 1223771.01 | 12861 | As per available hydrology from irrigation department all three units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-19 | 2026 | 7 | 19 | Pehur HPS | 18 | 10.33 | 8.55 | 205300 | 199000 | 21.22 | 17 | 47.52 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 749633 | 241938.61 | 6300 | plant remained off the bar for 55 minutes because of tripping on ''overcurrent protection'', due to 132kv supply failure. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-19 | 2026 | 7 | 19 | Reshun HPS | 4.2 | 2.68 | 1.89 | 42000 | 41780 | 2.65 | 2.57 | 41.67 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 563194.4 | 705004 | 220 | Line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-07-20 | 2026 | 7 | 20 | Daral Khwar HPS | 36.6 | 32.5 | 26.4 | 629900 | 629900 | 28.25 | 10.53 | 71.71 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 5208202.17 | 659623.64 | 0 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 26.4 MW according to the available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-20 | 2026 | 7 | 20 | Jabori HPS | 10.2 | 2.1 | 0.29 | 6963 | 6370 | 8.69 | 0.22 | 2.84 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 36367.6 | 1342578.4 | 593 | Unit 01 was synchronized at 1140 Hrs after muddy flood water subsided but due to heavy rainfall in catchment area the water again becomes muddy. The trash rack was also heavily choked. Trash rack couldn't be cleaned as water flow was high subsequently plant was again shutdown at 1417 Hrs. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-07-20 | 2026 | 7 | 20 | Karora HPS | 11.8 | 9.2 | 4.56 | 109532 | 107210 | 11.2 | 4 | 38.68 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 834093.8 | 1326738.46 | 2322 | 1. Unit No.1 and 02 are on bar, collectively delivering an average load of 4.56 MW according to the available inflow. 2. The Plant was completely shut down for the cleaning of Intake trash rack at 16:05 hrs. After completion of the cleaning, Unit # 02 was started and synchronized with system at 17:19 hrs and load gradually increased to 5.9 MW, similarly unit 01 was synchronized with grid at 17:40 hrs and load was gradually increased to 3.3 MW as per available hydrology 3. At 20:24 hrs, the complex was shutdown in a controlled manner due to flood conditions caused by heavy rainfall in the upstream area. The excessive inflow resulted in significant accumulation of debris, silt, and floating matrerial causing severe choking of the intake trashrack. 4. Energy generation remained below the target due to low hydrology. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-07-20 | 2026 | 7 | 20 | Koto HPS | 40.8 | 24 | 19.07 | 457702 | 456302 | 98.8 | 58.9 | 46.74 | 8.24 | 96 | 58 | 940000 | 7745600 | 3759928.48 | 3985671.52 | 1400 | Unit #01 and Unit #02 are synchronized to the grid and operating with Average load of 19.07 plant was shutdown for trash rack cleaning Unit #03 is on standby due to low hydrology and a communication system issue. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-20 | 2026 | 7 | 20 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 29.6 | 20 | 0 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 0 | 208730.42 | 0 | Unit stand still due to governor malfunctioning | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-07-20 | 2026 | 7 | 20 | Malakand-3 HPS | 81 | 65 | 61.55 | 1477188 | 1463900 | 51 | 41.01 | 75.99 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 4190706.53 | 1058192.44 | 13288 | As per available hydrology from irrigation department all three units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-20 | 2026 | 7 | 20 | Pehur HPS | 18 | 10.16 | 9.2 | 220800 | 214000 | 21.22 | 17 | 51.11 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 806138 | 185433.61 | 6800 | Plant remained operational throughout 24 hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-20 | 2026 | 7 | 20 | Reshun HPS | 4.2 | 2.77 | 1.81 | 42000 | 41790 | 2.65 | 2.57 | 41.67 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 563329.2 | 704869.2 | 210 | Line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-07-21 | 2026 | 7 | 21 | Daral Khwar HPS | 36.6 | 36.6 | 30.2 | 722550 | 722550 | 28.25 | 12.08 | 82.26 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 5974260.16 | -106434.36 | 0 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 30.2 MW according to the available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-21 | 2026 | 7 | 21 | Jabori HPS | 10.2 | 2.3 | 0.45 | 10714 | 10000 | 10.32 | 0.35 | 4.38 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 57092 | 1321854 | 714 | Plant was shutdown at 1510 Hrs due to extremely muddy water and flood condition in siren river. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-07-21 | 2026 | 7 | 21 | Karora HPS | 11.8 | 10.13 | 2.15 | 51591 | 51161 | 11.29 | 3.77 | 18.22 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 398032.58 | 1762799.68 | 430 | 1. Unit No.1 and 02 are on bar, collectively delivering an average load of 2.15MW according to the available inflow. 2 The Plant was completely shut down for the cleaning of Intake trash rack at 09:25 hrs. After completion of the cleaning, Unit # 02 was started and synchronized with system at 09:42 hrs. and load gradually increased to 5.9 MW, similarly unit 01 was synchronized with grid at 13:42 hrs. and load was gradually increased to 3.3 MW as per available hydrology 3. At 18:26 hrs., the complex was shutdown in a controlled manner due to flood conditions caused by heavy rainfall in the upstream area. The excessive inflow resulted in significant accumulation of debris, silt, and floating material causing severe choking of the intake trash rack. 4. Energy generation remained below the target due to low hydrology. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-07-21 | 2026 | 7 | 21 | Koto HPS | 40.8 | 26.9 | 19.8 | 475283 | 474003 | 98.8 | 61.16 | 48.54 | 8.24 | 96 | 58 | 940000 | 7745600 | 3905784.72 | 3839815.28 | 1280 | Unit 1 and 2 on bar delivering an average load of 19.80 MW. Unit #03 is on standby due to a communication/PLC issue. Plant load maintained according to Inflow and Intake choking. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-21 | 2026 | 7 | 21 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 29.2 | 8 | 0 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 0 | 208730.42 | 0 | Unit standstill due to less inflow. Governor Maintenance is in progress. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-07-21 | 2026 | 7 | 21 | Malakand-3 HPS | 81 | 66 | 51.17 | 1228139 | 1216760 | 51 | 35.38 | 63.18 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3483218.85 | 1765680.12 | 11379 | Due to heavy rainfall in the Upper Swat region, the Irrigation Department reduced the flow to avoid flooding & protect irrigation infrastructure. Consequently, due to the reduced hydrology, Unit #01 was desynchronized from the system at 15:15Hrs & kept standby. As per available hydrology from the Irrigation Department two Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-21 | 2026 | 7 | 21 | Pehur HPS | 18 | 10.18 | 3.99 | 95800 | 92000 | 21.22 | 7 | 22.18 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 346564 | 645007.61 | 3800 | The plant remained shut down for 14 hours due to heavy rainfall and nil irrigation demand as per instructions of irrigation officials. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-21 | 2026 | 7 | 21 | Reshun HPS | 4.2 | 2.58 | 1.59 | 36000 | 35790 | 2.3 | 2.2 | 35.71 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 482449.2 | 785749.2 | 210 | outhoing feeder breaker tripped 9times due to line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-07-22 | 2026 | 7 | 22 | Daral Khwar HPS | 36.6 | 36.6 | 36.7 | 877080 | 877080 | 28.25 | 14.67 | 99.85 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 7251960.56 | -1384134.76 | 0 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 36.7 MW according to the available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-22 | 2026 | 7 | 22 | Jabori HPS | 10.2 | 5 | 0.27 | 6595 | 5850 | 10.32 | 0.22 | 2.69 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 33398.82 | 1345547.18 | 745 | Unit 01 was synchronized at 1725 Hrs after cleaning the cooling water strainers and flushing the sand trap. However, the unit was shut down again at 1938 Hrs due to severe choking of the main trash rack caused by high water flow. Cleaning of the trash rack could not be carried out during the high-flow conditions as no trash rack cleaning mechanism is available. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-07-22 | 2026 | 7 | 22 | Karora HPS | 11.8 | 0 | 0 | 0 | 0 | 11.29 | 0 | 0 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 0 | 2160832.26 | 0 | 1. The Power Plant is completely shutdown since 21-07-2026 at 18:26 hrs due to monsoon flood at intake site. 2. The energy generation remained below the target due to low hydrology. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-07-22 | 2026 | 7 | 22 | Koto HPS | 40.8 | 26.83 | 21.18 | 508397 | 507137 | 98.8 | 65.42 | 51.92 | 8.24 | 96 | 58 | 940000 | 7745600 | 4178808.88 | 3566791.12 | 1260 | Units 1 and 2 remain on-bar, delivering an average load of 21.18 MW, while Unit 3 is on standby due to a Communication/PLC issue. Plant output was adjusted in response to water inflow and trash rack clogging. Floodwaters continue to surge through the Panjkora River, carrying heavy loads of trashes and floating waste. This frequent clogging of the intake trash racks is restricting plant capacity and causing a significant reduction in power generation. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-22 | 2026 | 7 | 22 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 11 | 2 | 0 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 0 | 208730.42 | 0 | (1) - Unit stands still due to less inflow. (2)- Governor Maintenance is in progress. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-07-22 | 2026 | 7 | 22 | Malakand-3 HPS | 81 | 41 | 34.95 | 838769 | 829160 | 51 | 24.36 | 43.15 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 2373636.33 | 2875262.64 | 9609 | As per Irrigation Department Letter C/W No. 394, due to heavy rainfall in the Upper Swat region, the water flow was reduced to prevent flooding and protect irrigation infrastructure. Consequently, Unit #02 was desynchronized from the system at 1435 Hrs and kept on standby. The unit #02 was synchronized at 1852 Hrs as hydrological conditions slightly improved. As per available hydrology from the Irrigation Department the two Units are on bar | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-22 | 2026 | 7 | 22 | Pehur HPS | 18 | 5.5 | 5.1 | 122400 | 117000 | 21.22 | 8 | 28.33 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 440739 | 550832.61 | 5400 | Unit#1 on bar with 5.5 MW of load with restricted flow of 8cms from irrigation department. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-22 | 2026 | 7 | 22 | Reshun HPS | 4.2 | 2.47 | 1.67 | 39000 | 38785 | 2.43 | 2.38 | 38.69 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 522821.8 | 745376.6 | 215 | outgoing feeder breaker tripped 7times due to line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-07-23 | 2026 | 7 | 23 | Daral Khwar HPS | 36.6 | 36.6 | 36.8 | 879340 | 879340 | 28.25 | 14.71 | 100.11 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 7270646.92 | -1402821.12 | 0 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 36.8 MW according to the available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-23 | 2026 | 7 | 23 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 10.32 | 0 | 0 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 0 | 1378946 | 0 | Due to continuous heavy rainfall over the past four days, the Siren River has experienced a moderate flood, resulting in highly turbid water. The excessive flow has completely choked the main trash rack and gravel trap with debris, preventing water from entering the intake channel. Furthermore, there is no safe and effective mechanism for cleaning the trash rack during high-flow conditions; therefore, the powerhouse has remained shut down. Once the river flow recedes to a safe level, the trash rack will be cleaned, and the powerhouse will be restarted in accordance with the applicable SOPs. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-07-23 | 2026 | 7 | 23 | Karora HPS | 11.8 | 0 | 0 | 0 | 0 | 11.29 | 0 | 0 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 0 | 2160832.26 | 0 | No data submitted for this date | rekarorahps2000@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-07-23 | 2026 | 7 | 23 | Koto HPS | 40.8 | 26.92 | 20.52 | 492401 | 491141 | 98.8 | 63.36 | 50.29 | 8.24 | 96 | 58 | 940000 | 7745600 | 4047001.84 | 3698598.16 | 1260 | Units 1 and 2 remained on-bar, delivering an average load of 20.52 MW, while Unit 3 was on standby due to a Communication/PLC issue. Trash rack cleaning at the intake was carried out; during the cleaning, the Koto plant remained shut down from 09:39 to 10:56 hours. This outage restricted overall plant generation. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-23 | 2026 | 7 | 23 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 0 | 208730.42 | 0 | (1) - Unit stands still due to less inflow. (2)- Governor Maintenance is in progress. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-07-23 | 2026 | 7 | 23 | Malakand-3 HPS | 81 | 36 | 13.36 | 320703 | 316550 | 51 | 9.85 | 16.5 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 906187.68 | 4342711.28 | 4153 | As per Irrigation Department Letter C/W No. 408-7, due to heavy rainfall in the Upper Swat region, the Irrigation Department diverted the water flow from the Auxiliary Tunnel of Malakand-III HPC to prevent potential damage. Consequently, Unit #02 was desynchronized from the system at 0924 Hrs, and Unit #03 was desynchronized at 0933 Hrs due to non-availability of water and kept on standby, while Unit #01 had already been on standby since 21 July 2026 at 1515 Hrs. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-23 | 2026 | 7 | 23 | Pehur HPS | 18 | 6.05 | 5.74 | 137900 | 131000 | 21.22 | 8 | 31.92 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 493477 | 498094.61 | 6900 | Plant remained operational throughout 24 hrs as per irrigation demand. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-23 | 2026 | 7 | 23 | Reshun HPS | 4.2 | 2.72 | 1.98 | 43000 | 42770 | 2.22 | 2.63 | 42.66 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 576539.6 | 691658.8 | 230 | Line faults. | zafar.src@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days; Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-07-24 | 2026 | 7 | 24 | Daral Khwar HPS | 36.6 | 36.6 | 36.7 | 876760 | 876760 | 28.25 | 14.66 | 99.81 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 7249314.71 | -1381488.9 | 0 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 36.7 MW according to the available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-24 | 2026 | 7 | 24 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 10.32 | 0 | 0 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 0 | 1378946 | 0 | Plant shutdown due to chocked trash rack, gravel trap and sand trap. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-07-24 | 2026 | 7 | 24 | Karora HPS | 11.8 | 0 | 0 | 0 | 0 | 11.29 | 0 | 0 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 0 | 2160832.26 | 0 | The Power Plant is completely shutdown since 21-07-2026 at 18:26 hrs due to monsoon flood at intake site. The energy generation remained below the target due to low flow hydrology. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-07-24 | 2026 | 7 | 24 | Koto HPS | 40.8 | 27.13 | 22.67 | 544099 | 542879 | 98.8 | 70.01 | 55.57 | 8.24 | 96 | 58 | 940000 | 7745600 | 4473322.96 | 3272277.04 | 1220 | 1) The actual daily inflow was recorded at 70.01 cumecs, The historical average of 98.80 cumecs.Units 1 and 2 were operated at an average load of 22.67 MW, with a maximum capacity of 27.13 MW. Unit 3 remained on standby an unresolved starting issue. In addition, the Intake Trash Rack Cleaning Machine (TRCM) is not yet operational, and issues with the powerhouse cooling water strainers also persist. 2) The plant shutdown from 09:46Hrs to 12:41Hrs for Intake Trash Racks Cleaning activity. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-24 | 2026 | 7 | 24 | Machai HPS | 2.6 | 0.87 | 0.64 | 16028 | 15268 | 0 | 15 | 25.69 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 71316.83 | 137413.59 | 760 | Unit synched at 0020 hrs. after successful maintenance of governor system. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-07-24 | 2026 | 7 | 24 | Malakand-3 HPS | 81 | 63 | 24.14 | 579360 | 574740 | 51 | 20.23 | 29.8 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 1645308.2 | 3603590.77 | 4620 | Water was released from Amandara Headwork’s by the Irrigation Department at 0800 Hrs. Consequently, Unit # 01, 02 & 03 synchronized with the system at 12:03, 13:06 & 11:46Hrs. Unit # 02 desynchronized from the system at 18:04Hrs for replacement of the broken shear pin. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-24 | 2026 | 7 | 24 | Pehur HPS | 18 | 9.37 | 6.88 | 165100 | 160000 | 21.22 | 11 | 38.22 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 602720 | 388851.61 | 5100 | Generation is less because of low irrigation demand. Also plant remained off the bar from 2315 hrs to 2355 Hrs due to tripping of 132KV supply line. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-24 | 2026 | 7 | 24 | Reshun HPS | 4.2 | 2.7 | 1.38 | 33000 | 32800 | 2.02 | 2.2 | 32.74 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 442144 | 826054.4 | 200 | clearance works of gravel and sand at Intake. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-07-25 | 2026 | 7 | 25 | Daral Khwar HPS | 36.6 | 36.6 | 36.2 | 866270 | 866270 | 28.25 | 14.49 | 98.62 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 7162580.24 | -1294754.44 | 0 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 36.2 MW according to the available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-25 | 2026 | 7 | 25 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 10.32 | 0 | 0 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 0 | 1378946 | 0 | Plant still shutdown due to chocked trash rack, gravel trap and sand trap. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-07-25 | 2026 | 7 | 25 | Karora HPS | 11.8 | 5.9 | 0.57 | 13897 | 13779 | 11.29 | 0.55 | 4.91 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 107200.62 | 2053631.64 | 118 | 1. Unit No. 1 is on bar, delivering an average load of 0.57 MW according to the available inflow. 2. The Powerplant remained completely shutdown since 21-07-2026 at 18:26 hrs due to monsoon flood at intake site. 3. After cleaning activity at intake site, Unit No. 01 synchronized with the National Grid at 21:31 hrs. 4. Energy generation remained below the target due to lower-than-expected hydrological flows. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-07-25 | 2026 | 7 | 25 | Koto HPS | 40.8 | 26.73 | 22.83 | 547833 | 546813 | 98.8 | 70.49 | 55.95 | 8.24 | 96 | 58 | 940000 | 7745600 | 4505739.12 | 3239860.88 | 1020 | 1) The actual daily inflow was recorded at 70.49 cumecs, the historical average of 98.80 cumecs. Due to the low hydrology, only Units 1 and 2 were operated at an average load of 22.83 MW, with a maximum capacity of 26.73 MW. Unit 3 remained an unresolved starting issue. In addition, the Intake Trash Rack Cleaning Machine (TRCM) is not yet operational, and issues with the powerhouse cooling water strainers also persist. 2)Both 132 kV LAL QILA MAIDAN and TIMERGARA transmission lines tripped at 00:08 hrs. Both lines were restored at 01:46 hrs. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-25 | 2026 | 7 | 25 | Machai HPS | 2.6 | 0.89 | 0.66 | 15893 | 15107 | 6 | 15 | 25.47 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 70564.8 | 138165.62 | 786 | No data submitted for this date | engr.atifwazir@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-07-25 | 2026 | 7 | 25 | Malakand-3 HPS | 81 | 66 | 54.66 | 1311825 | 1300840 | 51 | 41.38 | 67.48 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3723914.67 | 1524984.3 | 10985 | Unit 02 synchronized with the system at 03:10hrs after replacement of the broken shear pin. Unit 02 desynchronized from the system at 20:03hrs due to the rupture of the turbine guide bearing cooling water pipe. Unit 02 synchronized with the system at 22:35hrs after repair of the turbine guide cooling water pipe. All three Unit are on bar as per available hydrology. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-25 | 2026 | 7 | 25 | Pehur HPS | 18 | 11.2 | 9.91 | 238000 | 231000 | 21.22 | 16 | 55.09 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 870177 | 121394.61 | 7000 | plant remained operational throughout 24 hrs. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-25 | 2026 | 7 | 25 | Reshun HPS | 4.2 | 2.87 | 1.59 | 34000 | 33688 | 2.2 | 2.08 | 33.73 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 454114.24 | 814084.16 | 312 | 1. clearance of gravel and sand at Intake. 2. tripping due to line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-07-26 | 2026 | 7 | 26 | Daral Khwar HPS | 36.6 | 36.6 | 36.5 | 875160 | 872290 | 28.25 | 14.59 | 99.63 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 7212355.41 | -1344529.6 | 2870 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 36.5 MW according to the available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-26 | 2026 | 7 | 26 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 10.32 | 0 | 0 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 0 | 1378946 | 0 | Plant shutdown | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-07-26 | 2026 | 7 | 26 | Karora HPS | 11.8 | 5.93 | 5.83 | 140000 | 137312 | 11.29 | 4.4 | 49.44 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 1068287.36 | 1092544.9 | 2688 | 1.unit No . 1 is on bar delivering an average load of 5.83 MW according to the available inflow. 2. Energy generation remained below the target due to lower-than-expected hydrological flows. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-07-26 | 2026 | 7 | 26 | Koto HPS | 40.8 | 26.88 | 26.14 | 627318 | 626298 | 98.8 | 80.72 | 64.06 | 8.24 | 96 | 58 | 940000 | 7745600 | 5160695.52 | 2584904.48 | 1020 | The actual daily inflow was recorded at 80.72 cumecs, The historical average of 98.80 cumecs. Units 1 and 2 were operated at an average load of 26.14 MW, with a maximum load of 26.88 MW. Unit 3 remained on standby an unresolved starting issue. In addition, the Intake Trash Rack Cleaning Machine (TRCM) is not yet operational, and issues with the powerhouse cooling water strainers also persist. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-26 | 2026 | 7 | 26 | Machai HPS | 2.6 | 0.88 | 0.66 | 15759 | 14945 | 12 | 15 | 25.25 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 69808.1 | 138922.32 | 814 | No data submitted for this date | engr.atifwazir@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-07-26 | 2026 | 7 | 26 | Malakand-3 HPS | 81 | 66 | 64.12 | 1538993 | 1527500 | 51 | 42.33 | 79.17 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 4372774.25 | 876124.72 | 11493 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-26 | 2026 | 7 | 26 | Pehur HPS | 18 | 10.09 | 8.9 | 212700 | 207000 | 21.22 | 16 | 49.24 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 779769 | 211802.61 | 5700 | Plant remained operational throughout 24 hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-26 | 2026 | 7 | 26 | Reshun HPS | 4.2 | 2.55 | 1.73 | 39000 | 38685 | 2.43 | 2.38 | 38.69 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 521473.8 | 746724.6 | 315 | line faults | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-07-27 | 2026 | 7 | 27 | Daral Khwar HPS | 36.6 | 36.6 | 34.7 | 830400 | 830400 | 28.25 | 13.89 | 94.54 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 6865996.32 | -998170.51 | 0 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 34.7 MW according to the available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-27 | 2026 | 7 | 27 | Jabori HPS | 10.2 | 0 | 0 | 0 | 0 | 10.32 | 0 | 0 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 0 | 1378946 | 0 | Excavation of chocked trash rack and gravel trap carried out. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-07-27 | 2026 | 7 | 27 | Karora HPS | 11.8 | 10.17 | 8.52 | 204464 | 201490 | 11.29 | 6.77 | 72.2 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 1567592.2 | 593240.06 | 2974 | Unit No . 1 & 2 is on bar delivering an average load of 8.52 MW according to the available inflow. Unit #02 GCC temperature reached the alarm threshold of 45.2°C. Despite the cooling water pressure remaining stable at 3.2 bar and the GCC cooling water control valve being in the fully open position, the unit load was reduced to limit the GCC temperature and maintain safe operating conditions. At 22:21 hrs, Unit #01 electrically tripped following GCB opening. Upon investigation, protection relays F60 and F512 were found operated with an I2> alarm, while lockout relays 86T2 and 86T3 were also found operated. After resetting all operated relays, Unit #01 was resynchronized with the grid at 22:25 hrs, and the load was gradually increased to 5.9 MW. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-07-27 | 2026 | 7 | 27 | Koto HPS | 40.8 | 26.75 | 25.48 | 612156 | 610856 | 98.8 | 74.42 | 62.52 | 8.24 | 96 | 58 | 940000 | 7745600 | 5033453.44 | 2712146.56 | 1300 | Units#01 and Unit #02 are on bar delivering an average load of 25.48 MW to national grid, Unit#03 remains shut down due to unresolved starting issue. In addition, the Intake Trash Rack Cleaning Machine(TRCM) is not yet operational, and issues with the powerhouse cooling water strainers also persist. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-27 | 2026 | 7 | 27 | Machai HPS | 2.6 | 0.89 | 0.68 | 15624 | 14784 | 18 | 15 | 25.04 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 69056.06 | 139674.35 | 840 | 1) Unit tripped at 2226hrs due to temp sensor fault, after Unit synched at 0259hrs. 2) Unit tripped at 1327,1713hrs due to 11kv line tripe, 11kv line restored at 1333,1750hrs and Unit synched at 1342,1755hrs. 3) Unit normally stopped at 1634,2009,2201hrs due to less & low water level in irrigation canal, while unit synched at 1650,2058,2225hrs. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-07-27 | 2026 | 7 | 27 | Malakand-3 HPS | 81 | 67 | 62.98 | 1511632 | 1499650 | 51 | 41.44 | 77.76 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 4293048.06 | 955850.91 | 11982 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-27 | 2026 | 7 | 27 | Pehur HPS | 18 | 11.73 | 10.39 | 249500 | 243000 | 21.22 | 17 | 57.75 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 915381 | 76190.61 | 6500 | Units #01 and #02 at 0635 hrs tripped due to failure of the 132 kV supply because of the isolation of the Gadoon Grid from the National Grid. Units #01 and #02 were taken on bar at 0710 and 0725 hrs, respectively. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-27 | 2026 | 7 | 27 | Reshun HPS | 4.2 | 2.63 | 1.88 | 45000 | 44679 | 2.81 | 2.75 | 44.64 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 602272.92 | 665925.48 | 321 | outgoing feeder breaker tripped 4times due to line fault. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-07-28 | 2026 | 7 | 28 | Daral Khwar HPS | 36.6 | 32.3 | 30 | 717860 | 716260 | 28.25 | 11.98 | 81.72 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 5922252.56 | -54426.75 | 1600 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 30 MW according to the available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-28 | 2026 | 7 | 28 | Jabori HPS | 10.2 | 5.1 | 0.44 | 10540 | 9670 | 10.32 | 0.34 | 4.31 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 55207.96 | 1323738.04 | 870 | At 1200 Hrs, Unit 01 was operated in FSNL (Full Speed No Load) mode to facilitate flushing of the tunnel and penstock. At 1355 Hrs, the unit was synchronized with the grid and loaded to 5.1 MW. However, due to sudden heavy rainfall in the catchment area, the river water became extremely turbid. Consequently, Unit 01 was shut down at 1627 Hrs. Following the shutdown, the intake gate was closed to 90%, and the sand trap was kept under continuous flushing operation to remove the accumulated silt. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-07-28 | 2026 | 7 | 28 | Karora HPS | 11.8 | 9.48 | 7.21 | 172941 | 170672 | 11.29 | 5.85 | 61.07 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 1327828.16 | 833004.1 | 2269 | Unit No . 1 & 2 is on bar delivering an average load of 7.21 MW according to the available inflow. "At 12:44 hrs, Unit #01 mechanically tripped. During restoration, multiple attempts to start the lube oil pump in Auto mode were unsuccessful; therefore, the pump was started manually. At 13:50 hrs, Unit #01 was started, synchronized with the grid, and loaded to 5.9 MW. At 15:00 hrs, Unit #01 mechanically tripped again. The unit was restarted at 15:30 hrs, synchronized with the grid, and the load was restored to 5.9 MW." At 16:06 Hrs the complex was shutdown in a controlled manner as a safety measure due to heavy rainfall at upstream ,which made the water at intake muddy. After the water condition at intake returned to normal, Unit #02 was started and synchronized with the grid at 20:03 hrs. Subsequently, Unit #01 was started and synchronized with the grid at 20:09 hrs. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-07-28 | 2026 | 7 | 28 | Koto HPS | 40.8 | 26.4 | 26.22 | 625410 | 623910 | 98.8 | 76.22 | 63.87 | 8.24 | 96 | 58 | 940000 | 7745600 | 5141018.4 | 2604581.6 | 1500 | Units#01 and Unit #02 are on bar delivering an average load of 26.22 MW to national grid, Unit#03 remains shut down due to unresolved starting issue. In addition, the Intake Trash Rack Cleaning Machine(TRCM) is not yet operational, and issues with the powerhouse cooling water strainers also persist. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-28 | 2026 | 7 | 28 | Machai HPS | 2.6 | 0.55 | 0.42 | 10232 | 9284 | 19 | 15 | 16.4 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 43365.56 | 165364.85 | 948 | Unit tripped at 0138hrs due to 11kv line tripping, 11kv line restored at 0145hrs and Unit synched at 0151hrs. Unit stopped due to low water level in irrigation canal at 1105 while synced back with system at 1200hrs. Unit tripped due to reverse power at 1501,2359 while synced back with system at 1535,0012hrs | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-07-28 | 2026 | 7 | 28 | Malakand-3 HPS | 81 | 66 | 61.5 | 1476010 | 1462090 | 51 | 41.07 | 75.93 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 4185525.04 | 1063373.92 | 13920 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-28 | 2026 | 7 | 28 | Pehur HPS | 18 | 11.92 | 10.1 | 242400 | 236000 | 21.22 | 16 | 56.11 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 889012 | 102559.61 | 6400 | Not reported | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-28 | 2026 | 7 | 28 | Reshun HPS | 4.2 | 2.55 | 1.87 | 42000 | 41682 | 2.65 | 2.57 | 41.67 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 561873.36 | 706325.04 | 318 | outgoing feeder breaker tripped 4times due to line fault. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-07-29 | 2026 | 7 | 29 | Daral Khwar HPS | 36.6 | 30 | 28.1 | 674870 | 672070 | 28.25 | 11.24 | 76.83 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 5556876.38 | 310949.43 | 2800 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 28.1 MW according to the available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-29 | 2026 | 7 | 29 | Jabori HPS | 10.2 | 5 | 1.08 | 25955 | 25170 | 10.32 | 0.85 | 10.6 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 143700.56 | 1235245.44 | 785 | Unit 01 was synchronized at 1735 hrs and delivering an average load equals to 1.08 MW to the national grid. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-07-29 | 2026 | 7 | 29 | Karora HPS | 11.8 | 9.52 | 7.02 | 168459 | 167030 | 11.29 | 5.66 | 59.48 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 1299493.4 | 861338.86 | 1429 | Unit No . 1 & 2 is on bar delivering an average load of 7.02 MW according to the available inflow. "At 08:16 hrs, Unit #01 mechanically tripped. The HMI/SCADA alarm list indicated a ""Hydraulic Mechanical Accidental Shutdown,"" which initiated the governor emergency shutdown. The same recurring fault had previously occurred six times on 26.05.2026 and twice on 28.07.2026. After completing the necessary checks, Unit #01 was synchronized with the grid at 08:25 hrs and loaded to 5.9 MW. At 10:27 hrs, Unit #01 mechanically tripped again due to the same fault. After completing the necessary checks, Unit #01 was synchronized with the grid at 10:45 hrs and loaded to 5.9 MW. At 11:26 hrs, Unit #01 electrically tripped due to GCB opening. Protection relays F60, F511, 86T2, and 86T3 operated. After resetting the relays, Unit #01 was synchronized with the grid at 11:32 hrs and loaded to 5.9 MW. At 11:54 hrs, Unit #01 mechanically tripped again due to the same recurring fault. TR #27/2026 was issued for investigation. The EPC contractor was informed of the repeated tripping of Unit #01. Upon the contractor's advice, the unit was kept out of service until a detailed inspection and fault identification could be carried out for permanent rectification" Unit #02 remained in operation below its rated load due to elevated GCC temperature. The unit load was reduced to maintain the GCC temperature within the prescribed operating limits and ensure safe, reliable operation. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-07-29 | 2026 | 7 | 29 | Koto HPS | 40.8 | 26.1 | 23.5 | 560280 | 558880 | 98.8 | 71.95 | 57.22 | 8.24 | 96 | 58 | 940000 | 7745600 | 4605171.2 | 3140428.8 | 1400 | Units#01 and Unit #02 are on bar delivering an average load of 23.50 MW to national grid, Unit#03 remains shut down due to unresolved starting issue. In addition, the Intake Trash Rack Cleaning Machine(TRCM) is not yet operational, and issues with the powerhouse cooling water strainers also persist. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-29 | 2026 | 7 | 29 | Machai HPS | 2.6 | 0.54 | 0.38 | 9272 | 8360 | 19 | 15 | 14.86 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 39049.56 | 169680.86 | 912 | Unit stopped at 0513 hrs due to less water level in irrigation canal while unit synced back at 0609 hrs. Unit tripped due to reverse power at 0632,0640,0902 while synced back with system at 0638,0648,0938 hrs. due to recent heavy rainfall the irrigation department maintained reduced canal discharge in accordance with the demand of XEN Swabi irrigation Division. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-07-29 | 2026 | 7 | 29 | Malakand-3 HPS | 81 | 67 | 61.89 | 1485345 | 1472190 | 51 | 41.73 | 76.41 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 4214438.31 | 1034460.66 | 13155 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-29 | 2026 | 7 | 29 | Pehur HPS | 18 | 11 | 8 | 193100 | 187000 | 21.22 | 13 | 44.7 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 704429 | 287142.61 | 6100 | Plant operational 24 hrs | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-29 | 2026 | 7 | 29 | Reshun HPS | 4.2 | 2.68 | 1.8 | 42000 | 41688 | 2.65 | 2.57 | 41.67 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 561954.24 | 706244.16 | 312 | Line fault. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-07-30 | 2026 | 7 | 30 | Daral Khwar HPS | 36.6 | 28 | 26 | 624650 | 622250 | 28.25 | 10.41 | 71.11 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 5144949.68 | 722876.13 | 2400 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 26 MW according to the available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-30 | 2026 | 7 | 30 | Jabori HPS | 10.2 | 5.1 | 3.67 | 88044 | 86700 | 10.32 | 2.88 | 35.97 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 494987.64 | 883958.36 | 1344 | 1- Unit 01 was on the bar delivering an average load equals to 3.67 MW to the national grid according to the available hydrology and prevailing system constraints. 2- Unit 02 is in shutdown state due to chocked trash rack and accumulation of silt in one portion of sand trap and also in open channel before sand trap. Trash rack could not be cleaned due to high water flow as no mechanism of cleaning is available during high water flow. 3- Unit 01 was also shutdown at 1810 Hrs as precautionary measure due to heavy rainfall and muddy water. Flushing gates of sand trap is kept fully opened to remove the silt accumulated. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-07-30 | 2026 | 7 | 30 | Karora HPS | 11.8 | 9.96 | 6.82 | 163708 | 162168 | 11.29 | 5.39 | 57.81 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 1261667.04 | 899165.22 | 1540 | Unit No . 1 & 2 is on bar delivering an average load of 6.82 MW according to the available inflow. At 12:25 hrs, Unit #01 mechanically tripped. Upon inspection, the trip was attributed to a faulty shaft seal pressure gauge. At 13:20 hrs, the faulty shaft seal pressure gauge was replaced by the EPC contractor's representative. Following successful replacement and completion of operational checks, Unit #01 was synchronized with the grid at 13:30 hrs, and its load was gradually increased to 5.0 MW. At 17:51 hrs, Unit #01 again mechanically tripped. The SCADA alarm list indicated "Hydraulic Mechanical Accidental Shutdown Circuit Action." The EPC contractor's representative was informed. On his advice, the unit was restarted, and following the necessary checks, Unit #01 was synchronized with the grid at 19:15 hrs. The unit is currently under observation due to the recurrence of the mechanical trip. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-07-30 | 2026 | 7 | 30 | Koto HPS | 40.8 | 26.63 | 17.76 | 426170 | 424670 | 98.8 | 54.84 | 43.52 | 8.24 | 96 | 58 | 940000 | 7745600 | 3499280.8 | 4246319.2 | 1500 | Unit 1 and 2 on bar delivering an average load of 17.76 MW , plant was shutdown for 5hrs due to trash rack cleaning and T-46 turbine oil filling for unit 1 . Unit #03 is on standby due to a communication/PLC issue. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-30 | 2026 | 7 | 30 | Machai HPS | 2.6 | 0.53 | 0.38 | 9828 | 8976 | 19 | 15 | 15.75 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 41926.9 | 166803.52 | 852 | Unit stopped at 1659 hrs due to line tripping from katlang grid line restored at 1739 while unit synced back at 1744 hrs. Unit tripped due to reverse power at 1817, 2347 hrs while synced back with system at 1822, 2353 hrs. due to recent heavy rainfall the irrigation department maintained reduced canal discharge in accordance with the demand of XEN Swabi irrigation Division. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-07-30 | 2026 | 7 | 30 | Malakand-3 HPS | 81 | 66 | 61.73 | 1481625 | 1468350 | 51 | 41.52 | 76.22 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 4203445.54 | 1045453.42 | 13275 | As per available hydrology from Irrigation Department all three units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-30 | 2026 | 7 | 30 | Pehur HPS | 18 | 8.8 | 8.3 | 199800 | 194000 | 21.22 | 14 | 46.25 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 730798 | 260773.61 | 5800 | Generation is less because oflow irrigation demand. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-30 | 2026 | 7 | 30 | Reshun HPS | 4.2 | 2.67 | 1.84 | 45000 | 44678 | 2.81 | 2.75 | 44.64 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 602259.44 | 665938.96 | 322 | line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-07-31 | 2026 | 7 | 31 | Daral Khwar HPS | 36.6 | 28 | 25.8 | 620050 | 617250 | 28.25 | 10.32 | 70.59 | 8.2683 | 80.79 | 48 | 709677.42 | 5867825.81 | 5103608.18 | 764217.63 | 2800 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 25.8 MW according to the available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-07-31 | 2026 | 7 | 31 | Jabori HPS | 10.2 | 4.2 | 1.22 | 29178 | 28380 | 10.32 | 0.95 | 11.92 | 5.7092 | 98.66 | 79.57 | 241530.51 | 1378946 | 162027.1 | 1216918.9 | 798 | 1- Unit 01 delivered an average load equals to 1.22 MW to the national grid according to the prevailing system constraints. 2- Unit 02 is in shutdown state due to chocked trash rack and accumulation of silt in the sand trap and also in open channel before sand trap. Trash rack could not be cleaned due to high water flow as no mechanism of cleaning is available during high water flow. 3- Unit 01 was also shutdown at 1605 Hrs to flush the sand trap as accumulated silt was restricting the flow of water to tunnel. Flushing gates of sand trap is kept fully opened to remove the silt accumulated. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-07-31 | 2026 | 7 | 31 | Karora HPS | 11.8 | 8.2 | 7.14 | 171330 | 168342 | 11.29 | 5.64 | 60.5 | 7.78 | 98.07 | 0.69 | 277741.94 | 2160832.26 | 1309700.76 | 851131.5 | 2988 | Unit No . 1 & 2 is on bar delivering an average load of 7.14 MW according to the available inflow. At 21:44 hrs, Unit #02 was shut down in a controlled manner due to choking of the intake trash rack. TR#68/2026 was logged regarding an abnormal shutdown sequence observed during the controlled shutdown of Unit #02 initiated from SCADA due to intake trash rack choking. During the shutdown, the unit continued rotating at approximately 244 rpm while the main lube oil pump stopped operating prematurely. Lubrication to the bearings was maintained by the standby lube oil pump through the bypass line, as the standby pump was already in continuous operation. Under normal operating conditions, the main lube oil pump should remain in operation until the unit speed reaches 0 rpm, after which it stops automatically. The abnormal behavior was immediately communicated to the EPC Contractor's representative via WhatsApp, along with video evidence, for investigation and necessary corrective action. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-07-31 | 2026 | 7 | 31 | Koto HPS | 40.8 | 21.23 | 18.36 | 440556 | 439250 | 98.8 | 56.69 | 44.99 | 8.24 | 96 | 58 | 940000 | 7745600 | 3619420 | 4126180 | 1306 | Unit 1 and 2 on bar delivering an average load of 18.36 MW , Unit #03 is on standby due to a communication/PLC issue. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-31 | 2026 | 7 | 31 | Machai HPS | 2.6 | 0.63 | 0.41 | 10284 | 9504 | 19 | 15 | 16.48 | 4.671 | 71.61 | 70 | 44686.45 | 208730.42 | 44393.18 | 164337.23 | 780 | Unit stopped at 1658 hrs due to line tripping from katlang grid line restored at 1741 while unit synced back at 1748 hrs. Unit tripped due to reverse power at 0106,2041,2146 hrs while synced back with system at 0113,2122,2151 hrs. due to recent heavy rainfall the irrigation department maintained reduced canal discharge in accordance with the demand of XEN Swabi irrigation Division. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-07-31 | 2026 | 7 | 31 | Malakand-3 HPS | 81 | 61 | 46.96 | 1127051 | 1115480 | 51 | 32.37 | 57.98 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3193284.6 | 2055614.37 | 11571 | As per available hydrology from the Irrigation Department all the three Units are on bar. However from 07:01hrs to 17:18hrs two Units were on bar as of low hydrology later on all three Units are on bar as per available hydrology. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-07-31 | 2026 | 7 | 31 | Pehur HPS | 18 | 8.8 | 3.1 | 75300 | 73000 | 21.22 | 5 | 17.43 | 3.767 | 60.93 | 41 | 263225.81 | 991571.61 | 274991 | 716580.61 | 2300 | Plant remained shutdown since 1016 Hrs dt. 31-07-26 due to nil irrigation as per instruction of irrigation SDO. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-07-31 | 2026 | 7 | 31 | Reshun HPS | 4.2 | 2.63 | 2.06 | 45000 | 44678 | 2.81 | 2.75 | 44.64 | 13.48 | 93.33 | 45 | 94080 | 1268198.4 | 602259.44 | 665938.96 | 322 | nill | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-08-01 | 2026 | 8 | 1 | Daral Khwar HPS | 36.6 | 31 | 24.6 | 590550 | 587750 | 15.6 | 9.83 | 67.23 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 4859693.32 | 1776284.22 | 2800 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 24.6 MW according to the available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-01 | 2026 | 8 | 1 | Jabori HPS | 10.2 | 5.1 | 2.4 | 57483 | 56450 | 9.93 | 1.88 | 23.48 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 322284.34 | 1075327.82 | 1033 | 1- Unit 01 delivered an average load equals to 2.4 MW to the national grid according to the prevailing system constraints. 2- Unit 02 is in shutdown state due to chocked trash rack and accumulation of silt in one section of the sand trap and also in open channel before sand trap. Trash rack could not be cleaned due to high water flow as no mechanism of cleaning is available during high water flow. 3- Unit 01 was synchronized at 1207 Hrs after flushing one section of the sand trap, where silt had accumulated due to yesterday's heavy rainfall. The other section of sand trap couldn't be flushed due to choking. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-01 | 2026 | 8 | 1 | Karora HPS | 11.8 | 8.84 | 3.69 | 88560 | 87232 | 9.16 | 2.63 | 31.27 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 678664.96 | 1213631.81 | 1328 | 1.Unit No . 1 & 2 is on bar delivering an average load of 3.69MW according to the available inflow. 2. At 08:43 hrs, was complex shut down due to choking of the intake trash rack cleaning. Unit#01 synchronized with the system at 19:37 ,Unit#02 synchronized at 19:51 hrs. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-01 | 2026 | 8 | 1 | Koto HPS | 40.8 | 24.85 | 17.24 | 413770 | 412510 | 65.8 | 53.24 | 42.26 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 3399082.4 | 4040840.18 | 1260 | Unit 1 and 2 on bar delivering an average load of 17.24 MW Unit #03 is on standby due to a communication/PLC issue. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-01 | 2026 | 8 | 1 | Machai HPS | 2.6 | 0.6 | 0.45 | 10380 | 9548 | 17.87 | 15 | 16.63 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 44598.71 | 133809.38 | 832 | 1) Unit tripped at 2401,07441hrs due to revers power, while unit synched at 2410,0817hrs. 2) unit tripped at 1909hrs due to 11kv line tripe, 11kv line restored at 1938hrs, unit synched at 1949hrs. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-08-01 | 2026 | 8 | 1 | Malakand-3 HPS | 81 | 63 | 57.49 | 1379769 | 1368220 | 51 | 39.44 | 70.98 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3916803.39 | 1332095.57 | 11549 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-01 | 2026 | 8 | 1 | Pehur HPS | 18 | 5.65 | 2.7 | 65000 | 63000 | 18.39 | 9 | 15.05 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 237321 | 822299.65 | 2000 | Shortfall is due to less irrigation demand because of heavyrain. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-01 | 2026 | 8 | 1 | Reshun HPS | 4.2 | 2.89 | 1.86 | 45000 | 44675 | 2.81 | 2.75 | 44.64 | 13.48 | 100 | 45 | 100800 | 1358784 | 602219 | 756565 | 325 | Tripping due to line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-08-02 | 2026 | 8 | 2 | Daral Khwar HPS | 36.6 | 28 | 25.2 | 605720 | 602920 | 15.6 | 10.08 | 68.96 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 4985123.44 | 1650854.11 | 2800 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 25.2 MW according to the available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-02 | 2026 | 8 | 2 | Jabori HPS | 10.2 | 5.1 | 2.67 | 64019 | 62880 | 9.93 | 2.09 | 26.15 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 358994.5 | 1038617.66 | 1139 | 1- Unit 01 delivered an average load equals to 2.67 MW to the national grid according to the prevailing system constraints. 2- Unit 02 is in shutdown state due to chocked trash rack and accumulation of silt in the sand trap and also in open channel before sand trap. Trash rack could not be cleaned due to high water flow as no mechanism of cleaning is available during high water flow. 3- plant remained shutdown from 0640 Hrs to 1656 Hrs for flushing one section of the sand trap, where silt had accumulated due to yesterday's heavy rainfall. The other section od sand trap couldn't be flushed due to choking. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-02 | 2026 | 8 | 2 | Karora HPS | 11.8 | 9.3 | 8.42 | 202060 | 198935 | 9.16 | 6.99 | 71.35 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 1547714.3 | 344582.47 | 3125 | 1.Unit No . 1 & 2 is on bar delivering an average load of 8.42MW according to the available inflow. 2. At 04:20 hrs, Unit #01 mechanically tripped. During restoration, multiple attempts to start the lube oil pump in Auto mode were unsuccessful; therefore, the pump was started manually. At 05:29 hrs, Unit #01 was started, synchronized with the grid, and loaded to 3.5 MW. 3.The energy generation remained below the target due to low hydrology. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-02 | 2026 | 8 | 2 | Koto HPS | 40.8 | 24.42 | 18.72 | 449259 | 448019 | 65.8 | 57.81 | 45.88 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 3691676.56 | 3748246.02 | 1240 | Units 1 and 2 remain operational with an average plant load of 18.72 MW based on available inflow. Power generation fell sharply below expectations due to flood-induced intake choking, which forced shutdown of Unit 2 from 13:42 to 14:44 hours. Unit 3 has been shut down since 17th June 2026 due to an ongoing Communication/PLC issue. TRCM unavailability remains an active issue. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-02 | 2026 | 8 | 2 | Machai HPS | 2.6 | 0.62 | 0.45 | 10888 | 10164 | 19 | 15 | 17.45 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 47476.04 | 130932.05 | 724 | unit normally stopped at 0832,1213,1841hrs due to low & less inflow in irrigation canal, while unit synchronize wit the system at 0910,1255,1857hrs. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-08-02 | 2026 | 8 | 2 | Malakand-3 HPS | 81 | 63 | 59.12 | 1418944 | 1406830 | 51 | 40.44 | 72.99 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 4027332.24 | 1221566.73 | 12114 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-02 | 2026 | 8 | 2 | Pehur HPS | 18 | 10.13 | 7.5 | 180600 | 175000 | 18.39 | 12 | 41.81 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 659225 | 400395.65 | 5600 | Unit#02 at 1130 hrs started and loaded upto 4MW of load as per instructions of RE | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-02 | 2026 | 8 | 2 | Reshun HPS | 4.2 | 2.76 | 1.71 | 39000 | 38683 | 2.2 | 2.02 | 38.69 | 13.48 | 100 | 45 | 100800 | 1358784 | 521446.84 | 837337.16 | 317 | outgoing feeder breaker tripped 7times due to line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-08-03 | 2026 | 8 | 3 | Daral Khwar HPS | 36.6 | 36.6 | 27.5 | 660040 | 657240 | 15.6 | 10.99 | 75.14 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 5434257.49 | 1201720.06 | 2800 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 27.5 MW according to the available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-03 | 2026 | 8 | 3 | Jabori HPS | 10.2 | 5.7 | 2.59 | 62116 | 60960 | 9.93 | 2.03 | 25.37 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 348032.83 | 1049579.33 | 1156 | Unit 01 delivered an average load equals to 2.59 MW to the national grid according to prevailing system constraints. Plant remained shutdown t 1425 hrs due to heavy rain. A flood occurred in siren river resulting in a significant increase in water flow and high concentration of silt. To prevent muddy water entering the tunnel, the intake gate were closed and sand trap was placed on continuous flushing to remove accumulated silt. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-03 | 2026 | 8 | 3 | Karora HPS | 11.8 | 8.96 | 7.74 | 185754 | 182608 | 9.16 | 6 | 65.59 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 1420690.24 | 471606.53 | 3146 | 1. Unit No . 1 & 2 is on bar delivering an average load of 7.74 MW according to the available inflow. 2. At 16:30 hrs., the complex was shutdown as per the request of the contractor representative to rectify a fault in the lube oil system, which was in an emergency condition and not ready to start on auto mode through SCADA. After rectification, Unit # 01 was synchronized with the system at 17:20 hrs. and its load was gradually increased to 5MW, while Unit # 02 was synchronized at 17:27 hrs. and its load was gradually increased to 3.5 MW as per available hydrology. 3. At 23:23 hrs. Unit # 02 was shutdown due to continuous head drop caused by trash rack choking. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-03 | 2026 | 8 | 3 | Koto HPS | 40.8 | 26.73 | 20.01 | 480123 | 478823 | 65.8 | 61.78 | 49.03 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 3945501.52 | 3494421.06 | 1300 | Units 1 and 2 remained operational with an average plant load of 20.01 MW based on available inflow. Power generation was constrained due to intake choking, the shutdown of Unit 2 from 01:27 to 10:14 hrs, and subsequent trash rack cleaning. Unit 3 has been shut down since June 17, 2026, due to an ongoing PLC/communication issue. TRCM unavailability remains an active issue. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-03 | 2026 | 8 | 3 | Machai HPS | 2.6 | 0.9 | 0.67 | 16228 | 15356 | 25.3 | 15 | 26.01 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 71727.88 | 106680.22 | 872 | Unit tripped at 2018 & 2106 hrs due to line tripping while synced back at 2025 & 2115 hrs. Low Plant Factor due to recent heavy rainfall and irrigation department maintained reduced canal discharge in accordance with the demand of XEN Swabi irrigation Division. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-08-03 | 2026 | 8 | 3 | Malakand-3 HPS | 81 | 65 | 55.91 | 1341956 | 1329540 | 51 | 40.58 | 69.03 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3806074.16 | 1442824.81 | 12416 | Unit #01 was desynchronized at 12:12 Hrs dated:03-08-2026 for cleaning of the wicket gates and spiral case and removal of accumulated garbage/debris. Cleaning and debris removal were completed, and Unit #01 was synchronized with the system at 16:35 Hrs dated:03-08-2026 As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-03 | 2026 | 8 | 3 | Pehur HPS | 18 | 11.21 | 9.36 | 224700 | 218000 | 18.39 | 17 | 52.01 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 821206 | 238414.65 | 6700 | . | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-03 | 2026 | 8 | 3 | Reshun HPS | 4.2 | 2.59 | 1.29 | 29000 | 28700 | 2.43 | 1.77 | 28.77 | 13.48 | 100 | 45 | 100800 | 1358784 | 386876 | 971908 | 300 | at 18:20hrs a heavy flood occurred in Lotshal Gol Nala, due to accumulation of heavy boulders and debris in the Intake Gate No. I the diversion of water to the power house completely is suspended. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-08-04 | 2026 | 8 | 4 | Daral Khwar HPS | 36.6 | 35.3 | 29.9 | 716760 | 713960 | 15.6 | 11.94 | 81.6 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 5903235.47 | 732742.08 | 2800 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 29.9 MW according to the available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-04 | 2026 | 8 | 4 | Jabori HPS | 10.2 | 6 | 2.74 | 65695 | 64560 | 9.93 | 2.15 | 26.84 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 368585.95 | 1029026.21 | 1135 | 1- Unit 01 delivered an average load equals to 2.74 MW to the national grid according to the prevailing system constraints. 2- Unit 01 was synchronized at 1057 hrs after flushing one section of the sand trap. The other section of the sand trap is completely filled with silt and could not be emptied by flushing. Consequently, Unit 02 remained shut down. 3- The trash rack becomes choked whenever there is heavy rainfall due to the increased inflow of debris. Cleaning the trash rack is not possible during periods of high water flow, which adversely affects plant operation. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-04 | 2026 | 8 | 4 | Karora HPS | 11.8 | 10.26 | 6.25 | 150011 | 147292 | 9.16 | 5.08 | 52.97 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 1145931.76 | 746365.01 | 2719 | 1. Unit No . 1 & 2 is on bar delivering an average load of 6.25 MW according to the available inflow. 2.The Plant was completely shut down for the cleaning of Intake trash rack at 11:00 hrs. After completion of the cleaning, Unit # 01 was started and synchronized with system at 12:46 hrs. and load gradually increased to 5.5 MW, similarly unit 02 was synchronized with grid at 13:03 hrs. and load was gradually increased to 4 MW as per available hydrology 3. Energy generation remained below the target due to lower-than-expected hydrological flows. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-04 | 2026 | 8 | 4 | Koto HPS | 40.8 | 26.45 | 18.41 | 441762 | 440502 | 65.8 | 56.84 | 45.11 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 3629736.48 | 3810186.1 | 1260 | Units 1 and 2 remained operational with an average plant load of 18.41 MW. Total plant shutdown from 10:49 to 15:55 (5h 06m) for complete manual cleaning of the intake trash racks resulted in reduced generation. The extended duration was due to the non-availability of the Trash Rack Cleaning Machine (TRCM). Moreover unit 3 has been shut down since June 17, 2026, due to an ongoing Communication/PLC issue. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-04 | 2026 | 8 | 4 | Machai HPS | 2.6 | 0.88 | 0.61 | 15676 | 14828 | 25.3 | 15 | 25.12 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 69261.59 | 109146.5 | 848 | Unit tripped due to reverse power 6 times while synced back with system. Due to recent heavy rainfall the irrigation department maintained reduced canal discharge in accordance with the demand of XEN Swabi irrigation Division. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-08-04 | 2026 | 8 | 4 | Malakand-3 HPS | 81 | 65 | 58.43 | 1402388 | 1390170 | 51 | 40.59 | 72.14 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3979639.66 | 1269259.31 | 12218 | Unit #01 desynchronized from the system at 21:25 Hrs. dated:04-08-2026 due to vibration in the Turbine Guide Bearing. Unit# 01 synchronized with the system at 23:11 Hrs. dated: 04-08-2026. As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-04 | 2026 | 8 | 4 | Pehur HPS | 18 | 8.79 | 8.65 | 207600 | 202000 | 18.39 | 13 | 48.06 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 760934 | 298686.65 | 5600 | Plant remained operational throughout 24 hours as per available hydrology. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-04 | 2026 | 8 | 4 | Reshun HPS | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.48 | 100 | 45 | 100800 | 1358784 | 0 | 1358784 | 0 | due to flood occurred at Intake, the supply of water to the powerhouse has been blocked due to accumulation of debris and heavy boulders in Gate No. 1. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-08-05 | 2026 | 8 | 5 | Daral Khwar HPS | 36.6 | 26.3 | 24.1 | 578800 | 576000 | 15.6 | 9.63 | 65.89 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 4762540.8 | 1873436.75 | 2800 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 24.1 MW according to the available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-05 | 2026 | 8 | 5 | Jabori HPS | 10.2 | 7 | 4 | 96105 | 94800 | 9.93 | 3.14 | 39.26 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 541232.16 | 856380 | 1305 | 1- Unit 01 delivered an average load equals to 4 MW to the national grid according to the prevailing system constraints. 2- Plant shutdown at 1712 hrs due to heavy rainfall and flooding in the catchment area. Consequently, the intake gate was closed to 80%, and the sand trap was put on flushing mode to remove the accumulated silt. 3- The one section of the sand trap is completely filled with silt and could not be emptied by flushing. Consequently, Unit 02 remained shut down. 4- The trash rack becomes choked whenever there is heavy rainfall due to the increased inflow of debris. Cleaning the trash rack is not possible during periods of high water flow, which adversely affects plant operation. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-05 | 2026 | 8 | 5 | Karora HPS | 11.8 | 9.49 | 6.5 | 156003 | 153636 | 9.16 | 4.87 | 55.09 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 1195288.08 | 697008.69 | 2367 | 1.Unit No . 1 & 2 is on bar delivering an average load of 6.50 MW according to the available inflow. 2.The intake site team informed that water is completely muddy and contain a large amount debris due to heavy rain intake site. Therefore the complex was shutdown to prevent damage to the plant. 3. After coordination with the weir site team when the water conditions become normal. At 23:16 hrs. Unit #02 synchronized with grid load gradually increased to 5.9 MW. 4. Energy generation remained below the target due to lower-than-expected hydrological flows. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-05 | 2026 | 8 | 5 | Koto HPS | 40.8 | 26.52 | 25.85 | 620406 | 619046 | 65.8 | 79.83 | 63.36 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 5100939.04 | 2338983.54 | 1360 | The actual daily inflow was recorded at 79.83 cumecs,The historical average of 65.80 cumecs. Due to the low hydrology, only Units 1 and 2 were operated at an average load of 25.85 MW, with a maximum capacity of 26.50 MW. Unit 3 remained on standby because of the water deficit and an unresolved starting issue. In addition, the Intake Trash Rack Cleaning Machine (TRCM) is not yet operational, and issues with the powerhouse cooling water strainers also persist. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-05 | 2026 | 8 | 5 | Machai HPS | 2.6 | 0.88 | 0.67 | 16380 | 15620 | 25.3 | 15 | 26.25 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 72961.02 | 105447.07 | 760 | Unit tripped 3 times due to reverse power & 1 time due to line tripping. Due to recent heavy rainfall the irrigation department maintained reduced canal discharge in accordance with the demand of XEN Swabi irrigation Division. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-08-05 | 2026 | 8 | 5 | Malakand-3 HPS | 81 | 62 | 54.01 | 1296151 | 1283490 | 51 | 37.37 | 66.67 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3674246.82 | 1574652.14 | 12661 | Unit 03 & 01 desynchronized from the system at 19:23hrs & 23:17hrs as per Canal Wire No. 492-7 dated 05-08-2026, received from SDO irrigation Dargai, due to reduction of water supply in the Main Canal to facilitate the search operation for a dead body at Shergar Jalala Kalpani. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-05 | 2026 | 8 | 5 | Pehur HPS | 18 | 8.78 | 8.7 | 208800 | 203000 | 18.39 | 14 | 48.33 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 764701 | 294919.65 | 5800 | Plant remained operational throughout 24 hours as per available hydrology. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-05 | 2026 | 8 | 5 | Reshun HPS | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.48 | 100 | 45 | 100800 | 1358784 | 0 | 1358784 | 0 | Due to flood occurred at Intake, the supply of water to the powerhouse has been blocked due to accumulation of debris and heavy boulders in Gate No. 1. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-08-06 | 2026 | 8 | 6 | Daral Khwar HPS | 36.6 | 22.1 | 21.3 | 511460 | 509060 | 15.6 | 8.51 | 58.23 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 4209060.8 | 2426916.75 | 2400 | 1. Unit No. 01, 02 and 03 were on bar delivering an average load equal to 21.3 MW according to the available hydrology and existing system constraints. 2. Unit No. 01 put on standby at 0920 Hrs due to low hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-06 | 2026 | 8 | 6 | Jabori HPS | 10.2 | 9 | 3.18 | 76407 | 75120 | 9.93 | 2.5 | 31.21 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 428875.1 | 968737.06 | 1287 | 1- Unit 01 and 02 delivered an average load equals to 3.18 MW to the national grid according to the prevailing system constraints. 2- Both units were synchronized at 0930 hrs after flushing of one section of sand trap. Cooling water pump 01 drops pressure at 1030 hrs to 0.9 bar. Attempts to restore its pressure were unsuccessful so pump 02 was started. At 1400 hrs both cooling water pumps pressure gradually decreased to 0.5 bar. Despite repeated efforts, pressure couldn't be restored to cool temperatures of both units, Consequently unit 02 was shutdown. 3- The one section of the sand trap is completely filled with silt and could not be emptied by flushing. 4- The trash rack becomes choked whenever there is heavy rainfall due to the increased inflow of debris. Cleaning the trash rack is not possible during periods of high water flow, which adversely affects plant operation. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-06 | 2026 | 8 | 6 | Karora HPS | 11.8 | 5.9 | 2.74 | 65791 | 64787 | 9.16 | 2.2 | 23.23 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 504042.86 | 1388253.91 | 1004 | 1. Unit No 2 is on bar delivering an average load of 2.74 MW according to the available inflow. 2. Unit #01 was not started due to insufficient cooling water flow and pressure. 3. At 11:27 hrs, Unit #02 was tripped due to the tripping of the Main Transformer No. 1, 11 kV side circuit breaker (CB11) and the bus coupler (K3Q1) caused by an instantaneous overvoltage. Prior to tripping, the GCC temperature reached the alarm level due to low cooling water flow and pressure, therefore the cleaning of Both cooling water strainers were carried out to restore the required cooling water flow and pressure, ensuring safe unit operation. 4. The Weir Site Team requested a complex shutdown at 12:48 hrs for sand trap cleaning, and the intake gate was closed. However, at 14:59 hrs, following heavy rainfall in the intake catchment area, a flash flood carrying muddy water reached the intake, consequently due the bad cwater conditions the machine were not put into operation. 5. During the shutdown, cleaning of the Unit #01 generator air cooler and both cooling water pumps was carried out. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-06 | 2026 | 8 | 6 | Koto HPS | 40.8 | 26.48 | 23.44 | 562543 | 561183 | 65.8 | 72.39 | 57.45 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 4624147.92 | 2815774.66 | 1360 | 1) Units 01 and 02 were operated at an average load of 23.44 MW, 2) Unit #03 is standby due to a communication/PLC issue.In addition, the Intake Trash Rack Cleaning Machine (TRCM) is not yet operational and issues with the powerhouse cooling water strainers also persist. 3)Unit#02 shutdown due to Intake Trash Rack cleaning at 16:15Hrs and resynchronized with grid at 18:07Hrs. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-06 | 2026 | 8 | 6 | Machai HPS | 2.6 | 1.19 | 0.81 | 18948 | 18084 | 25.3 | 16 | 30.37 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 84470.36 | 93937.73 | 864 | Unit tripped 2 times due to line tripping. Due to recent heavy rainfall the irrigation department maintained reduced canal discharge in accordance with the demand of XEN Swabi irrigation Division. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-08-06 | 2026 | 8 | 6 | Malakand-3 HPS | 81 | 44 | 29.52 | 708466 | 698470 | 51 | 19.94 | 36.44 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 1999510.07 | 3249388.9 | 9996 | Unit # 03 synchronized with the system at 14:50hrs after the water flow improved from the Irrigation Department, Unit # 01 start pulse was given at 22:30hrs after the restoration of inflow by the Irrigation Department. An abnormal sound was observed from the turbine guide bearing during startup therefore, the unit was emergency shut down for further inspection, while two units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-06 | 2026 | 8 | 6 | Pehur HPS | 18 | 10.53 | 8.53 | 204800 | 199000 | 18.39 | 13 | 47.41 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 749633 | 309987.65 | 5800 | Plant remained operational throughout 24 hours with restricted outflow as per instructions of irrigation SDO. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-06 | 2026 | 8 | 6 | Reshun HPS | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.48 | 100 | 45 | 100800 | 1358784 | 0 | 1358784 | 0 | Due to flood occurred at Intake, the supply of water to the powerhouse has been blocked due to accumulation of debris and heavy boulders in Gate No. 1. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-08-07 | 2026 | 8 | 7 | Daral Khwar HPS | 36.6 | 21.1 | 20.1 | 482240 | 480240 | 15.6 | 8.03 | 54.9 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 3970768.39 | 2665209.16 | 2000 | Unit No. 01, 02 and 03 were on bar delivering an average load equal to 20.1 MW according to the available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-07 | 2026 | 8 | 7 | Jabori HPS | 10.2 | 7 | 3.96 | 95064 | 93600 | 9.93 | 3.11 | 38.83 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 534381.12 | 863231.04 | 1464 | 1- Unit 01 and 02 delivered an average load equals to 3.96 MW to the national grid according to the prevailing system constraints. 2- PTW # 35/2026 issued to contractor for inspection of tailrace of unit 01 and 02 as cooling water pumps were unable to build the required pressure. Plant was shutdown at 1129 Hrs. Inspection of tailrace, non return valve on cooling water line, impeller of both pumps were carried out and found satisfactory. 3- The one section of the sand trap is completely filled with silt and could not be emptied by flushing. 4- The trash rack becomes choked whenever there is heavy rainfall due to the inflow of debris. Cleaning the trash rack is not possible during periods of high water flow, which adversely affects plant operation. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-07 | 2026 | 8 | 7 | Karora HPS | 11.8 | 8.5 | 6.6 | 158512 | 155501 | 9.16 | 5.08 | 55.97 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 1209797.78 | 682498.99 | 3011 | 1. Unit No 1 & 2 are on bar delivering an average load of 6.60 MW according to the available inflow. 2. After the water conditions normalized following the flash flood, Unit #01 was synchronized with the system at 01:01 hrs and its load was gradually increased to 5.5 MW. Subsequently, Unit #02 was synchronized at 01:08 hrs and load was gradually increased to 3 MW, in accordance with the available hydrology. 3. At 18:40 hrs, Unit #02 was shut down due to choking of the intake trash rack. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-07 | 2026 | 8 | 7 | Koto HPS | 40.8 | 26.38 | 18.98 | 455525 | 454185 | 65.8 | 58.62 | 46.52 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 3742484.4 | 3697438.18 | 1340 | 1) Units 01 and 02 were operated at an average load of 18.98 MW, 2) Unit #03 is standby due to a communication/PLC issue.In addition, the Intake Trash Rack Cleaning Machine (TRCM) is not yet operational and issues with the powerhouse cooling water strainers also persist. 3)Unit#02 shutdown due to Intake Trash Rack cleaning at 07:28Hrs and resynchronized with grid at 11:34Hrs. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-07 | 2026 | 8 | 7 | Machai HPS | 2.6 | 1.56 | 1.07 | 24244 | 23408 | 24 | 16 | 38.85 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 109338.77 | 69069.32 | 836 | Unit tripped 07 times due to 11 KV line tripping. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-08-07 | 2026 | 8 | 7 | Malakand-3 HPS | 81 | 58 | 44.87 | 1076971 | 1065780 | 51 | 37.41 | 55.4 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3051008.41 | 2197890.56 | 11191 | Unit #01 synchronized with the system at 21:08 ,dated:07.08.2026 after rectification of fault, As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-07 | 2026 | 8 | 7 | Pehur HPS | 18 | 10.65 | 4.01 | 196400 | 189000 | 18.39 | 13 | 45.46 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 711963 | 347657.65 | 7400 | Plant operational 24 hrs with restricted discharge. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-07 | 2026 | 8 | 7 | Reshun HPS | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.48 | 100 | 45 | 100800 | 1358784 | 0 | 1358784 | 0 | Due to flood occurred at Intake, the supply of water to the powerhouse has been blocked due to accumulation of debris and heavy boulders in Gate No. 1. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-08-08 | 2026 | 8 | 8 | Daral Khwar HPS | 36.6 | 21 | 19.7 | 472790 | 471190 | 15.6 | 7.88 | 53.82 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 3895940.28 | 2740037.27 | 1600 | 1. Units No. 02 and 03 were on bar delivering an average load equal to 19.7 MW according to the available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-08 | 2026 | 8 | 8 | Jabori HPS | 10.2 | 8 | 6.9 | 165668 | 163440 | 9.93 | 5.41 | 67.67 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 933111.65 | 464500.51 | 2228 | 1- Unit 01 and 02 delivered an average load equals to 6.9 MW to the national grid according to the prevailing system constraints. 2- A significant issue persists in the coolimg water system which adversely affects plant operation. Both cooling watwr pumps are unable to maintain the required flow/pressure. 3- The one section of the sand trap is completely filled with silt and could not be emptied by flushing. 4- The trash rack becomes choked whenever there is heavy rainfall due to the inflow of debris. Cleaning the trash rack is not possible during periods of high water flow, which adversely affects plant operation. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-08 | 2026 | 8 | 8 | Karora HPS | 11.8 | 9.83 | 4.99 | 119835 | 117427 | 9.16 | 3.76 | 42.31 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 913582.06 | 978714.71 | 2408 | 1) Unit No 1 & 2 were on bar delivering an average load of 4.99 MW according to the available inflow. 2) Complex shutdown for intake trash rack and intake pond cleaning at 17:20 Hrs. 3) After cleaning of intake trash rack and intake pond, Unit # 01 was synchronized with system at 20:47 Hrs and load was gradually increased to 5.9 MW. Subsequently Unit # 02 was synchronized with system at 20:48 hrs with load of 3 MW. 4) At 23:49 hrs, a complex shutdown was carried out for physical inspection of the MIV floor, where water was observed. Upon inspection, no leakage was found from the GCC or cooling water pipes. The water was traced to the drainage pit. The drainage pit pump panel was found to have a base relay issue. The contractor’s representative was advised to rectify the relay issue by morning. Following the inspection, both units were found ready for start-up. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-08 | 2026 | 8 | 8 | Koto HPS | 40.8 | 21.08 | 19.08 | 455208 | 453968 | 65.8 | 65.02 | 46.49 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 3740696.32 | 3699226.26 | 1240 | 1) Units 01 and 02 were operated at an average load of 19.08 MW, 2) Unit #03 is standby due to a communication/PLC issue.In addition, the Intake Trash Rack Cleaning Machine (TRCM) is not yet operational and issues with the powerhouse cooling water strainers also persist. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-08 | 2026 | 8 | 8 | Machai HPS | 2.6 | 1.28 | 1.2 | 29636 | 28644 | 22 | 18 | 47.49 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 133796.12 | 44611.97 | 992 | Smooth operation as per available inflow. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-08-08 | 2026 | 8 | 8 | Malakand-3 HPS | 81 | 57 | 52.76 | 1266178 | 1253850 | 51 | 35.16 | 65.13 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3589396.4 | 1659502.57 | 12328 | The shortfall is primarily due to less hydrology. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-08 | 2026 | 8 | 8 | Pehur HPS | 18 | 8.08 | 6.85 | 164600 | 161000 | 18.39 | 11 | 38.1 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 606487 | 453133.65 | 3600 | Plant remained operational throughout 24 hours with restricted outflow as per instructions of irrigation SDO. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-08 | 2026 | 8 | 8 | Reshun HPS | 4.2 | 0.81 | 237 | 5000 | 4740 | 2.6 | 0.31 | 4.96 | 13.48 | 100 | 45 | 100800 | 1358784 | 63895.2 | 1294888.8 | 260 | Diversion work at Gate No.1 is in progress. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-08-09 | 2026 | 8 | 9 | Daral Khwar HPS | 36.6 | 21.1 | 18.6 | 446960 | 444960 | 15.6 | 7.44 | 50.88 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 3679062.77 | 2956914.78 | 2000 | 1. Units No. 02 and 03 were on bar delivering an average load equal to 18.6 MW according to the available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-09 | 2026 | 8 | 9 | Jabori HPS | 10.2 | 8.2 | 7.64 | 183384 | 180960 | 9.93 | 5.99 | 74.91 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 1033136.83 | 364475.33 | 2424 | 1- Unit 01 and 02 delivered an average load equals to 7.6 MW to the national grid according to the prevailing system constraints. 2- A significant issue persists in the coolimg water system which adversely affects plant operation. Both cooling water pumps are unable to maintain the required flow/pressure. 3- The one section of the sand trap is completely filled with silt and could not be emptied by flushing. 4- The trash rack becomes choked whenever there is heavy rainfall due to the inflow of debris. Cleaning the trash rack is not possible during periods of high water flow, which adversely affects plant operation. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-09 | 2026 | 8 | 9 | Karora HPS | 11.8 | 10.13 | 9.74 | 233724 | 230660 | 9.16 | 7.73 | 82.53 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 1794534.8 | 97761.97 | 3064 | 1) Unit No 1 & 2 is on bar delivering an average load of 9.74 MW according to the available inflow. 2) Unit No. 02 was synchronized with the system at 00:03 hrs with an initial load of 3.0 MW. Unit No. 01 was synchronized with the system at 00:08 hrs, and its load was gradually increased to 5.9 MW. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-09 | 2026 | 8 | 9 | Koto HPS | 40.8 | 21.05 | 17.15 | 407435 | 406195 | 65.8 | 59.72 | 41.61 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 3347046.8 | 4092875.78 | 1240 | 1) Units 01 and 02 were operated at an average load of 17.15MW, 2) Unit #03 is standby due to a communication/PLC issue.In addition, the Intake Trash Rack Cleaning Machine (TRCM) is not yet operational and issues with the powerhouse cooling water strainers also persist. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-09 | 2026 | 8 | 9 | Machai HPS | 2.6 | 1.35 | 1.19 | 29180 | 28380 | 24 | 18 | 46.76 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 132562.98 | 45845.11 | 800 | Unit tripped at 0020 hrs. with 11 KV line tripping; 11 KV line restored at 0022 hrs., while unit synched at 0025 hrs.. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-08-09 | 2026 | 8 | 9 | Malakand-3 HPS | 81 | 57 | 50.67 | 1216094 | 1204210 | 51 | 33.52 | 62.56 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3447291.97 | 1801607 | 11884 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-09 | 2026 | 8 | 9 | Pehur HPS | 18 | 10.9 | 8.6 | 207200 | 201000 | 18.39 | 13 | 47.96 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 757167 | 302453.65 | 6200 | Plant remained shut down for 0050 hrs due to failure of 132kv supply. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-09 | 2026 | 8 | 9 | Reshun HPS | 4.2 | 0.81 | 0.64 | 15000 | 15695 | 2.6 | 0.93 | 14.88 | 13.48 | 100 | 45 | 100800 | 1358784 | 211568.6 | 1147215.4 | 695 | Diversion work of flow to the Plant at Gate No.1 is in progress. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor; CHECK: Net > Units (source me verify karein) | Generation_Data.xlsx
2026-08-10 | 2026 | 8 | 10 | Daral Khwar HPS | 36.6 | 17.6 | 17.2 | 411890 | 409490 | 15.6 | 6.85 | 46.89 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 3385786.17 | 3250191.38 | 2400 | Unit No. 02 and 03 were on bar delivering an average load equal to 17.2 MW according to the available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-10 | 2026 | 8 | 10 | Jabori HPS | 10.2 | 7.7 | 6.78 | 162624 | 160080 | 9.93 | 5.31 | 66.43 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 913928.74 | 483683.42 | 2544 | 1- Unit 01 and 02 delivered an average load equals to 6.78 MW to the national grid according to the prevailing system constraints. 2- A significant issue persists in the coolimg water system which adversely affects plant operation. Both cooling water pumps are unable to maintain the required flow/pressure. 3- The one section of the sand trap is completely filled with silt and could not be emptied by flushing. 4- The trash rack becomes choked whenever there is heavy rainfall due to the inflow of debris. Cleaning the trash rack is not possible during periods of high water flow, which adversely affects plant operation. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-10 | 2026 | 8 | 10 | Karora HPS | 11.8 | 9.88 | 8.94 | 214663 | 211467 | 9.16 | 7 | 75.8 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 1645213.26 | 247083.51 | 3196 | 1.Unit No 1 & 2 is on bar delivering an average load of 8.94 MW according to the available inflow. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-10 | 2026 | 8 | 10 | Koto HPS | 40.8 | 21.35 | 14.02 | 336655 | 335255 | 65.8 | 56.66 | 34.38 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 2762501.2 | 4677421.38 | 1400 | 1) Units 01 and 02 were operated at an average load of 14.02MW, 2) Unit #03 is standby due to a communication/PLC issue.In addition, the Intake Trash Rack Cleaning Machine (TRCM) is not yet operational and issues with the powerhouse cooling water strainers also persist. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-10 | 2026 | 8 | 10 | Machai HPS | 2.6 | 1.54 | 1.12 | 28224 | 27152 | 24 | 20 | 45.23 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 126826.99 | 51581.1 | 1072 | Unit tripped at 2055 hrs. with 11 KV line tripping; 11 KV line restored at 2105 hrs., while unit synched at 2108 hrs.. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-08-10 | 2026 | 8 | 10 | Malakand-3 HPS | 81 | 53 | 47.83 | 1147836 | 1135270 | 51 | 32.67 | 59.05 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3249937.43 | 1998961.54 | 12566 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-10 | 2026 | 8 | 10 | Pehur HPS | 18 | 11.82 | 11.37 | 273000 | 265000 | 18.39 | 18 | 63.19 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 998255 | 61365.65 | 8000 | Plant remained operational throughout 24 hours as per available hydrology. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-10 | 2026 | 8 | 10 | Reshun HPS | 4.2 | 0.77 | 0.6 | 13000 | 12305 | 2.6 | 0.79 | 12.9 | 13.48 | 100 | 45 | 100800 | 1358784 | 165871.4 | 1192912.6 | 695 | shortage of water flow due to accumulation of boulders and debris at Gate No.1. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-08-11 | 2026 | 8 | 11 | Daral Khwar HPS | 36.6 | 25 | 18.4 | 441500 | 439500 | 15.6 | 7.35 | 50.26 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 3633917.85 | 3002059.7 | 2000 | 1: Unit No. 02 and 03 were on bar delivering an average load equal to 18.4 MW according to the available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-11 | 2026 | 8 | 11 | Jabori HPS | 10.2 | 7.9 | 6.91 | 165793 | 163220 | 8.94 | 5.42 | 67.73 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 931855.62 | 465756.54 | 2573 | 1- Unit 01 and 02 delivered an average load equals to 6.91 MW to the national grid according to the prevailing system constraints. 2- A significant issue persists in the coolimg water system which adversely affects plant operation. Both cooling water pumps are unable to maintain the required flow/pressure. 3- The one section of the sand trap is completely filled with silt and could not be emptied by flushing. 4- The trash rack becomes choked whenever there is heavy rainfall due to the inflow of debris. Cleaning the trash rack is not possible during periods of high water flow, which adversely affects plant operation. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-11 | 2026 | 8 | 11 | Karora HPS | 11.8 | 10.39 | 8.29 | 198927 | 195777 | 9.16 | 6.48 | 70.24 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 1523145.06 | 369151.71 | 3150 | Unit No 1 & 2 is on bar delivering an average load of 8.29MW according to the available inflow. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-11 | 2026 | 8 | 11 | Koto HPS | 40.8 | 14.9 | 13.19 | 316574 | 315254 | 65.8 | 40.74 | 32.33 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 2597692.96 | 4842229.62 | 1320 | Unit 1 and 2 on bar delivering an average load of 13.19 MW . Unit #03 is standby due to a communication/PLC issue. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-11 | 2026 | 8 | 11 | Machai HPS | 2.6 | 1.5 | 1.13 | 31048 | 29916 | 24 | 22 | 49.76 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 139737.64 | 38670.46 | 1132 | unit tripped at 0230,1445hrs due to revers power, while unit synched with system at 0238,1454hrs. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-08-11 | 2026 | 8 | 11 | Malakand-3 HPS | 81 | 54 | 49.95 | 1198773 | 1185500 | 51 | 32.21 | 61.67 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3393730.85 | 1855168.12 | 13273 | As per available hydrology from Irrigation Department all three units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-11 | 2026 | 8 | 11 | Pehur HPS | 18 | 11.9 | 11.73 | 281700 | 273000 | 18.39 | 18 | 65.21 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 1028391 | 31229.65 | 8700 | Plant remained operational throughout 24 hours as per available hydrology. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-11 | 2026 | 8 | 11 | Reshun HPS | 4.2 | 0.79 | 0.6 | 13000 | 12685 | 2.6 | 0.79 | 12.9 | 13.48 | 100 | 45 | 100800 | 1358784 | 170993.8 | 1187790.2 | 315 | boulders and debris accumulated in weir due to flood, the water flow cannot be fully divert to Plant. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-08-12 | 2026 | 8 | 12 | Daral Khwar HPS | 36.6 | 20 | 18 | 432500 | 430100 | 15.6 | 7.19 | 49.24 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 3556195.83 | 3079781.72 | 2400 | 1: Unit No. 02 and 03 were on bar delivering an average load equal to 18 MW according to the available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-12 | 2026 | 8 | 12 | Jabori HPS | 10.2 | 7.4 | 6.67 | 160037 | 157440 | 8.94 | 5.23 | 65.37 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 898856.45 | 498755.71 | 2597 | 1- Unit 01 and 02 delivered an average load equals to 6.67 MW to the national grid according to the prevailing system constraints. 2- A significant issue persists in the coolimg water system which adversely affects plant operation. Both cooling water pumps are unable to maintain the required flow/pressure. 3- The one section of the sand trap is completely filled with silt and could not be emptied by flushing. 4- The trash rack becomes choked whenever there is heavy rainfall due to the inflow of debris. Cleaning the trash rack is not possible during periods of high water flow, which adversely affects plant operation. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-12 | 2026 | 8 | 12 | Karora HPS | 11.8 | 9.89 | 6.72 | 161284 | 158722 | 9.16 | 5.55 | 56.95 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 1234857.16 | 657439.61 | 2562 | Unit No 1 & 2 is on bar delivering an average load of 6.72 MW according to the available inflow. The weir site operator informed that heavy rainfall had caused highly muddy water at the intake. To prevent excessive silt and debris from entering the water conveyance system, the intake channel gate was closed. Consequently, a controlled shutdown of the plant was carried out at 05:43 hrs. After the water quality at the intake improved, Unit #02 was started and synchronized with the system at 09:45 hrs. Subsequently, Unit #01 was started and synchronized with the system at 09:53 hrs. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-12 | 2026 | 8 | 12 | Koto HPS | 40.8 | 21.25 | 12.83 | 307827 | 306587 | 65.8 | 39.61 | 31.44 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 2526276.88 | 4913645.7 | 1240 | Unit 1 and 2 on bar delivering an average load of 12.83 MW . Unit #03 is standby due to a communication/PLC issue. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-12 | 2026 | 8 | 12 | Machai HPS | 2.6 | 1.43 | 0.56 | 13156 | 12672 | 24 | 18 | 21.08 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 59190.91 | 119217.18 | 484 | 1: Unit tripped at 1255, 0530, 0655 hrs due to Line tripping from Katlang grid due to stormy weather, line restored at 0327, 0544, 0658 while unit synched with system at 0339, 0553, 0707 hrs. 2: Unit tripped at 1126 hrs due to reverse power while synced back with system at 1137. Unit tripped at 1243 hrs due to line tripping from katlang because of PTW issued to work on Old katlang Line, line restored at 1420 while unit synced with system at 1430. 3: Unit tripped at 1540 due to tripping from katlang grid because of tripping on 132 KV line from Mardan line restored at 1627 while unit synced with system at 1633. 4: Unit precautionary shutdown occurred at 1931 Hrs due to auxiliary AC supply failure on the 200 kVA, 11 kV/400 V Auxiliary Transformer. Inspection under PTW confirmed missing Red (R) phase supply. Winding resistance tests indicated \approx 0\ \Omega on the Red phase, indicating a potential internal short circuit/winding fault. Unit remains shut down. Due to unavailable station maintenance staff, external technical experts have been engaged for diagnostic testing (IR, TTR, phase-to-phase checks) and necessary repair/replacement. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-08-12 | 2026 | 8 | 12 | Malakand-3 HPS | 81 | 54 | 49.72 | 1193284 | 1181160 | 51 | 32.26 | 61.38 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3381306.73 | 1867592.24 | 12124 | As per available hydrology all three units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-12 | 2026 | 8 | 12 | Pehur HPS | 18 | 12 | 8.4 | 202500 | 197000 | 18.39 | 13 | 46.88 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 742099 | 317521.65 | 5500 | Plant operational 24 hrs with restricted discharge. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-12 | 2026 | 8 | 12 | Reshun HPS | 4.2 | 3.02 | 0.69 | 15000 | 14710 | 2.6 | 0.91 | 14.88 | 13.48 | 100 | 45 | 100800 | 1358784 | 198290.8 | 1160493.2 | 290 | Removal works of bulders and gravels from the Intake Gate No.1 | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-08-13 | 2026 | 8 | 13 | Daral Khwar HPS | 36.6 | 16.7 | 16.2 | 389850 | 387850 | 15.6 | 6.49 | 44.38 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 3206860.16 | 3429117.39 | 2000 | Unit No. 02 and 03 were on bar delivering an average load equal to 16.2 MW according to the available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-13 | 2026 | 8 | 13 | Jabori HPS | 10.2 | 7.3 | 6.5 | 156048 | 153550 | 8.94 | 5.1 | 63.75 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 876647.66 | 520964.5 | 2498 | 1- Unit 01 and 02 delivered an average load equals to 6.5 MW to the national grid according to the available hydrology and prevailing system constraints. 2- A significant issue persists in the cooling water system which adversely affects plant operation. Both cooling water pumps are unable to maintain the required flow/pressure. 3- The one section of the sand trap is completely filled with silt and could not be emptied by flushing. 4- The trash rack becomes choked whenever there is heavy rainfall due to the inflow of debris. Cleaning the trash rack is not possible during periods of high water flow, which adversely affects plant operation. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-13 | 2026 | 8 | 13 | Karora HPS | 11.8 | 8.47 | 7.79 | 186858 | 183522 | 9.16 | 6.2 | 65.98 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 1427801.16 | 464495.61 | 3336 | Unit No 1 & 2 is on bar delivering an average load of 7.79 MW according to the available inflow. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-13 | 2026 | 8 | 13 | Koto HPS | 40.8 | 15.75 | 13.42 | 322034 | 320794 | 65.8 | 41.44 | 32.89 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 2643342.56 | 4796580.02 | 1240 | Unit 1 and 2 on bar delivering an average load of 13.42 MW, Unit #03 is standby due to a communication/PLC issue | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-13 | 2026 | 8 | 13 | Machai HPS | 2.6 | 1.17 | 0.49 | 11640 | 11044 | 15 | 18 | 18.65 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 51586.52 | 126821.57 | 596 | Unit was shutdown at 1931 hrs 12-08-2026 due to auxilary AC supply failure on the 200 KVA 11KV/ 400V auxilary transformer. After the faulty fuse was replaced, all pre-commissioning/safety checks were successfully completed, and the unit has been re-synchronized with the system at 1046 hrs. Unit tripped at 19:17, 19:59, and 20:34 hrs due to reverse power, while synced back with system at 19:23, 20:07, and 20:45 hrs respectively. Unit tripped due to 11 KV line tripping from Katlang grid at 23:16 hrs. The line was restored at 23:19 hrs, and the unit was synced back at 23:23 hrs. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-08-13 | 2026 | 8 | 13 | Malakand-3 HPS | 81 | 53 | 49.58 | 1189853 | 1177520 | 51 | 32.07 | 61.21 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3370886.5 | 1878012.46 | 12333 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-13 | 2026 | 8 | 13 | Pehur HPS | 18 | 11.95 | 11.51 | 276400 | 268000 | 18.39 | 17 | 63.98 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 1009556 | 50064.65 | 8400 | Plant remained operational throughout for 24 hrs. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-13 | 2026 | 8 | 13 | Reshun HPS | 4.2 | 2.67 | 1.86 | 44000 | 43670 | 2.8 | 2.69 | 43.65 | 13.48 | 100 | 45 | 100800 | 1358784 | 588671.6 | 770112.4 | 330 | Nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-08-14 | 2026 | 8 | 14 | Daral Khwar HPS | 36.6 | 30.6 | 10.2 | 245650 | 244450 | 15.6 | 4.09 | 27.97 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 2021185.94 | 4614791.61 | 1200 | 1: Units No.02 and 03 were on bar delivering an average load equal to 10.2 MW according to the available hydrology and existing system constraints. 2: "132 kV line tripped at 00.52 HRS dated 14-08-2026. From Madyan grid it was reported that line-04 breaker of DKHPC was tripped due to over current earth fault. DK team was sent to Madyan grid to confirm the situation. DK team reported from Madyan grid that as per instruction of RCC, DK line was isolated from system and try was given to restore the system, but madyan grid tripped again, indicating fault between Madyan Khwazakhela line/Madyan Grid. The PESCO team from Chakdara grid patrolled the line from khwazakhela to Madyan, while patrolling on our line was also carried out by our team in the morning. Ultimately, fault was detected on MYN-I (Khwazakhela to Madyan) breaker. PESCO team by-passed remaining two phases of their previously by-passed breaker to restore the system, as a stop gap arrangement, till August 17, 2026." 3: 132 kV line restored at 1237 Hrs. 4: Unit No. 3 and 2 synchronized at 1248 Hrs and 12 52 Hrs respectively. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-14 | 2026 | 8 | 14 | Jabori HPS | 10.2 | 8.3 | 6.33 | 151958 | 149550 | 8.94 | 4.97 | 62.07 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 853810.86 | 543801.3 | 2408 | 1- Unit 01 and 02 delivered an average load equals to 6.33 MW to the national grid according to the available hydrology and prevailing system constraints. 2- A significant issue persists in the cooling water system which adversely affects plant operation. Both cooling water pumps are unable to maintain the required flow/pressure. 3- The one section of the sand trap is completely filled with silt and could not be emptied by flushing. 4- The trash rack becomes choked whenever there is heavy rainfall due to the inflow of debris. Cleaning the trash rack is not possible during periods of high water flow, which adversely affects plant operation. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-14 | 2026 | 8 | 14 | Karora HPS | 11.8 | 9.7 | 6.43 | 154229 | 151272 | 9.16 | 4.85 | 54.46 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 1176896.16 | 715400.61 | 2957 | Unit No 1 & 2 is on bar delivering an average load of 6.43 MW according to the available inflow. At 18:41 hrs, Unit #01 and Unit #02 tripped due to tripping of the 132 kV transmission line. The 132 kV line was restored at 19:32 hrs. Following restoration of the 132 kV line, the start sequence for Unit #01 was attempted twice but failed. At 20:35 hrs, Unit #01 was started through the step-by-step sequence and successfully reached FSNL. At 20:31 hrs, the weir site operator informed the CCR that heavy rainfall had caused muddy water at the intake and requested plant shutdown. Accordingly, the stop sequence for Unit #01 was initiated but failed. Consequently, the emergency shutdown was applied to stop the unit safely. "At 22:24 hrs, a Rotor Earth Fault Protection alarm for Unit #01 was observed on the SCADA alarm screen. Upon inspection of the protection relay, the corresponding alarm was also found active. An attempt was made to reset the alarm but failed to reset. Accordingly, a TR was logged, and the EPC Contractor’s representative present at site was informed for necessary rectification". | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-14 | 2026 | 8 | 14 | Koto HPS | 40.8 | 20.45 | 12.84 | 308266 | 307026 | 65.8 | 39.67 | 31.48 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 2529894.24 | 4910028.34 | 1240 | Due to low hydrology, the plant experienced reduced overall generation with an average load of 12.84 MW, running Unit No. 1 according to available head and synchronizing Unit No. 2 at 21:28 hrs after rain-induced water inflow and head improvement. All intake under sluice gates were opened from 16:38 to 18:30 hrs (1 hr 52 min) to assist Rescue 1122 in searching for a dead body in the Panjkora River, resulting in a further load reduction and subsequent total plant shutdown from 18:45 to 19:25 hrs. Additionally, the Chinese technical team resolved Unit No. 3’s PLC communication issue; the unit was successfully run on FSNL at 09:40 hrs, but was returned to standby at 18:31 hrs due to limited water inflow. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-14 | 2026 | 8 | 14 | Machai HPS | 2.6 | 1.11 | 0.77 | 19004 | 18260 | 15 | 18 | 30.46 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 85292.46 | 93115.63 | 744 | Unit tripped at 1023, 2110, 2159, 2249, and 2323 hrs due to reverse power, and was synced back with the system at 1035, 2116, 2205, 2256, and 2340 hrs. Unit tripped due to 11 KV line tripping from Katlang grid at 0448 and 1116 hrs. Line was restored at 0708 and 1118 hrs, and synced back at 0711 and 1125 hrs | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-08-14 | 2026 | 8 | 14 | Malakand-3 HPS | 81 | 54 | 49.5 | 1188061 | 1176630 | 51 | 32.08 | 61.11 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3368338.7 | 1880560.27 | 11431 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-14 | 2026 | 8 | 14 | Pehur HPS | 18 | 11.73 | 8.94 | 214700 | 209000 | 18.39 | 13 | 49.7 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 787303 | 272317.65 | 5700 | Plant remained operational with restricted flow. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-14 | 2026 | 8 | 14 | Reshun HPS | 4.2 | 2.63 | 1.93 | 43000 | 42758 | 2.7 | 2.57 | 42.66 | 13.48 | 100 | 45 | 100800 | 1358784 | 576377.84 | 782406.16 | 242 | Nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-08-15 | 2026 | 8 | 15 | Daral Khwar HPS | 36.6 | 29.3 | 21.1 | 507140 | 505140 | 15.6 | 8.45 | 57.73 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 4176649.06 | 2459328.49 | 2000 | 1: Unit No. 02 and 03 were on bar delivering an average load equal to 21.1 MW according to the available hydrology and existing system constraints. 2: Unit No. 01 stopped at 0115 Hrs due to low hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-15 | 2026 | 8 | 15 | Jabori HPS | 10.2 | 7.3 | 6.31 | 151389 | 149050 | 8.94 | 4.95 | 61.84 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 850956.26 | 546655.9 | 2339 | 1- Unit 01 and 02 delivered an average load equals to 6.31 MW to the national grid according to the available hydrology and prevailing system constraints. 2- A significant issue persists in the cooling water system which adversely affects plant operation. Both cooling water pumps are unable to maintain the required flow/pressure. 3- The one section of the sand trap is completely filled with silt and could not be emptied by flushing. 4- The trash rack becomes choked whenever there is heavy rainfall due to the inflow of debris. Cleaning the trash rack is not possible during periods of high water flow, which adversely affects plant operation. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-15 | 2026 | 8 | 15 | Karora HPS | 11.8 | 5.91 | 4.77 | 114488 | 112674 | 6.16 | 3.03 | 40.43 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 876603.72 | 1015693.05 | 1814 | Unit No 1 & 2 is on bar delivering an average load of 4.77 MW according to the available inflow. At 22:44 hrs, cooling water pressure dropped from 2.9 bar to 0.6 bar Upon investigation, it was found that Cooling Water Pump #1 had tripped and was in fault condition . Consequently, Unit #02 was tripped on low cooling water pressure at 22:50 hrs. The pump phase currents had been checked in evening time by the EPC representative in the presence of the Employer and were found normal. However, during present inspection, Cooling Water Pump #1 was found overheated and kept out of service pending for further invetigation . TR No. 71/2026 was logged for further corrective action. Currently only one cooling water pump remained in service, pressure remained low at approximately 0.6 bar. The relevant valves were adjusted, increasing the pressure to 1.7 bar. Subsequently, Unit #02 was started and successfully synchronized with the grid at 23:24 hrs. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-15 | 2026 | 8 | 15 | Koto HPS | 40.8 | 23.77 | 15.35 | 368424 | 367224 | 65.8 | 47.41 | 37.62 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 3025925.76 | 4413996.82 | 1200 | Units 1 & 2 operated on-bar, delivering a combined average load of 15.35 MW, while Unit 3 remained on standby due to insufficient hydrology. Undersluice gates were opened to lower the intake water level and facilitate trash racks cleaning, resulting in a plant shutdown from 12:02 to 13:09 hrs. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-15 | 2026 | 8 | 15 | Machai HPS | 2.6 | 1.02 | 0.99 | 21620 | 20812 | 15 | 18 | 34.65 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 97212.85 | 81195.24 | 808 | Unit tripped at 0543, 0926, 1347, 1427, 2025, and 2310 hrs due to reverse power, while it was synced back with the system at 0553, 0954, 1354, 1440, 2025, and 2310 hrs. Unit tripped due to 11 KV line tripping from Katlang grid at 1705 hrs. Line was restored at 1746 hrs, and the unit was synced back at 1751 hrs. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-08-15 | 2026 | 8 | 15 | Malakand-3 HPS | 81 | 55 | 50.59 | 1214276 | 1202770 | 51 | 32.83 | 62.46 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3443169.68 | 1805729.29 | 11506 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-15 | 2026 | 8 | 15 | Pehur HPS | 18 | 11.87 | 10.48 | 251600 | 245000 | 18.39 | 15 | 58.24 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 922915 | 136705.65 | 6600 | Plant remained operational throughout 24 hrs. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-15 | 2026 | 8 | 15 | Reshun HPS | 4.2 | 2.46 | 1.75 | 43000 | 42770 | 2.7 | 2.57 | 42.66 | 13.48 | 100 | 45 | 100800 | 1358784 | 576539.6 | 782244.4 | 230 | line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-08-16 | 2026 | 8 | 16 | Daral Khwar HPS | 36.6 | 19 | 18.2 | 436700 | 434700 | 15.6 | 7.27 | 49.72 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 3594230.01 | 3041747.54 | 2000 | Unit No. 02 and 03 were on bar delivering an average load equal to 18.2 MW according to the available hydrology and existing system constraints. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-16 | 2026 | 8 | 16 | Jabori HPS | 10.2 | 7.3 | 4.66 | 111927 | 109960 | 8.94 | 3.66 | 45.72 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 627783.63 | 769828.53 | 1967 | 1- Unit 01 and 02 delivered an average load equals to 4.66 MW to the national grid according to the available hydrology and prevailing system constraints. 2- A significant issue persists in the cooling water system which adversely affects plant operation. Both cooling water pumps are unable to maintain the required flow/pressure. 3- The one section of the sand trap is completely filled with silt and could not be emptied by flushing. 4- The trash rack becomes choked whenever there is heavy rainfall due to the inflow of debris. Cleaning the trash rack is not possible during periods of high water flow, which adversely affects plant operation. 5- plant was shutdown at 1905 Hrs due to heavy rainfall and flooding in the catchment area. Consequently the intake gate was closed 80% and the sand trap was put on flushing mode to remove the accumulated silt. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-16 | 2026 | 8 | 16 | Karora HPS | 11.8 | 5.93 | 5.86 | 140583 | 138656 | 9.16 | 4.84 | 49.64 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 1078743.68 | 813553.09 | 1927 | 1. Unit No. 2 is on bar delivering an average load of 5.86 MW according to the available inflow. 2. At 09:20 hrs., the EPC Contractor dismantled Cooling Water Pump No. 01 and removed it from service for repair and maintenance. 3. Currently, only one cooling water pump remains in service. Following adjustment of the relevant valves, the cooling water pressure has stabilized at 1.9 bar. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-16 | 2026 | 8 | 16 | Koto HPS | 40.8 | 21.38 | 17.03 | 408607 | 407387 | 65.8 | 52.58 | 41.73 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 3356868.88 | 4083053.7 | 1220 | Units 1 and 2 operated on-bar, delivering a combined average load of 17.03 MW, while Unit 3 remained on standby due to insufficient hydrology. Overall plant generation remained constrained due to low water inflow. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-16 | 2026 | 8 | 16 | Machai HPS | 2.6 | 0.98 | 0.61 | 16228 | 15488 | 15 | 18 | 26.01 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 72344.45 | 106063.64 | 740 | 1) unit tripped at 0120,0805hrs due to 11kv line tripe, 11kv line restored at 0204,0855hrs, unit synched with system at 0214,0906hrs. 2) unit tripped at 0249,0553,0743,1512,1731hrs due to reverse power, while unit synched with the system at 0309,0736,0750,1527,1746hrs. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-08-16 | 2026 | 8 | 16 | Malakand-3 HPS | 81 | 54 | 49.31 | 1183335 | 1171780 | 51 | 32.04 | 60.87 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3354454.61 | 1894444.36 | 11555 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-16 | 2026 | 8 | 16 | Pehur HPS | 18 | 11.86 | 11.09 | 266100 | 258000 | 18.39 | 16 | 61.6 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 971886 | 87734.65 | 8100 | Plant remained operational throughout 24 hrs with restricted flow. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-16 | 2026 | 8 | 16 | Reshun HPS | 4.2 | 2.53 | 2 | 47000 | 46750 | 2.95 | 2.87 | 46.63 | 13.48 | 100 | 45 | 100800 | 1358784 | 630190 | 728594 | 250 | nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-08-17 | 2026 | 8 | 17 | Daral Khwar HPS | 36.6 | 17 | 6 | 143680 | 142880 | 15.6 | 2.39 | 16.36 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 1181374.7 | 5454602.84 | 800 | 1: Unit No. 02 and 03 were on bar delivering an average load equal to 6 MW according to the available hydrology and existing system constraints. 2: The plant was shutdown at 08:01HRS on 17-08-2026 against PESCO shutdown approval No. 2044-54/CE(O&M)/Distt:/Shutdowns dated 6-08-2026 (NOC No. 500/RE(O&M)/DKHPC) for replacement of PESCO 132 kV damaged by-passed breaker (MYN-1) Madyan Grid Station. The shutdown was extended beyond the anticipated time (8 HRS) due to fault tracing/ testing activities by PESCO P&I team. 3: During the shutdown period maintenance activities were carried out at DK weir site including flushing of weir, gravel trap, sand trap, cleaning trash racks, maintenance on sandtrap flushing gates and monthly preventive maintenance on all 3 units at powerhouse including seals replacement of servomotor of unit 2. 4: The 132 kV supply was restored at 23:30 HRS (17-08-26). Unit 3 and 2 synchronised with the grid at 23:40 and 23:42 HRS respectively. Plant operational at 17 MW as per available hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-17 | 2026 | 8 | 17 | Jabori HPS | 10.2 | 8.4 | 4.15 | 99655 | 97970 | 8.94 | 3.26 | 40.71 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 559330.32 | 838281.84 | 1685 | 1- Unit 01 and 02 delivered an average load equals to 4.15 MW to the national grid according to the available hydrology and prevailing system constraints. 2- Unit 02 and unit 01 were synchronized at 0811 Hrs and 0912 Hrs respectively after muddy rainwater subsided. 3- A significant issue persists in the cooling water system which adversely affects plant operation. Both cooling water pumps are unable to maintain the required flow/pressure. 4- The one section of the sand trap is completely filled with silt and could not be emptied by flushing. 5- The trash rack becomes choked whenever there is heavy rainfall due to the inflow of debris. Cleaning the trash rack is not possible during periods of high water flow, which adversely affects plant operation. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-17 | 2026 | 8 | 17 | Karora HPS | 11.8 | 5.93 | 5.61 | 134636 | 132847 | 9.16 | 4.55 | 47.54 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 1033549.66 | 858747.11 | 1789 | 1. Unit No. 2 is on bar delivering an average load of 5.61 MW according to the available inflow. 2. The EPC Contractor dismantled Cooling Water Pump No. 01 and removed it from service for repair and maintenance since on 16.08.2026 at 09:20 hrs. 3. Currently, only one cooling water pump remains in service. Following adjustment of the relevant valves, the cooling water pressure has stabilized at 1.9 bar. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-17 | 2026 | 8 | 17 | Koto HPS | 40.8 | 19.75 | 13.93 | 334205 | 332825 | 65.8 | 43 | 34.13 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 2742478 | 4697444.58 | 1380 | 1) Unit#1 is on bar, delivering average load of 19.75 MW, while Unit #02 & 03 remained on standby due to insufficient hydrology. Overall plant generation remained constrained due to low water inflow. 2) Unit#02 started and synchronized with grid at 02:16 Hrs& 14:24Hrs and shutdown due to low hydrology at 06:28Hrs and 20:02Hrs respectively. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-17 | 2026 | 8 | 17 | Machai HPS | 2.6 | 0.87 | 0.48 | 14212 | 13552 | 25.3 | 18 | 22.78 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 63301.39 | 115106.7 | 660 | Unit tripped due to 11 KV line tripping from Katlang grid at 0301, 0455, 0701, 1045 hrs. Unit was synced back at 0311, 0509, 0722, 1051 hrs respectively. Unit tripped at 1001, 1501, 1547, 1604, 1654, 1855 hrs due to reverse power, while it was synced back with the system at1009, 1510, 1558, 1622, 1749, 1919 hrs respectively. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-08-17 | 2026 | 8 | 17 | Malakand-3 HPS | 81 | 53 | 48.81 | 1171406 | 1159520 | 51 | 32.01 | 60.26 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3319357.9 | 1929541.06 | 11886 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-17 | 2026 | 8 | 17 | Pehur HPS | 18 | 11.7 | 10.25 | 246100 | 239000 | 18.39 | 15 | 56.97 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 900313 | 159307.65 | 7100 | Plant remained operational throughout 24 hrs with restricted flow from irrigation department | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-17 | 2026 | 8 | 17 | Reshun HPS | 4.2 | 2.61 | 1.84 | 47000 | 46740 | 2.96 | 2.87 | 46.63 | 13.48 | 100 | 45 | 100800 | 1358784 | 630055.2 | 728728.8 | 260 | line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-08-18 | 2026 | 8 | 18 | Daral Khwar HPS | 36.6 | 16.5 | 16 | 384440 | 382040 | 15.6 | 6.39 | 43.77 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 3158821.33 | 3477156.22 | 2400 | 1: Unit No. 02 and 03 were on bar delivering an average load equal to 16 MW according to the available hydrology and existing system constraints. 2: Unit No. 01 stand by due to less hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-18 | 2026 | 8 | 18 | Jabori HPS | 10.2 | 8.1 | 6.52 | 156533 | 154070 | 8.94 | 5.12 | 63.94 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 879616.44 | 517995.72 | 2463 | 1- Unit 01 and 02 delivered an average load equals to 6.52 MW to the national grid according to the available hydrology and prevailing system constraints. 2- A significant issue persists in the cooling water system which adversely affects plant operation. Both cooling water pumps are unable to maintain the required flow/pressure. 3- The one section of the sand trap is completely filled with silt and could not be emptied by flushing. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-18 | 2026 | 8 | 18 | Karora HPS | 11.8 | 5.93 | 5.77 | 138455 | 136711 | 9.16 | 4.42 | 48.89 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 1063611.58 | 828685.19 | 1744 | Unit No. 1 is on bar delivering an average load of 5.77 MW according to the available inflow. The EPC Contractor dismantled Cooling Water Pump No. 01 and removed it from service for repair and maintenance since on 16.08.2026 at 09:20 hrs. Currently, only one cooling water pump remains in service. Following adjustment of the relevant valves, the cooling water pressure has stabilized at 1.9 bar. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-18 | 2026 | 8 | 18 | Koto HPS | 40.8 | 18.23 | 13.6 | 326340 | 324940 | 65.8 | 41.99 | 33.33 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 2677505.6 | 4762416.98 | 1400 | 1) Unit#1 is on bar, delivering average load of 13.60 MW, while Unit #02 & 03 remained on standby due to insufficient hydrology. Overall plant generation remained constrained due to low water inflow. 2) Unit#02 started and synchronized with grid at 09:12 Hrs and shutdown due to low hydrology at 10:02Hrs. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-18 | 2026 | 8 | 18 | Machai HPS | 2.6 | 0.64 | 0.4 | 9880 | 9284 | 25.3 | 14 | 15.83 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 43365.56 | 135042.53 | 596 | Unit tripped 2 times due to line tripping. Unit stopped normally at 1723hrs Due to recent heavy rainfall the irrigation department maintained reduced canal discharge in accordance with the demand of XEN Swabi irrigation Division. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-08-18 | 2026 | 8 | 18 | Malakand-3 HPS | 81 | 53 | 49.27 | 1182595 | 1170100 | 51 | 31.88 | 60.83 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3349645.27 | 1899253.7 | 12495 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-18 | 2026 | 8 | 18 | Pehur HPS | 18 | 11.8 | 11.7 | 280900 | 273000 | 18.39 | 17 | 65.02 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 1028391 | 31229.65 | 7900 | Plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-18 | 2026 | 8 | 18 | Reshun HPS | 4.2 | 2.57 | 1.9 | 43000 | 42790 | 2.85 | 2.63 | 42.66 | 13.48 | 100 | 45 | 100800 | 1358784 | 576809.2 | 781974.8 | 210 | Nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-08-19 | 2026 | 8 | 19 | Daral Khwar HPS | 36.6 | 17 | 15.8 | 380300 | 378300 | 15.6 | 6.33 | 43.29 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 3127897.89 | 3508079.66 | 2000 | 1: Unit No. 02 and 03 were on bar delivering an average load equal to 15.8 MW according to available hydrology and existing system constraints. 2: Unit No. 01 stand by due to less hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-19 | 2026 | 8 | 19 | Jabori HPS | 10.2 | 8.3 | 6.17 | 148196 | 145680 | 8.94 | 4.84 | 60.54 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 831716.26 | 565895.9 | 2516 | 1- Unit 01 and 02 delivered an average load equals to 6.17 MW to the national grid according to the available hydrology and prevailing system constraints. 2- A significant issue persists in the cooling water system which adversely affects plant operation. Both cooling water pumps are unable to maintain the required flow/pressure. 3- The one section of the sand trap is completely filled with silt and could not be emptied by flushing. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-19 | 2026 | 8 | 19 | Karora HPS | 11.8 | 5.97 | 4.1 | 98343 | 97248 | 9.16 | 3.12 | 34.73 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 756589.44 | 1135707.33 | 1095 | 1.Unit No. 1 is on bar delivering an average load of 4.10MW according to the available inflow. 2.The EPC Contractor dismantled Cooling Water Pump No. 01 and removed it from service for repair and maintenance since on 16.08.2026 at 09:20 hrs. 3.Currently, only one cooling water pump remains in service. Following adjustment of the relevant valves, the cooling water pressure has stabilized at 1.9 bar resulting in generation loss. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-19 | 2026 | 8 | 19 | Koto HPS | 40.8 | 13.7 | 13.34 | 318804 | 317426 | 65.8 | 36.04 | 32.56 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 2615590.24 | 4824332.34 | 1378 | Unit#1 is on bar, delivering average load of 13.34 MW, while Unit #02 & 03 remained on standby due to insufficient hydrology. Overall plant generation remained constrained due to low water inflow. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-19 | 2026 | 8 | 19 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 6 | 12 | 0 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 0 | 178408.09 | 0 | unit stand still due to low inflow & less water level in irrigation canal. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Generation_Data.xlsx
2026-08-19 | 2026 | 8 | 19 | Malakand-3 HPS | 81 | 54 | 49.61 | 1190668 | 1178000 | 51 | 31.98 | 61.25 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3372260.6 | 1876638.37 | 12668 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-19 | 2026 | 8 | 19 | Pehur HPS | 18 | 11.78 | 6.87 | 165000 | 158000 | 18.39 | 12 | 38.19 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 595186 | 464434.65 | 7000 | Generation is less because Unit #02 was taken off the bar at 10:25 hrs, while Unit #01 load reduce to 2.7 MW with restricted flow of 05 cms instructed by the irrigation department due to heavy rain at down stream of the canal. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-19 | 2026 | 8 | 19 | Reshun HPS | 4.2 | 2.63 | 1.91 | 46000 | 45770 | 2.96 | 2.81 | 45.63 | 13.48 | 100 | 45 | 100800 | 1358784 | 616979.6 | 741804.4 | 230 | line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-08-20 | 2026 | 8 | 20 | Daral Khwar HPS | 36.6 | 16.5 | 15.8 | 380030 | 378030 | 15.6 | 6.32 | 43.26 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 3125665.45 | 3510312.1 | 2000 | 1: Unit No. 02 and 03 were on bar delivering an average load equal to 15.8 MW according to the available hydrology and existing system constraints. 2: Unit No.01 stand by due to less hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-20 | 2026 | 8 | 20 | Jabori HPS | 10.2 | 7.5 | 6.92 | 165993 | 163440 | 8.94 | 5.42 | 67.81 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 933111.65 | 464500.51 | 2553 | 1- Unit 01 and 02 delivered an average load equals to 6.92 MW to the national grid according to the available hydrology and prevailing system constraints. 2- A significant issue persists in the cooling water system which adversely affects plant operation. Both cooling water pumps are unable to maintain the required flow/pressure. 3- The one section of the sand trap is completely filled with silt and could not be emptied by flushing. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-20 | 2026 | 8 | 20 | Karora HPS | 11.8 | 5.97 | 3.69 | 88444 | 87728 | 9.16 | 2.77 | 31.23 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 682523.84 | 1209772.93 | 716 | Unit no 1 is on bar delivering an average load of 3.69 MW according to the available inflow the EPC contractor dismantled cooling water pump no 1 and removed it from service for repair and maintenance since on 16.08.2026 at 09.20 Hrs. resulting in continuous generation loss the plant was safely shutdown at 06.48 hrs. due to heavy muddy water intake site unit 01 was successfully synchronized again to the grid at 15.42.hrs.currently only one cooling water pump remains in service following adjustment of the relevant valves the cooling water pressure has stabilized at 1.9 bar | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-20 | 2026 | 8 | 20 | Koto HPS | 40.8 | 19.45 | 13.47 | 327286 | 325966 | 65.8 | 37.86 | 33.42 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 2685959.84 | 4753962.74 | 1320 | The plant delivered an average load of 13.47 MW. Mostly One Unit remain operational.Second unit was synchronized at 18:22 hrs following a head rise and then shut down at 20:44 hrs due to low hydrology. Third Unit kept on standby due to low hydrology. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-20 | 2026 | 8 | 20 | Machai HPS | 2.6 | 0.7 | 0.4 | 7408 | 7128 | 2 | 13.5 | 11.87 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 33294.89 | 145113.2 | 280 | Unit stand still of many time due to low hydrology in irrigation canal, because of no hydrology demand in irrigation of sawabi. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-08-20 | 2026 | 8 | 20 | Malakand-3 HPS | 81 | 55 | 50.28 | 1206693 | 1194630 | 51 | 32.3 | 62.07 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3419867.3 | 1829031.67 | 12063 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-20 | 2026 | 8 | 20 | Pehur HPS | 18 | 6.01 | 4.15 | 99700 | 95000 | 18.39 | 7 | 23.08 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 357865 | 701755.65 | 4700 | Generation is less because Unit#02 remained off the bar while Unit#01 is running on 6.0 mw with restricted flow instructed by irrigation department due to heavy rain at down sream of the canal. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-20 | 2026 | 8 | 20 | Reshun HPS | 4.2 | 2.87 | 1.31 | 33000 | 32790 | 2.2 | 2.65 | 32.74 | 13.48 | 100 | 45 | 100800 | 1358784 | 442009.2 | 916774.8 | 210 | outgoing Feeder Breaker reamined off for 6hours due to line fault. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-08-21 | 2026 | 8 | 21 | Daral Khwar HPS | 36.6 | 15 | 14.3 | 342160 | 340160 | 15.6 | 5.69 | 38.95 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 2812544.93 | 3823432.62 | 2000 | 1: Unit No. 02 and 03 were on bar delivering an average load equal to 14.3 MW according to the available hydrology and existing system constraints. 2: Unit No. 01 stand by due to less hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-21 | 2026 | 8 | 21 | Jabori HPS | 10.2 | 8.2 | 6.65 | 159489 | 156960 | 8.24 | 5.21 | 65.15 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 896116.03 | 501496.13 | 2529 | 1- Unit 01 and 02 delivered an average load equals to 6.65 MW to the national grid according to the available hydrology and prevailing system constraints. 2- A significant issue persists in the cooling water system which adversely affects plant operation. Both cooling water pumps are unable to maintain the required flow/pressure. 3- The one section of the sand trap is completely filled with silt and could not be emptied by flushing. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-21 | 2026 | 8 | 21 | Karora HPS | 11.8 | 5.97 | 4.68 | 112272 | 110955 | 9.16 | 3.63 | 39.64 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 863229.9 | 1029066.87 | 1317 | 1. Unit No. 1 is on bar delivering an average load of 4.68 MW according to the available inflow. 2. The EPC Contractor dismantled Cooling Water Pump No. 01 and removed it from service for repair and maintenance since on 16.08.2026 at 09:20 hrs resulting in continuous generation loss. 3. Plant shutdown was carried out for sand trap flushing at 09:48 hrs. Following completion of the flushing activity, Unit #01 was restarted and synchronized with the system at 13:16 hrs, and its load was gradually increased to 5.9 MW as per available inflow. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-21 | 2026 | 8 | 21 | Koto HPS | 40.8 | 13.63 | 12.77 | 306552 | 305212 | 65.8 | 39.45 | 31.31 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 2514946.88 | 4924975.7 | 1340 | Unit#03is on bar delivering an average load of 12.77 MW , Unit# 01 & 02 are on standby due to low hydrology. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-21 | 2026 | 8 | 21 | Machai HPS | 2.6 | 0.86 | 0.62 | 14664 | 13860 | 6 | 14 | 23.5 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 64740.06 | 113668.03 | 804 | 1)unit tripped at 1045,1708hrs due to low & less water level in irrigation canal, while unit synched with system at 1147,1754hrs. 2) unit tripped at 2108hrs due to 11kv line tripe, 11kv line restored at 2110hrs. unit synched with system at 2127hrs. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-08-21 | 2026 | 8 | 21 | Malakand-3 HPS | 81 | 53 | 48.78 | 1170715 | 1158180 | 51 | 31.44 | 60.22 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3315521.89 | 1933377.08 | 12535 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-21 | 2026 | 8 | 21 | Pehur HPS | 18 | 6 | 5.7 | 138300 | 132000 | 18.39 | 9 | 32.01 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 497244 | 562376.65 | 6300 | At 2221 hrs, Unit #01 tripped due to failure of 132 KV supply. After restoration of 132 KV supply Unit # 01 taken on bar at 2310 hrs, with 6.0 MW load. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-21 | 2026 | 8 | 21 | Reshun HPS | 4.2 | 2.68 | 1.91 | 43000 | 42770 | 2.65 | 2.57 | 42.66 | 13.48 | 100 | 45 | 100800 | 1358784 | 576539.6 | 782244.4 | 230 | Nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-08-22 | 2026 | 8 | 22 | Daral Khwar HPS | 36.6 | 13.5 | 13.2 | 317220 | 315220 | 15.6 | 5.27 | 36.11 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 2606333.53 | 4029644.02 | 2000 | 1: Unit No. 02 and 03 were on bar delivering an average load equal to 13.2 MW according to the available hydrology and existing system constraints. 2: Unit No. 01 stand by due to less hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-22 | 2026 | 8 | 22 | Jabori HPS | 10.2 | 8.5 | 6.76 | 162196 | 159600 | 8.24 | 5.3 | 66.26 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 911188.32 | 486423.84 | 2596 | Unit 01 and 02 delivered an average load equals to 6.76 MW to the national grid according to the available hydrology and prevailing system constraints. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-22 | 2026 | 8 | 22 | Karora HPS | 11.8 | 5.94 | 5.82 | 139610 | 138094 | 9.16 | 4.42 | 49.3 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 1074371.32 | 817925.45 | 1516 | 1. Unit No. 1 is on bar delivering an average load of 5.82 MW according to the available inflow. 2. The EPC Contractor dismantled Cooling Water Pump No. 01 and removed it from service for repair and maintenance since on 16.08.2026 at 09:20 hrs resulting in continuous generation loss. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-22 | 2026 | 8 | 22 | Koto HPS | 40.8 | 13.45 | 12.93 | 309164 | 307864 | 65.8 | 35.73 | 31.57 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 2536799.36 | 4903123.22 | 1300 | Unit #03 is on bar delivering an average load of 12.93 MW. Unit# 01,02 are on standby due to low hydrology. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-22 | 2026 | 8 | 22 | Machai HPS | 2.6 | 0.56 | 0.4 | 8264 | 7876 | 8 | 14 | 13.24 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 36788.8 | 141619.3 | 388 | Unit stopped at 0328, 0510 & 0955 hrs. due to low head intake, while resynched at 0419, 0532 & 1054 hrs.. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-08-22 | 2026 | 8 | 22 | Malakand-3 HPS | 81 | 52 | 49.28 | 1182738 | 1170680 | 51 | 31.93 | 60.84 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3351305.64 | 1897593.33 | 12058 | As per available hydrology from the Irrigation Department all the three Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-22 | 2026 | 8 | 22 | Pehur HPS | 18 | 8.15 | 6.47 | 155400 | 150000 | 18.39 | 10 | 35.97 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 565050 | 494570.65 | 5400 | Generationb is less because of low irrigation demand due to rainfall. At 1115 Hrs Unit # 02 started along with Unit # 01. Both Units running on partial load. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-22 | 2026 | 8 | 22 | Reshun HPS | 4.2 | 2.64 | 1.86 | 45000 | 44780 | 2.81 | 2.75 | 44.64 | 13.48 | 100 | 45 | 100800 | 1358784 | 603634.4 | 755149.6 | 220 | Nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-08-23 | 2026 | 8 | 23 | Daral Khwar HPS | 36.6 | 21 | 14.8 | 355030 | 353030 | 15.6 | 5.9 | 40.42 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 2918957.95 | 3717019.6 | 2000 | 1: Units No.02 and 03 were on bar delivering an average load equal to 14.8 MW according to the available hydrology and existing system constraints. 2: Suddenly the powerhouse auxiliary supply tripped at 13:27Hrs, due to bad weather and fault on weir supply line (line to line and ground), the cutout link has fused and one ceramic insulator was also found broken. 3: The auxiliary supply was transferred to MTR No.03 and restored at 16:00 Hrs,Unit No.02 was synchronized with the national grid at 16:18Hrs. 4: Unit No.03 was stopped at 13:27Hrs due to reduced hydrology and was later synchronized with the national grid at 20:54hrs once hydrology improved. 5: Unit No.01 standby due to less hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-23 | 2026 | 8 | 23 | Jabori HPS | 10.2 | 7.3 | 6.46 | 155006 | 153120 | 8.24 | 5.07 | 63.32 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 874192.7 | 523419.46 | 1886 | Unit 01 and 02 were on the bar delivering an average load equals to 6.46 MW to the national grid according to the available hydrology and prevailing system constraints. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-23 | 2026 | 8 | 23 | Karora HPS | 11.8 | 8.9 | 6.3 | 151179 | 149554 | 9.16 | 5.17 | 53.38 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 1163530.12 | 728766.65 | 1625 | 1.Unit No . 1 & 2 is on bar delivering an average load of 6.30 MW according to the available inflow. 2. Following the installation of Cooling Water System Pump No. 1, the pump could not be placed in service due to a rise in bearing temperature. Currently, Cooling Water System Pump No. 2 is in operation. 3. Following the completion of the Generator Air Cooler (GCC) cleaning of Unit #02, the unit was started and synchronized with the system at 14:04 hrs. and its load was gradually increased to 3.2 MW. 4. At 15:00 hrs., a 132 kV transmission line supply failure occurred. Following restoration of the supply at 15:23 hrs., Unit #02 was synchronized with the system at 15:40 hrs., and its load was gradually increased to 3.8 MW. Subsequently, Unit #01 was synchronized with the system at 15:47 hrs., and its load was gradually increased to 3.8 MW in accordance with the available water inflow. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-23 | 2026 | 8 | 23 | Koto HPS | 40.8 | 13.57 | 11.74 | 281852 | 280692 | 65.8 | 36.27 | 28.78 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 2312902.08 | 5127020.5 | 1160 | Unit#03is on bar delivering an average load of 11.74 MW Unit# 01 & 02 are on standby due to low hydrology. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-23 | 2026 | 8 | 23 | Machai HPS | 2.6 | 0 | 0 | 52 | 0 | 8 | 13 | 0.08 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 0 | 178408.09 | 52 | Unit remained still due to low water level & fault in synchronization system. Maintenance in progress. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-08-23 | 2026 | 8 | 23 | Malakand-3 HPS | 81 | 54 | 48.95 | 1174896 | 1162900 | 51 | 31.61 | 60.44 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3329033.83 | 1919865.14 | 11996 | As per available hydrology from the Irrigation Department all three units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-23 | 2026 | 8 | 23 | Pehur HPS | 18 | 8.15 | 7.6 | 182600 | 177000 | 18.39 | 12 | 42.27 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 666759 | 392861.65 | 5600 | Generationb is less because of low irrigation demand due to rainfall. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-23 | 2026 | 8 | 23 | Reshun HPS | 4.2 | 2.64 | 1.93 | 45000 | 44800 | 2.85 | 2.75 | 44.64 | 13.48 | 100 | 45 | 100800 | 1358784 | 603904 | 754880 | 200 | Nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-08-24 | 2026 | 8 | 24 | Daral Khwar HPS | 36.6 | 16 | 11.9 | 286550 | 284490 | 15.6 | 4.76 | 32.62 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 2352248.67 | 4283728.88 | 2060 | 1: Units No.02 and 03 were on bar delivering an average load equal to 11.9 MW according to the available hydrology and existing system constraints. 2: The powerhouse was shutdown at 14:20Hrs for replacement of 2 burnt cutout fuses on 11KV weir line and broken isolator of cutout link. 3: After the replacement, the auxiliary was switched back to generator busbar at 19:18Hrs but both incoming and outgoing breakers of the isolation transformer kept opening.subsequently, meggering of all cables on the supply line from isolation transformer to auxiliary breaker of station was meticulously carried out and the fault was traced to a single cable (Phase-B) on the 400V side of station transformer.The minor damage to insulation of the said cable was rectified and then the isolation. transformer was successfully energized and auxiliary supply was restored at 19:18Hrs, Unit No.02 was synchronized with the national grid at 19:25Hrs. 4: Unit No.03 was stopped at 14:20Hrs due to less hydrology. 5: Unit No.01 standby due to less hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-24 | 2026 | 8 | 24 | Jabori HPS | 10.2 | 7.4 | 6.4 | 154525 | 153120 | 8.24 | 5.05 | 63.12 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 874192.7 | 523419.46 | 1405 | Unit 01 and 02 were on the bar delivering an average load equals to 6.4 MW to the national grid according to the available hydrology and prevailing system constraints. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-24 | 2026 | 8 | 24 | Karora HPS | 11.8 | 8.7 | 7.32 | 175785 | 173848 | 9.16 | 5.78 | 62.07 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 1352537.44 | 539759.33 | 1937 | 1. Unit No . 1 & 2 is on bar delivering an average load of 7.32 MW according to the available inflow. 2. Following the installation of Cooling Water System Pump No. 1, the pump could not be placed in service due to an abnormal rise in bearing temperature. Currently, Cooling Water System Pump No. 2 is in operation. In the event of failure of Pump No. 2, or if it is unable to maintain the required cooling water flow and pressure for both units, plant generation may be adversely affected. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-24 | 2026 | 8 | 24 | Koto HPS | 40.8 | 20.75 | 16.75 | 401936 | 400696 | 65.8 | 51.72 | 41.05 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 3301735.04 | 4138187.54 | 1240 | Unit#02 and03 are on bar delivering an average load of 16.75 Unit# 01 are on standby due to low hydrology. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-24 | 2026 | 8 | 24 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 8 | 13 | 0 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 0 | 178408.09 | 0 | Unit stands still due to low water level & fault in synchronization system. Maintenance in progress. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-08-24 | 2026 | 8 | 24 | Malakand-3 HPS | 81 | 52 | 48.38 | 1161139 | 1148420 | 51 | 31.49 | 59.73 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3287581.93 | 1961317.03 | 12719 | As per available hydrology from the Irrigation Department all three units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-24 | 2026 | 8 | 24 | Pehur HPS | 18 | 10.7 | 9.3 | 223200 | 218000 | 18.39 | 14 | 51.67 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 821206 | 238414.65 | 5200 | Generation is less because of low irrigation demand. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-24 | 2026 | 8 | 24 | Reshun HPS | 4.2 | 2.74 | 1.81 | 41000 | 40766 | 2.8 | 2.51 | 40.67 | 13.48 | 100 | 45 | 100800 | 1358784 | 549525.68 | 809258.32 | 234 | Line faults | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-08-25 | 2026 | 8 | 25 | Daral Khwar HPS | 36.6 | 13.5 | 13.2 | 316630 | 314630 | 15.6 | 5.26 | 36.05 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 2601455.23 | 4034522.32 | 2000 | 1: Unit No. 02 was on bar delivering an average load equal to 13.2 MW according to the available hydrology. 2: Unit No. 01 and 03 are on standby due to low hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-25 | 2026 | 8 | 25 | Jabori HPS | 10.2 | 6.8 | 5.99 | 143755 | 142320 | 8.24 | 4.7 | 58.72 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 812533.34 | 585078.82 | 1435 | Unit 01 and 02 were on the bar delivering an average load equals to 5.99 MW to the national grid according to the available hydrology and prevailing system constraints. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-25 | 2026 | 8 | 25 | Karora HPS | 11.8 | 6.84 | 6.19 | 148534 | 146782 | 9.16 | 4.76 | 52.45 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 1141963.96 | 750332.81 | 1752 | 1. Unit No . 1 & 2 is on bar delivering an average load of 6.19 MW according to the available inflow. 2. Following the installation of Cooling Water System Pump No. 1, the pump could not be placed in service due to an abnormal rise in bearing temperature. Currently, Cooling Water System Pump No. 2 is in operation. In the event of failure of Pump No. 2, or if it is unable to maintain the required cooling water flow and pressure for both units, plant generation may be adversely affected. 3. Unit No. 2 was shut down at 16:58 hrs due to low hydrology and remains at a standstill due to continued low hydrology. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-25 | 2026 | 8 | 25 | Koto HPS | 40.8 | 13.68 | 12.91 | 309738 | 308438 | 65.8 | 39.86 | 31.63 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 2541529.12 | 4898393.46 | 1300 | Unit#03 is on bar delivering an average load of 12.91 MW Unit# 01 and 03 are on standby due to low hydrology. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-25 | 2026 | 8 | 25 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 8 | 13 | 0 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 0 | 178408.09 | 0 | Unit stands still due to low water level. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-08-25 | 2026 | 8 | 25 | Malakand-3 HPS | 81 | 51 | 45.71 | 1097141 | 1085400 | 51 | 30.3 | 56.44 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3107174.58 | 2141724.39 | 11741 | As per available hydrology from the Irrigation Department two units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-25 | 2026 | 8 | 25 | Pehur HPS | 18 | 11.6 | 11.2 | 268600 | 260000 | 18.39 | 17 | 62.18 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 979420 | 80200.65 | 8600 | Plant operational 24 hrs | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-25 | 2026 | 8 | 25 | Reshun HPS | 4.2 | 2.7 | 1.78 | 41000 | 40796 | 2.8 | 2.51 | 40.67 | 13.48 | 100 | 45 | 100800 | 1358784 | 549930.08 | 808853.92 | 204 | Nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-08-26 | 2026 | 8 | 26 | Daral Khwar HPS | 36.6 | 13.2 | 12.6 | 303400 | 301000 | 15.6 | 5.03 | 34.54 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 2488758.3 | 4147219.25 | 2400 | 1: Unit No. 02 was on bar delivering an average load equal to 12.6 MW according to the available hydrology and existing system constraints. 2: Units No. 01 and 03 are on stand by due to low hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-26 | 2026 | 8 | 26 | Jabori HPS | 10.2 | 6.2 | 3.82 | 91796 | 90720 | 8.24 | 3 | 37.5 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 517938.62 | 879673.54 | 1076 | 1- Unit 01 and 02 delivered an average load equals to 3.82 MW to the national grid according to the available hydrology and prevailing system constraints. 2- Plant was shut down from 1210 Hrs to 1853 Hrs for opening of the gravel trap and flushing of one section of the sand trap. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-26 | 2026 | 8 | 26 | Karora HPS | 11.8 | 5.9 | 5.83 | 139908 | 138474 | 9.16 | 4.41 | 49.4 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 1077327.72 | 814969.05 | 1434 | 1. Unit No. 1 is on bar and delivering an average load of 5.83 MW, in accordance with the available inflow. 2. The EPC Contractor has again taken Cooling Water System Pump No. 1 out of service for repair due to an abnormal rise in bearing temperature. Currently, Cooling Water System Pump No. 2 is in operation. In the event of failure of Pump No. 2 or its inability to maintain the required cooling water flow and pressure, plant generation may be affected. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-26 | 2026 | 8 | 26 | Koto HPS | 40.8 | 13.25 | 10.97 | 263284 | 261964 | 65.8 | 33.88 | 26.89 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 2158583.36 | 5281339.22 | 1320 | Due to a progressive decline in river water inflow, power plant generation capacity has been significantly reduced. Under current hydrological conditions, available inflow is only sufficient to operate a single unit. Unit 3 is running on-bar, while Units 1 and 2 are on standby due to low hydrology. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-26 | 2026 | 8 | 26 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 11 | 13 | 0 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 0 | 178408.09 | 0 | unit stand still due to low hydrology. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Generation_Data.xlsx
2026-08-26 | 2026 | 8 | 26 | Malakand-3 HPS | 81 | 50 | 46.25 | 1109982 | 1099200 | 51 | 30.01 | 57.1 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3146679.84 | 2102219.13 | 10782 | As per available hydrology from the Irrigation Department Two Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-26 | 2026 | 8 | 26 | Pehur HPS | 18 | 11.9 | 11.63 | 279200 | 272000 | 18.39 | 17 | 64.63 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 1024624 | 34996.65 | 7200 | Plant remained operational throughout 24 hours. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-26 | 2026 | 8 | 26 | Reshun HPS | 4.2 | 2.69 | 1.83 | 44000 | 43767 | 2.8 | 2.69 | 43.65 | 13.48 | 100 | 45 | 100800 | 1358784 | 589979.16 | 768804.84 | 233 | Nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-08-27 | 2026 | 8 | 27 | Daral Khwar HPS | 36.6 | 12.5 | 11.4 | 273940 | 271940 | 15.6 | 4.55 | 31.19 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 2248481.5 | 4387496.05 | 2000 | 1: Unit No.02 was on bar delivering an average load equal to 11.4 MW according to the available hydrology and existing system constraints. 2: Unit No.02 tripped at 1911 Hrs due to the failure of 132 kV line. The line restored at 1940 Hrs and Unit 2 synchronized at 1952 HRS. 3: Units No.01 and 03 are on standby due to low hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-27 | 2026 | 8 | 27 | Jabori HPS | 10.2 | 6 | 5.2 | 124752 | 123360 | 8.24 | 4.08 | 50.96 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 704286.91 | 693325.25 | 1392 | Unit 01 and 02 were on the bar delivering an average load equals to 5.20 MW to the national grid according to the available hydrology and prevailing system constraints. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-27 | 2026 | 8 | 27 | Karora HPS | 11.8 | 5.94 | 5.84 | 140094 | 138573 | 8.43 | 4.42 | 49.47 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 1078097.94 | 814198.83 | 1521 | 1.Unit No . 1 is on bar delivering an average load of 5.84MW according to the available inflow. 2.The EPC Contractor has again taken Cooling Water System Pump No. 1 out of service for repair due to an abnormal rise in bearing temperature. Currently, Cooling Water System Pump No. 2 is in operation. In the event of failure of Pump No. 2 or its inability to maintain the required cooling water flow and pressure, plant generation may be affected. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-27 | 2026 | 8 | 27 | Koto HPS | 40.8 | 11.63 | 9.97 | 239167 | 237787 | 65.8 | 30.78 | 24.42 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 1959364.88 | 5480557.7 | 1380 | Hydrology & Generation Status River inflow remains insufficient for continuous full-load operation across units. Available hydrology supports running only one unit at partial load. Unit #03 is currently online delivering an average output of 9.97 MW; Unit#02 remain on standby. Unit #01 Overspeed Issue – Technical Update The EPC E&M Team has engaged the manufacturer to review the overspeed issue and determine root-cause corrective actions. Operational records, troubleshooting logs, and technical telemetry have been submitted to the EPC E&M team to verify control system response, governor performance, speed feedback, and protection parameters. Operational Availability: Unit #01 will remain unavailable for commercial operation until this issue is fully resolved. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-27 | 2026 | 8 | 27 | Machai HPS | 2.6 | 0.86 | 0.68 | 16684 | 15888 | 11.8 | 16 | 26.74 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 74212.85 | 104195.24 | 796 | unit tripped at 1634hrs due to 11kv line trip, 11kv line restored at 1705hrs, unit synched with system at 1709hrs. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-08-27 | 2026 | 8 | 27 | Malakand-3 HPS | 81 | 49 | 43.47 | 1043242 | 1032500 | 51 | 28.97 | 53.66 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 2955737.75 | 2293161.22 | 10742 | As per instructions from RCC(Mr. Osama), both units were desynchronized from the system following voltage and frequency disturbances, along with subsequent failure of the 132 kV supply at 13:43 hrs. After restoration of the 132 kV supply at 13:50hrs, after which the unit # 01 and Unit # 02 synchronized with the system at 14:05 & 13:58hrs.As per available hydrology from the Irrigation Department Two Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-27 | 2026 | 8 | 27 | Pehur HPS | 18 | 11.92 | 11.75 | 282000 | 274000 | 18.39 | 17 | 65.28 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 1032158 | 27462.65 | 8000 | Plant remained operational throughout 24 hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-27 | 2026 | 8 | 27 | Reshun HPS | 4.2 | 2.66 | 1.78 | 42000 | 41795 | 2.65 | 2.57 | 41.67 | 13.48 | 100 | 45 | 100800 | 1358784 | 563396.6 | 795387.4 | 205 | Line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-08-28 | 2026 | 8 | 28 | Daral Khwar HPS | 36.6 | 11.5 | 11.2 | 269870 | 267870 | 15.6 | 4.48 | 30.72 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 2214829.52 | 4421148.03 | 2000 | 1: Unit No. 02 was on bar delivering an average load equal to 11.2 MW according to the available hydrology and existing system constraints. 2: Unit No. 01 and 03 are on standby due to low hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-28 | 2026 | 8 | 28 | Jabori HPS | 10.2 | 5.6 | 5.16 | 123835 | 122450 | 8.24 | 4.05 | 50.59 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 699091.54 | 698520.62 | 1385 | Unit 01 and 02 were on the bar delivering an average load equals to 5.16 MW to the national grid according to the available hydrology and prevailing system constraints. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-28 | 2026 | 8 | 28 | Karora HPS | 11.8 | 5.93 | 5.76 | 138176 | 136640 | 9.16 | 4.37 | 48.79 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 1063059.2 | 829237.57 | 1536 | 1.Unit No . 1 is on bar delivering an average load of 5.76MW according to the available inflow. 2.The EPC Contractor has again taken Cooling Water System Pump No. 1 out of service for repair due to an abnormal rise in bearing temperature. Currently, Cooling Water System Pump No. 2 is in operation. In the event of failure of Pump No. 2 or its inability to maintain the required cooling water flow and pressure, plant generation may be affected. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-28 | 2026 | 8 | 28 | Koto HPS | 40.8 | 10.93 | 9.1 | 218501 | 217201 | 65.8 | 28.12 | 22.31 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 1789736.24 | 5650186.34 | 1300 | Unit 3 is currently online and delivering an average load of 9.10 MW. Unit 2 remains on standby due to low water availability. Unit 1 is unavailable and has been placed at the disposal of the EPC E&M team, which has recommended a detailed investigation to address the overspeed and upper guide bearing oil leak issues. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-28 | 2026 | 8 | 28 | Machai HPS | 2.6 | 0.97 | 0.86 | 19956 | 19144 | 11.8 | 16 | 31.98 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 89421.62 | 88986.47 | 812 | unit tripped at 0437,1103,2018hrs due to 11kv line trip, 11kv line restored at 0443,1127,2024hrs, unit synched with system at 0447,1132,2054hrs. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-08-28 | 2026 | 8 | 28 | Malakand-3 HPS | 81 | 47 | 43.79 | 1050973 | 1040050 | 51 | 28.85 | 54.06 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 2977351.14 | 2271547.83 | 10923 | As per available hydrology from the Irrigation Department, the 02 units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-28 | 2026 | 8 | 28 | Pehur HPS | 18 | 11.9 | 11.7 | 283100 | 274000 | 18.39 | 17 | 65.53 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 1032158 | 27462.65 | 9100 | Plant remained operational throughout 24 hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-28 | 2026 | 8 | 28 | Reshun HPS | 4.2 | 2.66 | 1.9 | 44000 | 43771 | 2.8 | 2.69 | 43.65 | 13.48 | 100 | 45 | 100800 | 1358784 | 590033.08 | 768750.92 | 229 | Nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-08-29 | 2026 | 8 | 29 | Daral Khwar HPS | 36.6 | 12 | 11.2 | 267810 | 266210 | 15.6 | 4.45 | 30.49 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 2201104.14 | 4434873.4 | 1600 | 1: Unit No. 02 was on bar delivering an average load equal to 11.2 MW according to the available hydrology and existing system constraints. 2: Unit No. 01 and 03 were on standby due to low hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-29 | 2026 | 8 | 29 | Jabori HPS | 10.2 | 8 | 5.3 | 127783 | 126280 | 8.24 | 4.18 | 52.2 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 720957.78 | 676654.38 | 1503 | Unit 01 and 02 were on the bar delivering an average load equals to 5.3 MW to the national grid according to the available hydrology and prevailing system constraints. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-29 | 2026 | 8 | 29 | Karora HPS | 11.8 | 5.94 | 5.61 | 134702 | 133160 | 9.16 | 4.27 | 47.56 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 1035984.8 | 856311.97 | 1542 | 1.Unit No . 1 is on bar delivering an average load of 5.61MW according to the available inflow. 2.The EPC Contractor has again taken Cooling Water System Pump No. 1 out of service for repair due to an abnormal rise in bearing temperature. Currently, Cooling Water System Pump No. 2 is in operation. In the event of failure of Pump No. 2 or its inability to maintain the required cooling water flow and pressure, plant generation may be affected. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-29 | 2026 | 8 | 29 | Koto HPS | 40.8 | 11.32 | 9.25 | 221969 | 220769 | 65.8 | 28.56 | 22.67 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 1819136.56 | 5620786.02 | 1200 | Unit 3 is on bar and delivering an average load of 9.25 MW. Unit 2 remains on standby due to low water availability. Unit 1 is unavailable and has been placed at the disposal of the EPC E&M team, which has recommended a detailed investigation to address the overspeed and upper guide bearing oil leak issues. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-29 | 2026 | 8 | 29 | Machai HPS | 2.6 | 1.04 | 0.64 | 15776 | 15132 | 13.1 | 18 | 25.28 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 70681.57 | 107726.52 | 644 | unit tripped at 0303 hrs due to 11kv line, 11kv line restored at 0318hrs, unit synched at 0321hrs. Unit tripped due to governor oil high temperature at 0535,0630,0654,0820 while synced back with system at 0605,0643,0816,1350 hrs. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-08-29 | 2026 | 8 | 29 | Malakand-3 HPS | 81 | 47 | 44.02 | 1056410 | 1045690 | 51 | 29.11 | 54.34 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 2993496.76 | 2255402.2 | 10720 | As per available hydrology from the Irrigation Department, two Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-29 | 2026 | 8 | 29 | Pehur HPS | 18 | 11.98 | 11.83 | 283900 | 276000 | 18.39 | 18 | 65.72 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 1039692 | 19928.65 | 7900 | Plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-29 | 2026 | 8 | 29 | Reshun HPS | 4.2 | 2.61 | 1.9 | 45000 | 44793 | 2.85 | 2.75 | 44.64 | 13.48 | 100 | 45 | 100800 | 1358784 | 603809.64 | 754974.36 | 207 | Nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-08-30 | 2026 | 8 | 30 | Daral Khwar HPS | 36.6 | 22 | 12.2 | 293210 | 291210 | 15.6 | 4.87 | 33.38 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 2407811.64 | 4228165.9 | 2000 | 1: Unit No. 02 and 03 were on bar delivering an average load equal to 12.2 MW according to the available hydrology and existing system constraints. 2: Unit No.03 synchronized with the national grid at 22:22 Hrs due to increased hydrology. 3: Unit No. 01 was on standby due to low hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-30 | 2026 | 8 | 30 | Jabori HPS | 10.2 | 6 | 5.15 | 123634 | 122020 | 8.24 | 4.04 | 50.5 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 696636.58 | 700975.58 | 1614 | Unit 01 was on the bar delivering an average load equals to 5.15 MW to the national grid according to the available hydrology and prevailing system constraints. Unit 02 is in shutdown state due to low hydrology. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-30 | 2026 | 8 | 30 | Karora HPS | 11.8 | 5.5 | 4.38 | 105063 | 103798 | 9.16 | 3.25 | 37.1 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 807548.44 | 1084748.33 | 1265 | 1.Unit No . 1 is on bar delivering an average load of 4.3MW according to the available inflow. 2.The EPC Contractor has again taken Cooling Water System Pump No. 1 out of service for repair due to an abnormal rise in bearing temperature. Currently, Cooling Water System Pump No. 2 is in operation. In the event of failure of Pump No. 2 or its inability to maintain the required cooling water flow and pressure, plant generation may be affected. 3.The weir site team informed that heavy rainfall caused highly muddy water at intake. Accordingly, the plant was smoothly and safely shutdown at 20:35 hrs to avoid excessive silt and debris entering the system. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-30 | 2026 | 8 | 30 | Koto HPS | 40.8 | 13.43 | 11.01 | 264191 | 263011 | 65.8 | 34 | 26.98 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 2167210.64 | 5272711.94 | 1180 | Unit 3 is on bar and delivering an average load of 11.01 MW. Unit 2 remains on standby due to low water availability. Unit 1 is unavailable and has been placed at the disposal of the EPC E&M team, which has recommended a detailed investigation to address the overspeed and upper guide bearing oil leak issues. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-30 | 2026 | 8 | 30 | Machai HPS | 2.6 | 0.92 | 0.79 | 19200 | 18392 | 13 | 18 | 30.77 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 85909.03 | 92499.06 | 808 | unit tripped at 0528,0853,1758,2003 hrs due to 11kv line, 11kv line restored at 0530,0855,1803,2016 hrs, unit synched at 0537,0858,1807,2055hrs. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-08-30 | 2026 | 8 | 30 | Malakand-3 HPS | 81 | 48 | 44.1 | 1058507 | 1048400 | 51 | 29.59 | 54.45 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3001254.68 | 2247644.29 | 10107 | 132 kV lines DRG1 & DRG 2 tripped at Dated: 30-08-2026 00:50hrs, supply resorted at 01:06hrs, and Unit # 02 and 01 synchronized with the system, at 01:17hrs, 01:22hrs, as per available hydrology from the Irrigation Department two Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-30 | 2026 | 8 | 30 | Pehur HPS | 18 | 12 | 11.88 | 285200 | 277000 | 18.39 | 18 | 66.02 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 1043459 | 16161.65 | 8200 | Plant remained operational throughout 24 hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-30 | 2026 | 8 | 30 | Reshun HPS | 4.2 | 2.8 | 1.86 | 44000 | 43761 | 2.8 | 2.69 | 43.65 | 13.48 | 100 | 45 | 100800 | 1358784 | 589898.28 | 768885.72 | 239 | Line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-08-31 | 2026 | 8 | 31 | Daral Khwar HPS | 36.6 | 26.3 | 16.2 | 388850 | 386450 | 15.6 | 6.46 | 44.27 | 8.2683 | 91.37 | 48 | 802580.65 | 6635977.55 | 3195284.54 | 3440693.01 | 2400 | 1: Unit No. 01, 02 and 03 were on bar delivering an average load equal to 16.2 MW according to the available hydrology and existing system constraints. 2: Unit No. 03 stopped at 01:40 Hrs due to low hydrology. 3: Unit No. 03 synchronized with the national grid at 16:19 Hrs due to increased hydrology. 4: Unit No. 01 on standby due to low hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-08-31 | 2026 | 8 | 31 | Jabori HPS | 10.2 | 6.3 | 4.73 | 113589 | 112000 | 8.24 | 3.71 | 46.4 | 5.7092 | 100 | 79.57 | 244800 | 1397612.16 | 639430.4 | 758181.76 | 1589 | Unit-01 remained on the bar, delivering power according to the available hydrology and prevailing system constraints, while Unit-02 remained shut down due to low hydrology. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-08-31 | 2026 | 8 | 31 | Karora HPS | 11.8 | 5.94 | 2.73 | 65458 | 64959 | 9.16 | 2.38 | 23.11 | 7.78 | 85.88 | 0.69 | 243225.81 | 1892296.77 | 505381.02 | 1386915.75 | 499 | unit No . 1 is on bar delivering an average load of 2.73MW according to the available inflow.The EPC Contractor has again taken Cooling Water System Pump No. 1 out of service for repair due to an abnormal rise in bearingtemperature. Currently, Cooling Water System Pump No. 2 is in operation. In the event of failure of Pump No. 2 or its inability to maintain therequired cooling water flow and pressure, plant generation may be affected.The weir site team informed that heavy rainfall caused highly muddy water at intake. Accordingly, the plant was smoothly and safely shutdown at 17:22 hrs to avoid excessive silt and debris entering the intake system. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-08-31 | 2026 | 8 | 31 | Koto HPS | 40.8 | 13.52 | 11.64 | 279400 | 278180 | 65.8 | 35.95 | 28.53 | 8.24 | 92.21 | 58 | 902903.23 | 7439922.58 | 2292203.2 | 5147719.38 | 1220 | Unit 3 is on bar and delivering an average load of 11.64 MW. Unit 2 remains on standby due to low water availability. Unit 1 is unavailable and has been placed at the disposal of the EPC E&M team, which has recommended a detailed investigation to address the overspeed and upper guide bearing oil leak issues. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-31 | 2026 | 8 | 31 | Machai HPS | 2.6 | 0.93 | 0.6 | 15828 | 15136 | 25.3 | 18 | 25.37 | 4.671 | 61.21 | 70 | 38194.84 | 178408.09 | 70700.26 | 107707.84 | 692 | Unit tripped twice due to reverse power. Unit stopped immediately due to turbine bearing temp alarm as water is mixed into the oil. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-08-31 | 2026 | 8 | 31 | Malakand-3 HPS | 81 | 56 | 47.84 | 1148263 | 1136590 | 51 | 30.94 | 59.07 | 2.8627 | 94.32 | 77.5 | 1833548.39 | 5248898.97 | 3253716.19 | 1995182.78 | 11673 | Unit #03 synchronized with the system at 09:53hrs after improvement in Hydrology. Unit # 03 desynchronized from the system at 16:37hrs & kept standby due to less Hydrology. As per available hydrology from the Irrigation Department Two Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-08-31 | 2026 | 8 | 31 | Pehur HPS | 18 | 12.09 | 11.87 | 284900 | 277000 | 18.39 | 18 | 65.95 | 3.767 | 65.11 | 41 | 281290.32 | 1059620.64 | 1043459 | 16161.65 | 7900 | Not reported | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-08-31 | 2026 | 8 | 31 | Reshun HPS | 4.2 | 2.37 | 1.73 | 39000 | 38785 | 2.8 | 2.38 | 38.69 | 13.48 | 100 | 45 | 100800 | 1358784 | 522821.8 | 835962.2 | 215 | Line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-09-01 | 2026 | 9 | 1 | Daral Khwar HPS | 36.6 | 17.5 | 14.8 | 354940 | 352540 | 15.6 | 5.9 | 40.41 | 8.2683 | 47.32 | 48 | 415666.67 | 3436856.7 | 2914906.48 | 521950.22 | 2400 | 1: Unit No.02 and 03 were on bar delivering an average load equal to 14.8 MW according to the available hydrology and existing system constraints. 2: Unit #3 stopped at 0738 Hrs due to less hydrology. 3: Unit #3 synchronized with national grid at 1140 Hrs due to increased hydrology. 4: Unit #3 stopped at 1543 Hrs due to less hydrology. 5: Units No.01 standby due to low hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-09-01 | 2026 | 9 | 1 | Jabori HPS | 10.2 | 5.3 | 4.95 | 118685 | 117090 | 7.72 | 3.88 | 48.48 | 5.7092 | 84.89 | 79.57 | 207821.82 | 1186496.36 | 668490.23 | 518006.13 | 1595 | Unit 02 was on the bar and delivered power to the national grid according to the available hydrology and prevailing system constraints while unit 01 was in stopped state due to leakage from the wicket gates. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-09-01 | 2026 | 9 | 1 | Karora HPS | 11.8 | 5.92 | 2.73 | 19794 | 19953 | 6.53 | 0.74 | 6.99 | 7.78 | 69.09 | 0.69 | 195666.67 | 1522286.67 | 155234.34 | 1367052.33 | 159 | 1. unit#1 is on bar delivering an average load of 2.73 MW according to available inflow. 2. The EPC Contractor has again taken the cooling water system pump No.1 out service for repair due to abnormal rise in bearing temprature, cooling water system pumpNo.2 is in operation. In the event of failure of pumpNo.2 or its inability to maintain the requried cooling water flow and pressure , plant generation may be affected. 3. Following the improvement in water quality at the intake, the plant was smoothly and safely synchronized at 20:37hrs with the national grid. | rekarorahps2000@gmail.com | Original | CHECK: Net > Units (source me verify karein) | Generation_Data.xlsx
2026-09-01 | 2026 | 9 | 1 | Koto HPS | 40.8 | 21.67 | 14.89 | 355824 | 354564 | 65.8 | 36.49 | 36.34 | 8.24 | 63.59 | 58 | 622666.67 | 5130773.33 | 2921607.36 | 2209165.97 | 1260 | Avg. Plant Load: 14.89 MW Unit Operation:Unit#01 remained operational . Unit-02:Synchronized with grid at 11:30 hrs on head rise and shutdown at 19:06 hrs on head drop. Unit-03: On standby due to low hydrology. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-01 | 2026 | 9 | 1 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 28.6 | 6 | 0 | 4.671 | 71.5 | 70 | 44616 | 208401.34 | 0 | 208401.34 | 0 | Unit standstill due to Turbine guide bearing maintenance. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-09-01 | 2026 | 9 | 1 | Malakand-3 HPS | 81 | 52 | 50.11 | 1202577 | 1191840 | 51 | 32.31 | 61.86 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 3411880.37 | 1837357.2 | 10737 | As per available hydrology from the Irrigation Department two Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-01 | 2026 | 9 | 1 | Pehur HPS | 18 | 11.98 | 11.7 | 280700 | 272000 | 21.22 | 18 | 64.98 | 3.767 | 66.67 | 41 | 288000 | 1084896 | 1024624 | 60272 | 8700 | Plant operational 24 hrs. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-09-01 | 2026 | 9 | 1 | Reshun HPS | 4.2 | 2.54 | 1.37 | 33000 | 32759 | 2.8 | 2.02 | 32.74 | 13.48 | 100 | 45 | 100800 | 1358784 | 441591.32 | 917192.68 | 241 | Outgoing feeder breaker remained Off 2.30hours due to line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-09-02 | 2026 | 9 | 2 | Daral Khwar HPS | 36.6 | 14.5 | 13.9 | 334440 | 332440 | 15.6 | 5.56 | 38.07 | 8.2683 | 47.32 | 48 | 415666.67 | 3436856.7 | 2748713.65 | 688143.05 | 2000 | 1: Unit No.02 was on bar delivering an average load equal to 13.9 MW according to the available hydrology and existing system constraints. 2: Unit No.01 and 03 on standby due to low hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-09-02 | 2026 | 9 | 2 | Jabori HPS | 10.2 | 5.2 | 5.1 | 123338 | 121660 | 7.72 | 4.03 | 50.38 | 5.7092 | 84.89 | 79.57 | 207821.82 | 1186496.36 | 694581.27 | 491915.08 | 1678 | Unit 02 was on the bar delivering 5.1 MW to the national grid according to the available hydrology and prevailing system constraints while unit 01 was shutdown due to leakage issue from the wicket gates. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-09-02 | 2026 | 9 | 2 | Karora HPS | 11.8 | 5.9 | 2.73 | 53056 | 52738 | 6.53 | 1.59 | 18.73 | 7.78 | 69.09 | 0.69 | 195666.67 | 1522286.67 | 410301.64 | 1111985.03 | 318 | 1. Unit No . 1 is on bar delivering an average load of 2.73 MW according to the available inflow. 2. The EPC Contractor removed again the Cooling Water System Pump No. 1 for repair works due to an abnormal rise in bearing temperature. Currently, Cooling Water System Pump No. 2 is in operation. In the event of failure of Pump No. 2 or its inability to maintain the required cooling water flow and pressure, plant generation may be affected. 3. Following the improvement in water quality at intake site, the plant was smoothly and safely synchronized at 17:23 hrs with the National Grid. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-09-02 | 2026 | 9 | 2 | Koto HPS | 40.8 | 19.95 | 13.11 | 314660 | 313400 | 40.9 | 40.49 | 32.13 | 8.24 | 63.59 | 58 | 622666.67 | 5130773.33 | 2582416 | 2548357.33 | 1260 | 1)Unit-03 is on bar delivering an average load of 13.11 MW. 2)Unit-02 remains shut down due to governor lock pipe issue that has not been replaced by the EPC contractor. 3)Unit-01 is unavailable and has been placed at the disposal of EPC contractor to thoroughly investigate the governor overspeeding and upper guide bearing oil leakage issues. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-02 | 2026 | 9 | 2 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 28.6 | 15 | 0 | 4.671 | 71.5 | 70 | 44616 | 208401.34 | 0 | 208401.34 | 0 | Unit standstill due to Turbine guide bearing maintenance. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-09-02 | 2026 | 9 | 2 | Malakand-3 HPS | 81 | 51 | 11.98 | 287532 | 285640 | 51 | 9.57 | 14.79 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 817701.63 | 4431535.94 | 1892 | Due to heavy rainfall in the Upper Swat catchment area, a large quantity of trash and debris accumulated at the Forebay and Sediment. As a result total shut down carried out to facilitate cleaning of the trash racks at the Forebay and Sediment, along with inspection and cleaning of the units’ spiral casings. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-02 | 2026 | 9 | 2 | Pehur HPS | 18 | 12.05 | 11.9 | 285700 | 278000 | 21.2 | 18 | 66.13 | 3.767 | 66.67 | 41 | 288000 | 1084896 | 1047226 | 37670 | 7700 | The plant remained operational throughout 24 hrs as per available hydrology. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-09-02 | 2026 | 9 | 2 | Reshun HPS | 4.2 | 2.53 | 1.81 | 42000 | 41770 | 2.76 | 2.57 | 41.67 | 13.48 | 100 | 45 | 100800 | 1358784 | 563059.6 | 795724.4 | 230 | Nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-09-03 | 2026 | 9 | 3 | Daral Khwar HPS | 36.6 | 13.5 | 12.5 | 299610 | 297610 | 15.6 | 4.98 | 34.11 | 8.2683 | 47.32 | 48 | 415666.67 | 3436856.7 | 2460728.76 | 976127.94 | 2000 | 1: Unit No. 02 was on bar delivering an average load equal to 12.5 MW according to the available hydrology and existing system constraints. 2: Unit No. 01 and 03 on standby due to low hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-09-03 | 2026 | 9 | 3 | Jabori HPS | 10.2 | 5.2 | 5.1 | 124009 | 122350 | 7.72 | 4.05 | 50.66 | 5.7092 | 84.89 | 79.57 | 207821.82 | 1186496.36 | 698520.62 | 487975.74 | 1659 | Unit 02 was on the bar delivering an average load equals to 5.1 MW to the national grid according to the available hydrology and prevailing system constraints while unit 02 was shutdown due to leakage from the wicket gates. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-09-03 | 2026 | 9 | 3 | Karora HPS | 11.8 | 6.58 | 6.02 | 144387 | 142495 | 6.53 | 4.53 | 50.98 | 7.78 | 69.09 | 0.69 | 195666.67 | 1522286.67 | 1108611.1 | 413675.57 | 1892 | 1. Unit No. 1 & 2 is on bar delivering an average load of 6.02 MW according to the available inflow. 2. The EPC Contractor installed the Cooling Water System Pump No. 1 after repair works. Currently, both Cooling Water Pumps produce requisite pressure. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-09-03 | 2026 | 9 | 3 | Koto HPS | 40.8 | 13.63 | 6.91 | 165883 | 164603 | 40.9 | 21.35 | 16.94 | 8.24 | 63.59 | 58 | 622666.67 | 5130773.33 | 1356328.72 | 3774444.61 | 1280 | 1) Unit-03 was shut down at 09:34 hrs for The intake and sand trap trash racks cleaning. As the TRCM is not operational, manual cleaning of the intake and sand trap trash racks was carried out. After completion of cleaning, Unit-03 started and synchronized with the grid at 20:48 hrs, delivering an average load of 6.91MW. 2) Unit-02 remains shut down due to governor lock pipe issue. The pipes has not yet been replaced by the EPC contractor. 3) Unit-01 is unavailable and has been placed at the disposal of the EPC contractor for detailed investigation of governor overspeed and upper guide bearing oil leakage issues.. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-03 | 2026 | 9 | 3 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 28.6 | 17 | 0 | 4.671 | 71.5 | 70 | 44616 | 208401.34 | 0 | 208401.34 | 0 | Unit standstill due to Turbine guide bearing maintenance. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-09-03 | 2026 | 9 | 3 | Malakand-3 HPS | 81 | 54 | 35.5 | 852048 | 849540 | 51 | 23.67 | 43.83 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 2431978.16 | 2817259.41 | 2508 | Units synchronized with the system at 0658Hrs after carrying out cleaning of trash racks and Units spiral casing. As per available Hydrology from irrigation department two Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-03 | 2026 | 9 | 3 | Pehur HPS | 18 | 11.9 | 11.4 | 274600 | 266000 | 21.22 | 18 | 63.56 | 3.767 | 66.67 | 41 | 288000 | 1084896 | 1002022 | 82874 | 8600 | Not reported | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-09-03 | 2026 | 9 | 3 | Reshun HPS | 4.2 | 2.76 | 1.8 | 42000 | 41710 | 2.76 | 2.57 | 41.67 | 13.48 | 100 | 45 | 100800 | 1358784 | 562250.8 | 796533.2 | 290 | Nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-09-04 | 2026 | 9 | 4 | Daral Khwar HPS | 36.6 | 13 | 11.9 | 285300 | 283300 | 15.6 | 4.74 | 32.48 | 8.2683 | 47.32 | 48 | 415666.67 | 3436856.7 | 2342409.39 | 1094447.31 | 2000 | 1: Unit No. 02 was on bar delivering an average load equal to 11.9 MW according to the available hydrology and existing system constraints. 2: Unit No. 01 and 03 on standby due to low hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-09-04 | 2026 | 9 | 4 | Jabori HPS | 10.2 | 6.2 | 5.25 | 126064 | 124460 | 7.74 | 4.12 | 51.5 | 5.7092 | 84.89 | 79.57 | 207821.82 | 1186496.36 | 710567.03 | 475929.32 | 1604 | 1- unit 02 was on the bar delivering an average load equals to 5.25 MW to the national grid according to the available hydrology and prevailing system constraints. 2- The leakage from the wicket gates was stopped by tightening the associated nuts and bolts, and the wicket gates were kept under observation. After confirming that the leakage had stopped, Unit-01 was synchronized at 2038 Hrs. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-09-04 | 2026 | 9 | 4 | Karora HPS | 11.8 | 7.52 | 6.04 | 144881 | 143136 | 8.77 | 4.75 | 51.16 | 7.78 | 69.09 | 0.69 | 195666.67 | 1522286.67 | 1113598.08 | 408688.59 | 1745 | 1. Unit No. 1 & 2 is on bar delivering an average load of 6.04 MW according to the available inflow. 2. The EPC Contractor installed the Cooling Water System Pump No. 1 on 03.09.2026 after repair works. Currently, both Cooling Water Pumps produce requisite pressure but the pumps vibrates abnormally. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-09-04 | 2026 | 9 | 4 | Koto HPS | 40.8 | 18.52 | 13.48 | 323620 | 322460 | 40.9 | 41.64 | 33.05 | 8.24 | 63.59 | 58 | 622666.67 | 5130773.33 | 2657070.4 | 2473702.93 | 1160 | Unit#02 and 03 are on bar delivering an average load of 13.48MW according to avalible hydrology, unit#01 shutdown and under inspection of governor over speed issue | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-04 | 2026 | 9 | 4 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 28.6 | 17 | 0 | 4.671 | 71.5 | 70 | 44616 | 208401.34 | 0 | 208401.34 | 0 | Unit standstill due to Turbine guide bearing maintenance. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-09-04 | 2026 | 9 | 4 | Malakand-3 HPS | 81 | 54 | 51.88 | 1245127 | 1235690 | 51 | 32.88 | 64.05 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 3537409.76 | 1711827.8 | 9437 | As per available hydrology from Irrigation Department two units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-04 | 2026 | 9 | 4 | Pehur HPS | 18 | 8.97 | 5.48 | 131600 | 126000 | 20 | 9 | 30.46 | 3.767 | 66.67 | 41 | 288000 | 1084896 | 474642 | 610254 | 5600 | Generation is less because, Units #01 and #02 tripped due to isolation of Gadoon grid from national grid from 0335 Hrs to 0430 Hrs. unit#02 taken off the bar at 0950 Hrs dt 04-09-26 as per instruction of irrigation SDO due to low irrigation demand. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-09-04 | 2026 | 9 | 4 | Reshun HPS | 4.2 | 2.46 | 1.7 | 38000 | 37730 | 2.8 | 2.32 | 37.7 | 13.48 | 100 | 45 | 100800 | 1358784 | 508600.4 | 850183.6 | 270 | Line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-09-05 | 2026 | 9 | 5 | Daral Khwar HPS | 36.6 | 30.6 | 15.3 | 366900 | 365300 | 15.6 | 6.11 | 41.77 | 8.2683 | 47.32 | 48 | 415666.67 | 3436856.7 | 3020409.99 | 416446.71 | 1600 | 1: Units No.02 and 03 were on bar delivering an average load equal to 15.3 MW according to the available hydrology and existing system constraints. 2: 132KV supply line tripped at 16:24Hrs and was restored at 16:48Hrs. 3: Unit No.02 was synchronized with the national grid at 17:03Hrs. 4: Unit No.03 was synchronized with the national grid at 18:52 Hrs due to increased Hydrology.However, Unit No.03 was stopped at 23:17Hrs due to low hydrology. 5: Units No.01 and 03 standby due to low hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-09-05 | 2026 | 9 | 5 | Jabori HPS | 10.2 | 7.7 | 5.58 | 133999 | 132430 | 7.72 | 4.38 | 54.74 | 5.7092 | 84.89 | 79.57 | 207821.82 | 1186496.36 | 756069.36 | 430427 | 1569 | Unit 01 and 02 were on the bar delivering an average load equals to 5.58 MW to the national grid according to the available hydrology and prevailing system constraints. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-09-05 | 2026 | 9 | 5 | Karora HPS | 11.8 | 5.96 | 5.82 | 139799 | 138152 | 8.77 | 4.68 | 49.36 | 7.78 | 69.09 | 0.69 | 195666.67 | 1522286.67 | 1074822.56 | 447464.11 | 1647 | Unit No. 2 is on bar delivering an average load of 5.82 MW according to the available inflow. At 10:44 hrs, the Khan–Karora Circuit was de-energized after a Permit to Work (PTW) was requested from RCC to carry out the physical interconnection of the Red and Yellow phases of the CVTs installed in the 132 kV line bay for the Karora–Khan Khwar link, along with the interconnection and line tuning of the switchyard telecommunication equipment, including Wave Traps, Line Matching Units (LMUs), and CVTs, with the PLCC panels. Upon instruction from RCC, Circuit Breaker E2Q1 was opened, Isolator E2Q10 was opened, and Earthing Switch E2E20 was closed. At 17:05 hrs, upon completion of the required work by the EPC Contractor, RCC was informed accordingly. On the instruction of RCC, the Khan–Karora Circuit was re-energized. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-09-05 | 2026 | 9 | 5 | Koto HPS | 40.8 | 13.65 | 12.66 | 303911 | 302871 | 40.9 | 39.11 | 31.04 | 8.24 | 63.59 | 58 | 622666.67 | 5130773.33 | 2495657.04 | 2635116.29 | 1040 | Unit 03 is on bar delivering an average load of 12.66 MW according to avalible hydrology Unit 02 is s/by due to low hydrology unit#01 shutdown and under inspection of governor over speed issue | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-05 | 2026 | 9 | 5 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 21.8 | 17 | 0 | 4.671 | 71.5 | 70 | 44616 | 208401.34 | 0 | 208401.34 | 0 | Unit stand still due to Turbine Guide bearing Maintenance under progress. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load; Avg Historical Hydrology interpolated from neighbouring days; Actual Avg Cumic interpolated from neighbouring days | Generation_Data.xlsx
2026-09-05 | 2026 | 9 | 5 | Malakand-3 HPS | 81 | 51 | 45.94 | 1102621 | 1093600 | 51 | 29.87 | 56.72 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 3130648.72 | 2118588.85 | 9021 | As per available hydrology from Irrigation Department two units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-05 | 2026 | 9 | 5 | Pehur HPS | 18 | 8.12 | 6.14 | 147400 | 142000 | 21.2 | 10 | 34.12 | 3.767 | 66.67 | 41 | 288000 | 1084896 | 534914 | 549982 | 5400 | Generation is less because of: Unit # 02 remained off the bar since 0950 Hrs dated 04-09-2026. On 05-09-2026 at 1725 Hrs Unit # 02 taken on bar. Both units are running on partial load due to less demand | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-09-05 | 2026 | 9 | 5 | Reshun HPS | 4.2 | 2.36 | 1.6 | 38705 | 38000 | 2.8 | 2.38 | 38.4 | 13.48 | 100 | 45 | 100800 | 1358784 | 512240 | 846544 | 705 | Line faults | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-09-06 | 2026 | 9 | 6 | Daral Khwar HPS | 36.6 | 18.5 | 15.1 | 362150 | 360150 | 15.6 | 6.02 | 41.23 | 8.2683 | 47.32 | 48 | 415666.67 | 3436856.7 | 2977828.24 | 459028.46 | 2000 | 1: Units No.02 and 03 were on bar delivering an average load equal to 15.1 MW according to the available hydrology and existing system constraints. 2: Unit No.03 was synchronized with the national grid at 02:20Hrs due to increased Hydrology.However, Unit No.03 was stopped at 14:32Hrs due to low hydrology. 3: Units No.01 and 03 standby due to low hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-09-06 | 2026 | 9 | 6 | Jabori HPS | 10.2 | 8 | 5.53 | 132627 | 131090 | 7.72 | 4.33 | 54.18 | 5.7092 | 84.89 | 79.57 | 207821.82 | 1186496.36 | 748419.03 | 438077.33 | 1537 | 1- Unit 01 and 02 were on the bar delivering an average load equals to 5.53 MW to the national grid according to the available hydrology and prevailing system constraints. 2- At 1640 Hrs, both units tripped due to a sudden drop in the discharge pressure of Cooling Water Pump-01 from 2.0 bar to 0.2 bar. Unit-02 and Unit-01 were subsequently resynchronized at 1647 Hrs and 1710 Hrs, respectively. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-09-06 | 2026 | 9 | 6 | Karora HPS | 11.8 | 5.94 | 5.82 | 139662 | 137949 | 8.77 | 4.87 | 49.32 | 7.78 | 69.09 | 0.69 | 195666.67 | 1522286.67 | 1073243.22 | 449043.45 | 1713 | Unit No. 2 is on bar delivering an average load of 5.82 MW according to the available inflow. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-09-06 | 2026 | 9 | 6 | Koto HPS | 40.8 | 13.75 | 12.68 | 304305 | 303345 | 40.9 | 39.16 | 31.08 | 8.24 | 63.59 | 58 | 622666.67 | 5130773.33 | 2499562.8 | 2631210.53 | 960 | Unit 03 is on bar delivering an average load of 12.68 MW according to avalible hydrology Unit 02 is s/by due to low hydrology unit#01 shutdown and under inspection of governor over speed issue | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-06 | 2026 | 9 | 6 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 15 | 17 | 0 | 4.671 | 71.5 | 70 | 44616 | 208401.34 | 0 | 208401.34 | 0 | Unit stands still due to turbine guide bearing maintenance under progress. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-09-06 | 2026 | 9 | 6 | Malakand-3 HPS | 81 | 51 | 46.84 | 1124082 | 1115230 | 51 | 30.52 | 57.82 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 3192568.92 | 2056668.65 | 8852 | As per available hydrology from Irrigation Department two units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-06 | 2026 | 9 | 6 | Pehur HPS | 18 | 12.04 | 9.09 | 218200 | 212000 | 21.2 | 13 | 50.51 | 3.767 | 66.67 | 41 | 288000 | 1084896 | 798604 | 286292 | 6200 | Plant remained operational throughout 24 hrs with restricted flow in the canal. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-09-06 | 2026 | 9 | 6 | Reshun HPS | 4.2 | 2.67 | 1.82 | 42000 | 41715 | 2.76 | 2.57 | 41.67 | 13.48 | 100 | 45 | 100800 | 1358784 | 562318.2 | 796465.8 | 285 | nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-09-07 | 2026 | 9 | 7 | Daral Khwar HPS | 36.6 | 15.3 | 13.6 | 326730 | 324730 | 15.6 | 5.43 | 37.2 | 8.2683 | 47.32 | 48 | 415666.67 | 3436856.7 | 2684965.06 | 751891.64 | 2000 | 1: Unit No. 03 was on bar delivering an average load equal to 13.6 MW according to the available hydrology and existing system constraints. 2: Unit No.02 stopped at 0001 Hrs for necessary maintenance and started Unit No. 03 at 0004 Hrs. 3: Unit No.01 standby due to low hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-09-07 | 2026 | 9 | 7 | Jabori HPS | 10.2 | 6 | 5.23 | 125591 | 124020 | 7.72 | 4.1 | 51.3 | 5.7092 | 84.89 | 79.57 | 207821.82 | 1186496.36 | 708054.98 | 478441.37 | 1571 | Both units eere on the bar delivering power according to the available hydrology and prevailing system constraints. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-09-07 | 2026 | 9 | 7 | Karora HPS | 11.8 | 5.92 | 5.39 | 129352 | 127712 | 8.77 | 4.69 | 45.68 | 7.78 | 69.09 | 0.69 | 195666.67 | 1522286.67 | 993599.36 | 528687.31 | 1640 | Unit No. 2 is on bar delivering an average load of 5.39 MW according to the available inflow. At 19:02 hrs, the complex was shut down to facilitate cleaning of the intake trash rack. Upon completion of the cleaning activity, Unit #02 was started and synchronized with the grid at 19:57 hrs. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-09-07 | 2026 | 9 | 7 | Koto HPS | 40.8 | 13.75 | 13.14 | 315280 | 314240 | 40.9 | 40.57 | 32.2 | 8.24 | 63.59 | 58 | 622666.67 | 5130773.33 | 2589337.6 | 2541435.73 | 1040 | Unit 3 is operational and delivering an average load of 13.14 MW. Unit 2 remains on standby due to low water availability. Unit 1 is unavailable and placed at the disposal of the EPC E&M team for detailed investigation and rectification of overspeed and upper guide bearing oil leak issues. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-07 | 2026 | 9 | 7 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 4.671 | 71.5 | 70 | 44616 | 208401.34 | 0 | 208401.34 | 0 | Unit stands still due to turbine guide bearing maintenance under progress. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-09-07 | 2026 | 9 | 7 | Malakand-3 HPS | 81 | 47 | 43 | 1032068 | 1022160 | 51 | 28.42 | 53.09 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 2926137.43 | 2323100.13 | 9908 | As per available hydrology from the Irrigation Department two Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-07 | 2026 | 9 | 7 | Pehur HPS | 18 | 12.02 | 9.2 | 220800 | 214000 | 21.22 | 13.5 | 51.11 | 3.767 | 66.67 | 41 | 288000 | 1084896 | 806138 | 278758 | 6800 | Plant remained off the bar from 1320 Hrs to 1350 Hrs due to 132 KV line fault, + low irrigation demand. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-09-07 | 2026 | 9 | 7 | Reshun HPS | 4.2 | 2.53 | 1.54 | 36000 | 35735 | 2.8 | 2.2 | 35.71 | 13.48 | 100 | 45 | 100800 | 1358784 | 481707.8 | 877076.2 | 265 | Line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-09-08 | 2026 | 9 | 8 | Daral Khwar HPS | 36.6 | 14 | 12.5 | 301110 | 299110 | 15.6 | 5 | 34.28 | 8.2683 | 47.32 | 48 | 415666.67 | 3436856.7 | 2473131.21 | 963725.49 | 2000 | 1: Unit No. 03 was on bar delivering an average load equal to 12.5 MW according to the available hydrology and existing system constraints. 2: Unit No. 01 and 02 standby due to low hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-09-08 | 2026 | 9 | 8 | Jabori HPS | 10.2 | 5.2 | 5.11 | 122660 | 121110 | 7.72 | 4.01 | 50.11 | 5.7092 | 84.89 | 79.57 | 207821.82 | 1186496.36 | 691441.21 | 495055.14 | 1550 | Unit # 02 delivered an average load of 5.11 MW to the national grid according to the available hydrology and prevailing system constraints. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-09-08 | 2026 | 9 | 8 | Karora HPS | 11.8 | 5.92 | 5.41 | 129820 | 128058 | 8.77 | 4.58 | 45.84 | 7.78 | 69.09 | 0.69 | 195666.67 | 1522286.67 | 996291.24 | 525995.43 | 1762 | Unit No. 2 is on bar delivering an average load of 5.41 MW according to the available inflow. "At 06:43 hrs, Unit No. 02 tripped with the 86T Lockout Relay alarm indication. Unit No. 02 was restarted and successfully synchronized with the system at 06:56 hrs. " | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-09-08 | 2026 | 9 | 8 | Koto HPS | 40.8 | 13.52 | 11.49 | 275870 | 274810 | 40.9 | 35.5 | 28.17 | 8.24 | 63.59 | 58 | 622666.67 | 5130773.33 | 2264434.4 | 2866338.93 | 1060 | Unit 3 is operational and delivering an average load of 11.49 MW. Unit 2 remains on standby due to low available hydrology. Unit 1 is unavailable and placed at the disposal of the EPC E&M team for detailed investigation and rectification of overspeed and upper guide bearing oil leak. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-08 | 2026 | 9 | 8 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 15.8 | 14 | 0 | 4.671 | 71.5 | 70 | 44616 | 208401.34 | 0 | 208401.34 | 0 | Unit stands still due to turbine guide bearing maintenance under progress. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-09-08 | 2026 | 9 | 8 | Malakand-3 HPS | 81 | 48 | 39.15 | 939718 | 929930 | 51 | 27.2 | 48.34 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 2662110.61 | 2587126.96 | 9788 | Unit #01 and Unit #02 tripped due to the tripping of the 132 kV incoming supply at 10:32hrs.Informed RCC. The 132 kV supply was restored at 10:38 hrs . Unit #02 was synchronized with the system at 10:52 hrs, and Unit #01 was synchronized with the system at 10:57 hrs. Voltage and frequency disturbances were observed. As per instructions from Mr. Nadeem (RCC), all generating units were desynchronized from the system due to frequency disturbance. Accordingly, the units were desynchronized at 20:45 hrs, at the same time the 132 kV supply failed while RCC was on line. After restoration of 132kV supply lines at 20:48hrs.Unit# 01 kept standby at 20:45hrs due to less hydrology Unit# 02 synchronized with the system at 21:03hrs while Unit# 03 synchronized with the system at 21:42hrs.As per available hydrology from the Irrigation Department two Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-08 | 2026 | 9 | 8 | Pehur HPS | 18 | 10.26 | 9.54 | 229000 | 222000 | 21.2 | 14 | 53.01 | 3.767 | 66.67 | 41 | 288000 | 1084896 | 836274 | 248622 | 7000 | Plant remained operational throughout 24 hrs. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-09-08 | 2026 | 9 | 8 | Reshun HPS | 4.2 | 2.66 | 1.61 | 35000 | 34712 | 2.2 | 2.8 | 34.72 | 13.48 | 100 | 45 | 100800 | 1358784 | 467917.76 | 890866.24 | 288 | Line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-09-09 | 2026 | 9 | 9 | Daral Khwar HPS | 36.6 | 12 | 11.6 | 278480 | 276480 | 15.6 | 4.62 | 31.7 | 8.2683 | 47.32 | 48 | 415666.67 | 3436856.7 | 2286019.58 | 1150837.12 | 2000 | 1: Unit No. 03 was on bar delivering an average load equal to 11.6 MW according to the available hydrology and existing system constraints. 2: Unit No.01 and 02 standby due to low hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-09-09 | 2026 | 9 | 9 | Jabori HPS | 10.2 | 5.15 | 5.13 | 123122 | 121550 | 7.72 | 4.02 | 50.29 | 5.7092 | 84.89 | 79.57 | 207821.82 | 1186496.36 | 693953.26 | 492543.1 | 1572 | Unit 02 delivered power to the national grid as per available hydrology. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-09-09 | 2026 | 9 | 9 | Karora HPS | 11.8 | 5.9 | 5.35 | 128395 | 126648 | 8.77 | 4.44 | 45.34 | 7.78 | 69.09 | 0.69 | 195666.67 | 1522286.67 | 985321.44 | 536965.23 | 1747 | Unit No. 2 is on bar delivering an average load of 5.35MW according to the available inflow. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-09-09 | 2026 | 9 | 9 | Koto HPS | 40.8 | 9.75 | 8.64 | 207392 | 206332 | 40.9 | 26.69 | 21.18 | 8.24 | 63.59 | 58 | 622666.67 | 5130773.33 | 1700175.68 | 3430597.65 | 1060 | Hydrology Impact: Plant average load and total generation decreased due to reduced inflow with the onset of the lean water period. Unit Status: Unit No. 3: Operational at an average load of 8.64 MW. Unit No. 2: On standby due to low hydrology. Unit No. 1: Handed over to the EPC E&M team to investigate governor response failure during tripping/load rejection, which is causing overspeed conditions and upper guide bearing oil leaks. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-09 | 2026 | 9 | 9 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 16 | 15 | 0 | 4.671 | 71.5 | 70 | 44616 | 208401.34 | 0 | 208401.34 | 0 | Unit stands still due to turbine guide bearing maintenance under progress. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-09-09 | 2026 | 9 | 9 | Malakand-3 HPS | 81 | 40 | 39.35 | 944362 | 934330 | 51 | 26.75 | 48.58 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 2674706.49 | 2574531.08 | 10032 | As per available hydrology from the Irrigation Department two Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-09 | 2026 | 9 | 9 | Pehur HPS | 18 | 11.84 | 10.32 | 247800 | 241000 | 21.2 | 15 | 57.36 | 3.767 | 66.67 | 41 | 288000 | 1084896 | 907847 | 177049 | 6800 | The plant remained operational throughout 24 hrs with restricted flow due to low irrigation demand. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-09-09 | 2026 | 9 | 9 | Reshun HPS | 4.2 | 2.51 | 1.57 | 38000 | 37705 | 2.8 | 2.32 | 37.7 | 13.48 | 100 | 45 | 100800 | 1358784 | 508263.4 | 850520.6 | 295 | Nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-09-10 | 2026 | 9 | 10 | Daral Khwar HPS | 36.6 | 11.1 | 10.9 | 262380 | 259980 | 15.6 | 4.35 | 29.87 | 8.2683 | 47.32 | 48 | 415666.67 | 3436856.7 | 2149592.63 | 1287264.07 | 2400 | 1: Unit No.03 was on bar delivering an average load equal to 10.9 MW according to the available hydrology and existing system constraints. 2: Unit No. 01 and 02 standby due to low hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-09-10 | 2026 | 9 | 10 | Jabori HPS | 10.2 | 5.1 | 5 | 120110 | 118560 | 7.72 | 3.93 | 49.06 | 5.7092 | 84.89 | 79.57 | 207821.82 | 1186496.36 | 676882.75 | 509613.6 | 1550 | 1: Unit # 02 delivered an average load of 5.0 MW to the national grid according to the available hydrology while unit # 01 remains on standby due to insufficient hydrological availability. 2: Unit # 02 was shutdown at 1815 Hrs for cleaning of cooling water strainer and was re-synchronized at 1835 Hrs after completion of the cleaning activity. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-09-10 | 2026 | 9 | 10 | Karora HPS | 11.8 | 6.18 | 4.81 | 115536 | 113874 | 8.77 | 4.02 | 40.8 | 7.78 | 69.09 | 0.69 | 195666.67 | 1522286.67 | 885939.72 | 636346.95 | 1662 | No data submitted for this date | rekarorahps2000@gmail.com | Added (date missing in source) | Row added: date missing in source, values estimated from neighbouring days | Estimated
2026-09-10 | 2026 | 9 | 10 | Koto HPS | 40.8 | 10.13 | 7.72 | 185178 | 184058 | 40.9 | 23.83 | 18.91 | 8.24 | 63.59 | 58 | 622666.67 | 5130773.33 | 1516637.92 | 3614135.41 | 1120 | Unit No. 3: Operational at an average load of 7.72 MW. Unit No. 2: On standby due to low hydrology. Unit No. 1: Handed over to the EPC E&M team to investigate governor response failure during tripping/load rejection, which is causing overspeed conditions and upper guide bearing oil leaks. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-10 | 2026 | 9 | 10 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 18 | 16 | 0 | 4.671 | 71.5 | 70 | 44616 | 208401.34 | 0 | 208401.34 | 0 | unit stand still due to turbine guide bearing maintenance under progress. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Generation_Data.xlsx
2026-09-10 | 2026 | 9 | 10 | Malakand-3 HPS | 81 | 40 | 38.28 | 918763 | 908470 | 51 | 25.85 | 47.26 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 2600677.07 | 2648560.5 | 10293 | As per available hydrology from the Irrigation Department two Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-10 | 2026 | 9 | 10 | Pehur HPS | 18 | 11.63 | 9.76 | 234200 | 228000 | 21.22 | 14.5 | 54.21 | 3.767 | 66.67 | 41 | 288000 | 1084896 | 858876 | 226020 | 6200 | Plant operational 24 Hrs. Generation is less because of restriction of flow in the canal. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-09-10 | 2026 | 9 | 10 | Reshun HPS | 4.2 | 2.52 | 1.56 | 37000 | 36739 | 2.8 | 2.26 | 36.71 | 13.48 | 100 | 45 | 100800 | 1358784 | 495241.72 | 863542.28 | 261 | Outgoing feeder breaker reamained off 1.07hour due to line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-09-11 | 2026 | 9 | 11 | Daral Khwar HPS | 36.6 | 15.3 | 10.7 | 256670 | 254670 | 15.6 | 4.26 | 29.22 | 8.2683 | 47.32 | 48 | 415666.67 | 3436856.7 | 2105687.96 | 1331168.74 | 2000 | 1: Unit No 03 was on bar delivering an average load equal to 10.7 MW according to the available hydrology and existing system constraints. 2: 132kV supply line failed at 1833 Hrs and restored at 1924Hrs. 3: Unit #3 synchronized with national grid at 1933Hrs. 4: Units No.01 and 2 standby due to low hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-09-11 | 2026 | 9 | 11 | Jabori HPS | 10.2 | 5.1 | 4.24 | 101660 | 100090 | 6.72 | 3.32 | 41.53 | 5.7092 | 84.89 | 79.57 | 207821.82 | 1186496.36 | 571433.83 | 615062.53 | 1570 | 1: Unit # 02 delivered an average load of 4.24 MW to the national grid according to the available hydrology while unit # 01 remains on standby due to insufficient hydrological availability. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-09-11 | 2026 | 9 | 11 | Karora HPS | 11.8 | 5.01 | 4.28 | 102677 | 101099 | 8.77 | 3.6 | 36.26 | 7.78 | 69.09 | 0.69 | 195666.67 | 1522286.67 | 786550.22 | 735736.45 | 1578 | 1. Unit No. 2 is on bar delivering an average load of 4.28 MW according to the available inflow. 2. The weir site team informed that heavy rainfall caused highly muddy water at intake. Accordingly, the plant was smoothly and safely shutdown at 22:25 hrs to avoid excessive silt and debris entering the system. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-09-11 | 2026 | 9 | 11 | Koto HPS | 40.8 | 13.6 | 8.36 | 200710 | 199650 | 40.9 | 25.83 | 20.5 | 8.24 | 63.59 | 58 | 622666.67 | 5130773.33 | 1645116 | 3485657.33 | 1060 | 1) Unit No. 3 Operational at an average load of 8.36 MW. 2) Unit 02 is stand by due to low hydrology. 3)As per the EPC Contractor’s instructions, Unit #03 was shut down at 11:40 hrs, and Unit #01 was started and synchronized at 11:45 hrs for testing and investigation of overspeed issue. As due to low hydrology both the units cannot be operated simultaneously. The issue in a solenoid valve was observed and will be replaced. Unit #01 shutdown and Unit#03 was restarted and synchronized at 12:35 hrs. 4) Unit #03 tripped at 18:05 hours due to back supply failure and resynchronized with the grid at 20:02 hours after restoration of back supply. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-11 | 2026 | 9 | 11 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 20 | 17 | 0 | 4.671 | 71.5 | 70 | 44616 | 208401.34 | 0 | 208401.34 | 0 | Unit stand still due to turbine guide bearing maintenance under progress. | engr.atifwazir@gmail.com | Original | Plant band (revenue 0) -> units 0; Plant factor recalculated; Avg load = Units / 24h; Max load estimated from Avg load | Generation_Data.xlsx
2026-09-11 | 2026 | 9 | 11 | Malakand-3 HPS | 81 | 40 | 36.83 | 883985 | 873960 | 51 | 25.04 | 45.47 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 2501885.29 | 2747352.28 | 10025 | As per available hydrology from the Irrigation Department two Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-11 | 2026 | 9 | 11 | Pehur HPS | 18 | 10.36 | 8.06 | 193500 | 187000 | 21.22 | 12 | 44.79 | 3.767 | 66.67 | 41 | 288000 | 1084896 | 704429 | 380467 | 6500 | At 2005 Hrs plant made shut down due to nil irrigation demand. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-09-11 | 2026 | 9 | 11 | Reshun HPS | 4.2 | 2.64 | 1.74 | 40000 | 39708 | 2.8 | 2.44 | 39.68 | 13.48 | 100 | 45 | 100800 | 1358784 | 535263.84 | 823520.16 | 292 | nil | zafar.src@gmail.com | Original | Avg Historical Hydrology interpolated from neighbouring days; Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-09-12 | 2026 | 9 | 12 | Daral Khwar HPS | 36.6 | 15.3 | 13 | 311500 | 309500 | 15.6 | 5.18 | 35.46 | 8.2683 | 47.32 | 48 | 415666.67 | 3436856.7 | 2559038.85 | 877817.85 | 2000 | 1: Unit No.03 was on bar delivering an average load equal to 13 MW according to the available hydrology and existing system constraints. 2: Unit No.01 and 02 standby due to low hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-09-12 | 2026 | 9 | 12 | Jabori HPS | 10.2 | 5.1 | 5 | 121850 | 120300 | 6.72 | 3.47 | 49.78 | 5.7092 | 84.89 | 79.57 | 207821.82 | 1186496.36 | 686816.76 | 499679.6 | 1550 | 1: Unit # 02 delivered an average load of 5.0 MW to the national grid according to the available hydrology while unit # 01 remains on standby due to insufficient hydrological availability. | faizanbabar5@gmail.com | Original | Actual Avg Cumic interpolated from neighbouring days | Generation_Data.xlsx
2026-09-12 | 2026 | 9 | 12 | Karora HPS | 11.8 | 5.3 | 2.37 | 56805 | 56034 | 8.77 | 2.11 | 20.06 | 7.78 | 69.09 | 0.69 | 195666.67 | 1522286.67 | 435944.52 | 1086342.15 | 771 | Unit No. 2 is on bar delivering an average load of 2.37 MW according to the available inflow. Following the improvement in water quality at intake site, the plant was smoothly and safely synchronized at 06:42 hrs with the Grid. At 11:22 hrs, Unit# 02 was shutdown for SADA signal testing purpose. At 13:06 hrs, trash-rack cleaning was in progress. AT 14:55 hrs, the weir site team informed the CCR that trash-Rack cleaning had been completed. Subsequently, Unit#02 was started and synchronized with the grid load gradually increased to 4MW. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-09-12 | 2026 | 9 | 12 | Koto HPS | 40.8 | 13.48 | 11.93 | 286305 | 285305 | 40.9 | 36.84 | 29.24 | 8.24 | 63.59 | 58 | 622666.67 | 5130773.33 | 2350913.2 | 2779860.13 | 1000 | Unit No. 3: Operational at an average load of 11.93 MW. Unit No. 2: On standby due to low hydrology. Unit No. 1: Handed over to the EPC E&M team to investigate governor response failure during tripping/load rejection, which is causing overspeed conditions and upper guide bearing oil leaks. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-12 | 2026 | 9 | 12 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 28.6 | 16 | 0 | 4.671 | 71.5 | 70 | 44616 | 208401.34 | 0 | 208401.34 | 0 | Unit stand still due to Turbine Guide bearing maintenance | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-09-12 | 2026 | 9 | 12 | Malakand-3 HPS | 81 | 40 | 38.82 | 931748 | 922490 | 51 | 26.25 | 47.93 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 2640812.12 | 2608425.44 | 9258 | As per available hydrology from the Irrigation Department two Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-12 | 2026 | 9 | 12 | Pehur HPS | 18 | 4.2 | 0.55 | 13400 | 13000 | 18 | 1 | 3.1 | 3.767 | 66.67 | 41 | 288000 | 1084896 | 48971 | 1035925 | 400 | Unit#01 started at 0755 Hrs and stopped at 2005 Hrs dt. 12-09-26, plant made shut down due to nil irrigation demand. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-09-12 | 2026 | 9 | 12 | Reshun HPS | 4.2 | 2.64 | 1.68 | 41000 | 40703 | 2.8 | 2.51 | 40.67 | 13.48 | 100 | 45 | 100800 | 1358784 | 548676.44 | 810107.56 | 297 | NIL | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-09-13 | 2026 | 9 | 13 | Daral Khwar HPS | 36.6 | 11.5 | 11 | 264060 | 262060 | 15.6 | 4.38 | 30.06 | 8.2683 | 47.32 | 48 | 415666.67 | 3436856.7 | 2166790.7 | 1270066 | 2000 | 1: Unit No.03 was on bar delivering an average load equal to 11 MW according to the available hydrology and existing system constraints. 2: Unit No.01 and 02 standby due to low hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-09-13 | 2026 | 9 | 13 | Jabori HPS | 10.2 | 5 | 4.6 | 111118 | 109680 | 6.72 | 3.63 | 45.39 | 5.7092 | 84.89 | 79.57 | 207821.82 | 1186496.36 | 626185.06 | 560311.3 | 1438 | Not reported | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-09-13 | 2026 | 9 | 13 | Karora HPS | 11.8 | 4.8 | 4.17 | 100062 | 98435 | 8.77 | 3.48 | 35.33 | 7.78 | 69.09 | 0.69 | 195666.67 | 1522286.67 | 765824.3 | 756462.37 | 1627 | 1.Unit No. 2 is on bar delivering an average load of 4.17 MW according to the available inflow. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-09-13 | 2026 | 9 | 13 | Koto HPS | 40.8 | 9.98 | 9.16 | 219802 | 218802 | 40.9 | 28.28 | 22.45 | 8.24 | 63.59 | 58 | 622666.67 | 5130773.33 | 1802928.48 | 3327844.85 | 1000 | Unit #03: Operational at an average load of 9.16 MW. Unit #02: On standby due to low hydrology. Unit #01: Handed over to the EPC E&M team for investigation of governor response failure during tripping/load rejection. The issue is causing over-speed condition and upper guide bearing oil leakage. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-13 | 2026 | 9 | 13 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 28.6 | 16 | 0 | 4.671 | 71.5 | 70 | 44616 | 208401.34 | 0 | 208401.34 | 0 | Unit stand still due to turbine guide bearing maintenance | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-09-13 | 2026 | 9 | 13 | Malakand-3 HPS | 81 | 40 | 38.34 | 920198 | 910290 | 51 | 26.22 | 47.34 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 2605887.18 | 2643350.38 | 9908 | As per available hydrology from the Irrigation Department two Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-13 | 2026 | 9 | 13 | Pehur HPS | 18 | 8.1 | 3.3 | 80300 | 78000 | 21.22 | 5.5 | 18.59 | 3.767 | 66.67 | 41 | 288000 | 1084896 | 293826 | 791070 | 2300 | Unit #01 and 02 synchronized at 1355 and 1400 hrs respectively with 4.0 MW load each, with restricted discharge of 12 cms. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-09-13 | 2026 | 9 | 13 | Reshun HPS | 4.2 | 2.72 | 1.75 | 41000 | 40780 | 2.8 | 2.51 | 40.67 | 13.48 | 100 | 45 | 100800 | 1358784 | 549714.4 | 809069.6 | 220 | Nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-09-14 | 2026 | 9 | 14 | Daral Khwar HPS | 36.6 | 10.5 | 9.9 | 237970 | 235970 | 15.6 | 3.95 | 27.09 | 8.2683 | 47.32 | 48 | 415666.67 | 3436856.7 | 1951070.75 | 1485785.95 | 2000 | 1: Unit No.03 was on bar delivering an average load equal to 9.9 MW according to the available hydrology and existing system constraints. 2: Unit No.01 and 02 standby due to low hydrology. 3: 132 KV Supply failed at 1844Hrs and restored 1918Hrs. 4: Unit No.03 synchronized with the national grid at 1932Hrs. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-09-14 | 2026 | 9 | 14 | Jabori HPS | 10.2 | 5 | 4.39 | 105380 | 103920 | 6.72 | 3.44 | 43.05 | 5.7092 | 84.89 | 79.57 | 207821.82 | 1186496.36 | 593300.06 | 593196.29 | 1460 | 1: Unit # 02 delivered an average load of 4.39 MW to the national grid according to the available hydrology while unit # 01 remains on standby due to insufficient hydrological availability. 2: 132kv transmission line tripped at 2003 Hrs. Line restored at 2034 Hrs. Subsequently unit 02 was synchronized at 2048 Hrs. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-09-14 | 2026 | 9 | 14 | Karora HPS | 11.8 | 4.9 | 3.82 | 91618 | 89951 | 8.77 | 3.21 | 32.35 | 7.78 | 69.09 | 0.69 | 195666.67 | 1522286.67 | 699818.78 | 822467.89 | 1667 | 1.Unit No. 2 is on bar delivering an average load of 3.82MW according to the available inflow. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-09-14 | 2026 | 9 | 14 | Koto HPS | 40.8 | 10.5 | 8.55 | 205246 | 204186 | 40.9 | 26.41 | 20.96 | 8.24 | 63.59 | 58 | 622666.67 | 5130773.33 | 1682492.64 | 3448280.69 | 1060 | Unit #03: Operational at an average load of 8.55 MW. Unit #02: On standby due to low hydrology. Unit #01: Handed over to the EPC E&M team for investigation of governor response failure during tripping/load rejection. The issue is causing over-speed condition and upper guide bearing oil leakage. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-14 | 2026 | 9 | 14 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 28.6 | 16 | 0 | 4.671 | 71.5 | 70 | 44616 | 208401.34 | 0 | 208401.34 | 0 | Unit stand still due to Turbine Guide bearing maintenance | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-09-14 | 2026 | 9 | 14 | Malakand-3 HPS | 81 | 39 | 36.2 | 868802 | 858680 | 51 | 24.77 | 44.69 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 2458143.24 | 2791094.33 | 10122 | As per available hydrology from the Irrigation Department two Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-14 | 2026 | 9 | 14 | Pehur HPS | 18 | 11.27 | 9.3 | 223400 | 217000 | 21.22 | 15 | 51.71 | 3.767 | 66.67 | 41 | 288000 | 1084896 | 817439 | 267457 | 6400 | Plant remained operational throughout 24 hrs with restricted discharge as per instructions of irrigation department. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-09-14 | 2026 | 9 | 14 | Reshun HPS | 4.2 | 2.71 | 1.6 | 39000 | 38790 | 2.8 | 2.38 | 38.69 | 13.48 | 100 | 45 | 100800 | 1358784 | 522889.2 | 835894.8 | 210 | Nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-09-15 | 2026 | 9 | 15 | Daral Khwar HPS | 36.6 | 10.3 | 10.1 | 242490 | 240490 | 6.47 | 4.02 | 27.61 | 8.2683 | 47.32 | 48 | 415666.67 | 3436856.7 | 1988443.47 | 1448413.23 | 2000 | 1: Unit No.03 was on bar delivering an average load equal to 10.1 MW according to the available hydrology and existing system constraints. 2: Unit No.01 and 02 standby due to low hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-09-15 | 2026 | 9 | 15 | Jabori HPS | 10.2 | 5 | 4.5 | 108680 | 107200 | 6.72 | 3.55 | 44.4 | 5.7092 | 84.89 | 79.57 | 207821.82 | 1186496.36 | 612026.24 | 574470.12 | 1480 | Not reported | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-09-15 | 2026 | 9 | 15 | Karora HPS | 11.8 | 4.9 | 2.6 | 62439 | 61558 | 8.77 | 2.08 | 22.05 | 7.78 | 69.09 | 0.69 | 195666.67 | 1522286.67 | 478921.24 | 1043365.43 | 881 | 1. Unit No. 2 is on bar delivering an average load of 2.60 MW according to the available inflow. 2. The weir site team informed that heavy rainfall caused highly muddy water at intake site. Accordingly, the plant was safely shut down at 15:40 hrs to prevent excessive silt and debris from entering the waterway. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-09-15 | 2026 | 9 | 15 | Koto HPS | 40.8 | 13.38 | 11.04 | 265071 | 263951 | 40.9 | 34.11 | 27.07 | 8.24 | 63.59 | 58 | 622666.67 | 5130773.33 | 2174956.24 | 2955817.09 | 1120 | 1. Unit #01: Operational at an average load of 11.04 MW. After installation of the solenoid valve filter the unit started and synchronized with the grid at 9:40 hours. The unit will remain under observation to check for governor over-speed issue during tripping/load rejection. 2. Unit #03: shutdown at 9:45 hours after starting unit #01 as both the units cannot be operated simultaneously due to low hydrology. 3. Unit #02 remains standby due to low hydrology. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-15 | 2026 | 9 | 15 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 28.6 | 16 | 0 | 4.671 | 71.5 | 70 | 44616 | 208401.34 | 0 | 208401.34 | 0 | Unit stand still due to Turbine Guide bearing maintenance | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-09-15 | 2026 | 9 | 15 | Malakand-3 HPS | 81 | 40 | 36.98 | 887634 | 877650 | 51 | 25.25 | 45.66 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 2512448.65 | 2736788.91 | 9984 | As per available hydrology from the Irrigation Department two Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-15 | 2026 | 9 | 15 | Pehur HPS | 18 | 11.27 | 8.82 | 211900 | 206000 | 21.2 | 14 | 49.05 | 3.767 | 66.67 | 41 | 288000 | 1084896 | 776002 | 308894 | 5900 | The plant remained operational throughout 24 hrs with restricted discharge as per instructions of the irrigation department. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-09-15 | 2026 | 9 | 15 | Reshun HPS | 4.2 | 2.63 | 1.63 | 38000 | 37800 | 2.8 | 2.32 | 37.7 | 13.48 | 100 | 45 | 100800 | 1358784 | 509544 | 849240 | 200 | Nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-09-16 | 2026 | 9 | 16 | Daral Khwar HPS | 36.6 | 21.3 | 11.1 | 266020 | 264020 | 6.47 | 4.42 | 30.28 | 8.2683 | 47.32 | 48 | 415666.67 | 3436856.7 | 2182996.57 | 1253860.13 | 2000 | 1: Units No. 01 and 03 were on bar delivering an average load equal to 11.1 MW according to the available hydrology and existing system constraints. 2: 132KV supply line failed at 18:53 Hrs and restored at 19:42Hrs. 3: Unit No.03 Synchronized with the National grid at 19:50Hrs. 4: Unit No.01 Synchronized with the National grid at 21:04Hrs due to increased Hydrology. 5: Unit No.02 is on Standby due to low Hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-09-16 | 2026 | 9 | 16 | Jabori HPS | 10.2 | 5 | 4.5 | 108530 | 107000 | 6.72 | 3.55 | 44.33 | 5.7092 | 84.89 | 79.57 | 207821.82 | 1186496.36 | 610884.4 | 575611.96 | 1530 | Plant operational as per available hydrology | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-09-16 | 2026 | 9 | 16 | Karora HPS | 11.8 | 7.8 | 2.11 | 50815 | 50745 | 8.77 | 1.64 | 17.94 | 7.78 | 69.09 | 0.69 | 195666.67 | 1522286.67 | 394796.1 | 1127490.57 | 70 | 1.Unit No. 2 is on bar delivering an average load of 2.11 MW according to the available inflow. 2. "Unit No. 02 was started and synchronized with the system at 04:18 hrs, and its load was gradually increased to 5.9 MW after the water conditions normalized. Subsequently, Unit No. 01 was started and synchronized with the system at 05:18 hrs, and its load was gradually increased to 3.0 MW as per the available hydrology. " 3 "At 08:12 hrs, Unit No. 01 mechanically tripped due to a shear pin fault. Following rectification of the shear pin fault, Unit No. 01 was restarted and re-synchronized with the system at 09:44 hrs. Subsequently, Unit No. 01 tripped again on Rotor Earth Fault protection, resulting in the tripping of MTR-1 (K1Q1). Consequently, Unit No. 02 also tripped due to loss of the associated auxiliary power supply. " 4 "After resetting all alarms, Unit No. 02 was restarted and re-synchronized with the system at 10:16 hrs, and its load was gradually increased to 5.9 MW as per the available hydrology. " 5 "At 13: 06hrs, The Unit No. 02 was shut down in connection with PTW No. 52/2026, issued at the request of the EPC Contractor to facilitate excavation and removal of accumulated silt and boulders from the intake area through the flood gates. " | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-09-16 | 2026 | 9 | 16 | Koto HPS | 40.8 | 13.02 | 10.4 | 249540 | 248500 | 40.9 | 32.11 | 25.48 | 8.24 | 63.59 | 58 | 622666.67 | 5130773.33 | 2047640 | 3083133.33 | 1040 | Unit 01 is on bar delivering an average load of 10.40 MW and will remain under observation to check governor over speed issue. Unit 02,03 are stand by due to low hydrology. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-16 | 2026 | 9 | 16 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 18 | 16 | 0 | 4.671 | 71.5 | 70 | 44616 | 208401.34 | 0 | 208401.34 | 0 | Unit stand still due to Turbine Guide bearing maintenance. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-09-16 | 2026 | 9 | 16 | Malakand-3 HPS | 81 | 40 | 38.67 | 928198 | 918400 | 51 | 26.76 | 47.75 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 2629103.68 | 2620133.89 | 9798 | As per available hydrology from Irrigation Department two units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-16 | 2026 | 9 | 16 | Pehur HPS | 18 | 10.16 | 6.63 | 159100 | 155000 | 21.2 | 10 | 36.83 | 3.767 | 66.67 | 41 | 288000 | 1084896 | 583885 | 501011 | 4100 | Generation is less because 1) Restriction of flow in the canal from irrigation department. 2) Plant remained shut down for 24 hours upon instructions of irrigation department in search of dead body in the canal. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-09-16 | 2026 | 9 | 16 | Reshun HPS | 4.2 | 2.55 | 1.6 | 38000 | 37790 | 2.8 | 2.32 | 37.7 | 13.48 | 100 | 45 | 100800 | 1358784 | 509409.2 | 849374.8 | 210 | Nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-09-17 | 2026 | 9 | 17 | Daral Khwar HPS | 36.6 | 21.3 | 17 | 407640 | 405640 | 6.47 | 6.78 | 46.41 | 8.2683 | 47.32 | 48 | 415666.67 | 3436856.7 | 3353953.21 | 82903.49 | 2000 | 1: Unit No.01 and 03 were on bar delivering an average load equal to 17 MW according to the available hydrology and existing system constraints. 2: Unit No. Stopped at 11:33 Hrs due to low hydrology. 3: Unit No.01 and 02 standby due to low hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-09-17 | 2026 | 9 | 17 | Jabori HPS | 10.2 | 5.1 | 4.98 | 119440 | 118000 | 6.72 | 3.9 | 48.79 | 5.7092 | 84.89 | 79.57 | 207821.82 | 1186496.36 | 673685.6 | 512810.76 | 1440 | 1: Unit # 02 delivered an average load of 4.98 MW to the national grid according to the available hydrology while unit # 01 remains on standby due to insufficient hydrological availability. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-09-17 | 2026 | 9 | 17 | Karora HPS | 11.8 | 5.9 | 1.04 | 25051 | 25162 | 8.77 | 1 | 8.85 | 7.78 | 69.09 | 0.69 | 195666.67 | 1522286.67 | 195760.36 | 1326526.31 | 111 | 1.Unit No. 2 is on bar delivering an average load of 1.04 MW according to the available inflow. 2.After cleaning activity carried out at Intake site, the Unit # 01 was started on FSNL and remained at FSNL for approximately 16 minutes. The unit was synchronized with the system at 19:14 hrs, and its load was gradually increased to 5.9 MW, as per the available hydrology. 3.At 20:04 hrs, a rotor earth fault alarm was observed in the event list and physically verified on the panel. The GRC representative was informed accordingly. Following an inspection by the operation team and the GRC representative, the operation team decided to shut down Unit 01 as a precautionary measure to ensure the safety of the machine. 4.Unit # 02 was started and synchronized with the system at 20:54 hrs, and its load was gradually increased to 5.9 MW, as per the available hydrology. | rekarorahps2000@gmail.com | Original | CHECK: Net > Units (source me verify karein) | Generation_Data.xlsx
2026-09-17 | 2026 | 9 | 17 | Koto HPS | 40.8 | 13.57 | 13.38 | 321194 | 320134 | 40.9 | 41.33 | 32.8 | 8.24 | 63.59 | 58 | 622666.67 | 5130773.33 | 2637904.16 | 2492869.17 | 1060 | Unit 01 is on bar delivering an average load of 13.38 MW and will remain under observation to check governor over speed issue Unit 02,03 are stand by due to low hydrology. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-17 | 2026 | 9 | 17 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 18 | 18 | 0 | 4.671 | 71.5 | 70 | 44616 | 208401.34 | 0 | 208401.34 | 0 | Unit stand still due to Turbine Guide bearing maintenance. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-09-17 | 2026 | 9 | 17 | Malakand-3 HPS | 81 | 49 | 39.25 | 941967 | 931980 | 51 | 26.62 | 48.46 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 2667979.15 | 2581258.42 | 9987 | As per available hydrology from Irrigation Department two units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-17 | 2026 | 9 | 17 | Pehur HPS | 18 | 9.18 | 8.48 | 203700 | 198000 | 21.22 | 13 | 47.15 | 3.767 | 66.67 | 41 | 288000 | 1084896 | 745866 | 339030 | 5700 | "Generation is less because of restriction of flow in the canal from irrigation department. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-09-17 | 2026 | 9 | 17 | Reshun HPS | 4.2 | 2.63 | 1.57 | 37000 | 36810 | 2.8 | 2.26 | 36.71 | 13.48 | 100 | 45 | 100800 | 1358784 | 496198.8 | 862585.2 | 190 | Line faults. | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-09-18 | 2026 | 9 | 18 | Daral Khwar HPS | 36.6 | 15.3 | 14.6 | 350080 | 348480 | 6.47 | 5.83 | 39.85 | 8.2683 | 47.32 | 48 | 415666.67 | 3436856.7 | 2881337.18 | 555519.52 | 1600 | 1: Unit No.03 was on bar delivering an average load equal to 14.6 MW according to the available hydrology and existing system constraints. 2: Unit No. 01 and 02 are on standby due to low hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-09-18 | 2026 | 9 | 18 | Jabori HPS | 10.2 | 5.4 | 5.3 | 127564 | 126130 | 6.72 | 4.17 | 52.11 | 5.7092 | 84.89 | 79.57 | 207821.82 | 1186496.36 | 720101.4 | 466394.96 | 1434 | 1: Unit # 02 delivered an average load of 5.3 MW to the national grid according to the available hydrology while unit # 01 remains on standby due to insufficient hydrological availability. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-09-18 | 2026 | 9 | 18 | Karora HPS | 11.8 | 5.94 | 2.07 | 49607 | 49324 | 8.77 | 1.6 | 17.52 | 7.78 | 69.09 | 0.69 | 195666.67 | 1522286.67 | 383740.72 | 1138545.95 | 283 | 1) Unit No. 2 was on bar delivering an average load of 2.07 MW according to the available inflow. 2) Unit # 02 was Shutdown at 8:46 Hrs, as per the request of GRC representative under PTW # 52/2026 for the Excavation and removal of soil, gravel and sediments from flood gate side. 3) Unit #01 remained shutdown since 20:34 hrs on 17-09-2026 due to rotor Earth fault. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-09-18 | 2026 | 9 | 18 | Koto HPS | 40.8 | 13.65 | 12.2 | 292906 | 291886 | 40.9 | 37.69 | 29.91 | 8.24 | 63.59 | 58 | 622666.67 | 5130773.33 | 2405140.64 | 2725632.69 | 1020 | Unit 01 is on bar delivering an average load of 12.20 MW and will remain under observation to check governor over speed issue. Unit 02,03 are stand by due to low hydrology. Plant was shutdown from 11:30 to12:45 due to trash rack cleaning at intack | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-18 | 2026 | 9 | 18 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 18 | 18 | 0 | 4.671 | 71.5 | 70 | 44616 | 208401.34 | 0 | 208401.34 | 0 | Unit stand still due to Turbine Guide bearing maintenance. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-09-18 | 2026 | 9 | 18 | Malakand-3 HPS | 81 | 41 | 39.01 | 936183 | 926010 | 51 | 27.1 | 48.16 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 2650888.83 | 2598348.74 | 10173 | As per available hydrology from Irrigation Department two units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-18 | 2026 | 9 | 18 | Pehur HPS | 18 | 10.16 | 9.13 | 219100 | 213000 | 21.22 | 14 | 50.72 | 3.767 | 66.67 | 41 | 288000 | 1084896 | 802371 | 282525 | 6100 | Generation is less because of restriction of flow in the canal. Tripping of 132 KV line supply from Gadoon grid for 30 mints. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-09-18 | 2026 | 9 | 18 | Reshun HPS | 4.2 | 2.68 | 1.66 | 40000 | 39785 | 2.8 | 2.44 | 39.68 | 13.48 | 100 | 45 | 100800 | 1358784 | 536301.8 | 822482.2 | 215 | Nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx
2026-09-19 | 2026 | 9 | 19 | Daral Khwar HPS | 36.6 | 13.5 | 13.2 | 317540 | 315940 | 6.47 | 6.28 | 36.15 | 8.2683 | 47.32 | 48 | 415666.67 | 3436856.7 | 2612286.7 | 824570 | 1600 | 1: Unit No.03 was on bar delivering an average load equal to 13.2 MW according to the available hydrology and existing system constraints. 2: Unit No.01 and 02 are on standby due to low hydrology. | passion.to.programe@gmail.com | Original |  | Generation_Data.xlsx
2026-09-19 | 2026 | 9 | 19 | Jabori HPS | 10.2 | 5.1 | 3.2 | 78504 | 77370 | 6.72 | 2.57 | 32.07 | 5.7092 | 84.89 | 79.57 | 207821.82 | 1186496.36 | 441720.8 | 744775.55 | 1134 | 1: Unit # 02 delivered an average load of 4.98 MW to the national grid according to the available hydrology while unit # 01 remains on standby due to insufficient hydrological availability. 2: plant was shutdown at 1010 Hrs for flushing o one section of the sand trap. Alongside the flushing activity, emergency work has also been initiated and excavation of already chocked sand trap has been started. After the activity, unit 02 was synchronized at 1715 Hrs. | faizanbabar5@gmail.com | Original |  | Generation_Data.xlsx
2026-09-19 | 2026 | 9 | 19 | Karora HPS | 11.8 | 4.61 | 1.02 | 24361 | 24331 | 8.77 | 0.84 | 8.6 | 7.78 | 69.09 | 0.69 | 195666.67 | 1522286.67 | 189295.18 | 1332991.49 | 30 | 1) Unit 02 was on bar delivering an average load of 1.02 MW to the system according to the available inflow 2) Unit 02 was synchronized with system at 18:05 Hrs and load gradually increased to 5.9 MW 3) Unit 01 remained shutdown since 20:34 Hrs on 17-09-2026 due to rotor earth fault. | rekarorahps2000@gmail.com | Original |  | Generation_Data.xlsx
2026-09-19 | 2026 | 9 | 19 | Koto HPS | 40.8 | 13.25 | 11.95 | 286905 | 285925 | 40.9 | 36.92 | 29.3 | 8.24 | 63.59 | 58 | 622666.67 | 5130773.33 | 2356022 | 2774751.33 | 980 | Unit 01 is on bar, delivering an average load of 11.95 MW, and remains under observation to monitor governor response during overspeed conditions. Units 02 and 03 are on standby due to low hydrology. Overall power generation was reduced due to seasonally low hydrology, with inflows averaging 36.92 cumecs against the historical average of 40.9 cumecs. | rekotohpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-19 | 2026 | 9 | 19 | Machai HPS | 2.6 | 0 | 0 | 0 | 0 | 18 | 18 | 0 | 4.671 | 71.5 | 70 | 44616 | 208401.34 | 0 | 208401.34 | 0 | Unit stand still due to Turbine Guide bearing maintenance. | engr.atifwazir@gmail.com | Original |  | Generation_Data.xlsx
2026-09-19 | 2026 | 9 | 19 | Malakand-3 HPS | 81 | 40 | 36.97 | 887389 | 878010 | 51 | 25.21 | 45.65 | 2.8627 | 94.32 | 77.5 | 1833666.67 | 5249237.57 | 2513479.23 | 2735758.34 | 9379 | As per available hydrology from the Irrigation Department two Units are on bar. | malakand03hpc@gmail.com | Original |  | Generation_Data.xlsx
2026-09-19 | 2026 | 9 | 19 | Pehur HPS | 18 | 10.15 | 9.47 | 227200 | 220000 | 21.22 | 14 | 52.59 | 3.767 | 66.67 | 41 | 288000 | 1084896 | 828740 | 256156 | 7200 | Plant remained operational throughout 24 hrs with restricted flow from irrigation department. | phpcmw18@gmail.com | Original |  | Generation_Data.xlsx
2026-09-19 | 2026 | 9 | 19 | Reshun HPS | 4.2 | 2.51 | 1.62 | 39000 | 38810 | 2.8 | 2.38 | 38.69 | 13.48 | 100 | 45 | 100800 | 1358784 | 523158.8 | 835625.2 | 190 | Nil | zafar.src@gmail.com | Original | Expected gen estimated from plant-month design plant factor | Generation_Data.xlsx

## Previous_Years_Clean
Power Plant | Capacity (MW) | FY Start | FY End | Financial Year | Annual Energy (GWH) | Actual Generation (GWH) | Auxiliary Consumption (GWH) | NEO (GWH) | Generation Difference (GWH) | Total Revenue (Mill. Rs) | Total Expenditures (Mill. Rs) | Net Profit (Mill. Rs) | Reasons for Variance | Remarks | Previous Year Revenue | Previous Year Expenditure | Previous Year Net Profit | Revenue Growth % | Expenditure Growth % | Performance Indicator | Profit Margin | Interpretation | Score | Fin Health | Status Label | Auto Interpretation | Actions Required
Daral Khwar HPS | 36.6 | 2018-07-01 | 2019-06-30 | 2018-2019 | 154 | 13.3 | 0.22205 | 13.3 | -141 | 3 | 6 | -3 | Less Hydrology and Change in Hydrological Trends Due to Climate Changes 1- The annual energy estimated in energy computations sheet is based on average monthly discharges in Daral Khwar from 1961-2012. However, due to climate changes the hydrological trend has changed in Daral Khwar in the past five years. A dry year was witnessed in 2021 followed by torrential rains & flash flood in August 2022 and medium floods in April 2024. 2- Daral Khwar HPC sustained damages due to the devasting flood in August-2022. The powerhouse remained stand-by for almost a month in 2022 due to emergency rehabilitation work at weir site. Although the water way was cleared, and plant was operationalized in a record time but the presence of overburden material upstream of weir caused difficulties for smooth operation of the power plant resulting in an overall less annual energy generation in 2022 & 2023. The debris accumulation upstream of intake channel was cleared with successful operation of flushing gates after necessary works at downstream, in August 2023. 3- The annual energy 154 GWh for Daral Khwar HPC is based on a gross capacity 36.6 MW (including auxiliaries). While the tariff petition is based on the assumptions of the annual plant factor of 48%, auxiliary consumption of 0.366 MW. The energy based on net capacity of 36.23 MW comes out to be 152.34 GWh. Moreover, it is pertinent to mention that the Energy Purchase Agreement is take-and-pay basis. | (1).Generation from the date of installation of primary energy meters 08-10-2019 (2). Revenue at pre-COD tariff of Rs.0.2228 | [5 empty] | 0 | -1 | Stable: Revenue and expenditure are growing at the same pace | 1.6 | Poor | 🔴 | Declining revenue or high expenditure with low profitability | Immediate management intervention required; perform financial and technical audit; reduce operational costs urgently; identify causes of low revenue; address outages and inefficiencies; consider restructuring or rehabilitation plan
Daral Khwar HPS | 36.6 | 2019-07-01 | 2020-06-30 | 2019-2020 | 154 | 157.3 | 1.2246 | 157.3 | 3 | 35.1 | 16 | 19 | Less Hydrology and Change in Hydrological Trends Due to Climate Changes 1- The annual energy estimated in energy computations sheet is based on average monthly discharges in Daral Khwar from 1961-2012. However, due to climate changes the hydrological trend has changed in Daral Khwar in the past five years. A dry year was witnessed in 2021 followed by torrential rains & flash flood in August 2022 and medium floods in April 2024. 2- Daral Khwar HPC sustained damages due to the devasting flood in August-2022. The powerhouse remained stand-by for almost a month in 2022 due to emergency rehabilitation work at weir site. Although the water way was cleared, and plant was operationalized in a record time but the presence of overburden material upstream of weir caused difficulties for smooth operation of the power plant resulting in an overall less annual energy generation in 2022 & 2023. The debris accumulation upstream of intake channel was cleared with successful operation of flushing gates after necessary works at downstream, in August 2023. 3- The annual energy 154 GWh for Daral Khwar HPC is based on a gross capacity 36.6 MW (including auxiliaries). While the tariff petition is based on the assumptions of the annual plant factor of 48%, auxiliary consumption of 0.366 MW. The energy based on net capacity of 36.23 MW comes out to be 152.34 GWh. Moreover, it is pertinent to mention that the Energy Purchase Agreement is take-and-pay basis. | Revenue at pre-COD tariff of Rs.0.2228 | 3 | 6 | -3 | 10.7 | -7.3333 | 18.0333 | 0.54131 | Efficient Plant: Revenue growth exceeds expenditure growth | 3 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Daral Khwar HPS | 36.6 | 2020-07-01 | 2021-06-30 | 2020-2021 | 154 | 108.9 | 1.1435 | 108.9 | -45 | 584.9 | 65 | 520 | Less Hydrology and Change in Hydrological Trends Due to Climate Changes 1- The annual energy estimated in energy computations sheet is based on average monthly discharges in Daral Khwar from 1961-2012. However, due to climate changes the hydrological trend has changed in Daral Khwar in the past five years. A dry year was witnessed in 2021 followed by torrential rains & flash flood in August 2022 and medium floods in April 2024. 2- Daral Khwar HPC sustained damages due to the devasting flood in August-2022. The powerhouse remained stand-by for almost a month in 2022 due to emergency rehabilitation work at weir site. Although the water way was cleared, and plant was operationalized in a record time but the presence of overburden material upstream of weir caused difficulties for smooth operation of the power plant resulting in an overall less annual energy generation in 2022 & 2023. The debris accumulation upstream of intake channel was cleared with successful operation of flushing gates after necessary works at downstream, in August 2023. 3- The annual energy 154 GWh for Daral Khwar HPC is based on a gross capacity 36.6 MW (including auxiliaries). While the tariff petition is based on the assumptions of the annual plant factor of 48%, auxiliary consumption of 0.366 MW. The energy based on net capacity of 36.23 MW comes out to be 152.34 GWh. Moreover, it is pertinent to mention that the Energy Purchase Agreement is take-and-pay basis. | Revenue at pre-COD tariff of Rs.0.2228 till 26-05-2021 | 35.1 | 16 | 19 | 15.6638 | 26.3684 | -10.7046 | 0.88904 | Cost Pressure: Expenditure growth is higher than revenue growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Daral Khwar HPS | 36.6 | 2021-07-01 | 2022-06-30 | 2021-2022 | 154 | 136.6 | 1.2178 | 136.1 | -17 | 1125.5 | 241 | 884 | Less Hydrology and Change in Hydrological Trends Due to Climate Changes 1- The annual energy estimated in energy computations sheet is based on average monthly discharges in Daral Khwar from 1961-2012. However, due to climate changes the hydrological trend has changed in Daral Khwar in the past five years. A dry year was witnessed in 2021 followed by torrential rains & flash flood in August 2022 and medium floods in April 2024. 2- Daral Khwar HPC sustained damages due to the devasting flood in August-2022. The powerhouse remained stand-by for almost a month in 2022 due to emergency rehabilitation work at weir site. Although the water way was cleared, and plant was operationalized in a record time but the presence of overburden material upstream of weir caused difficulties for smooth operation of the power plant resulting in an overall less annual energy generation in 2022 & 2023. The debris accumulation upstream of intake channel was cleared with successful operation of flushing gates after necessary works at downstream, in August 2023. 3- The annual energy 154 GWh for Daral Khwar HPC is based on a gross capacity 36.6 MW (including auxiliaries). While the tariff petition is based on the assumptions of the annual plant factor of 48%, auxiliary consumption of 0.366 MW. The energy based on net capacity of 36.23 MW comes out to be 152.34 GWh. Moreover, it is pertinent to mention that the Energy Purchase Agreement is take-and-pay basis. | No remarks | 584.9 | 65 | 520 | 0.92426 | 0.7 | 0.22426 | 0.78543 | Efficient Plant: Revenue growth exceeds expenditure growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Daral Khwar HPS | 36.6 | 2022-07-01 | 2023-06-30 | 2022-2023 | 154 | 121.6 | 1.07 | 120.5 | -32 | 996.3 | 362 | 635 | Less Hydrology and Change in Hydrological Trends Due to Climate Changes 1- The annual energy estimated in energy computations sheet is based on average monthly discharges in Daral Khwar from 1961-2012. However, due to climate changes the hydrological trend has changed in Daral Khwar in the past five years. A dry year was witnessed in 2021 followed by torrential rains & flash flood in August 2022 and medium floods in April 2024. 2- Daral Khwar HPC sustained damages due to the devasting flood in August-2022. The powerhouse remained stand-by for almost a month in 2022 due to emergency rehabilitation work at weir site. Although the water way was cleared, and plant was operationalized in a record time but the presence of overburden material upstream of weir caused difficulties for smooth operation of the power plant resulting in an overall less annual energy generation in 2022 & 2023. The debris accumulation upstream of intake channel was cleared with successful operation of flushing gates after necessary works at downstream, in August 2023. 3- The annual energy 154 GWh for Daral Khwar HPC is based on a gross capacity 36.6 MW (including auxiliaries). While the tariff petition is based on the assumptions of the annual plant factor of 48%, auxiliary consumption of 0.366 MW. The energy based on net capacity of 36.23 MW comes out to be 152.34 GWh. Moreover, it is pertinent to mention that the Energy Purchase Agreement is take-and-pay basis. | No remarks | 1125.5 | 241 | 884 | -0.11479 | -0.28167 | 0.16688 | 0.63736 | Efficient Plant: Revenue growth exceeds expenditure growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Daral Khwar HPS | 36.6 | 2023-07-01 | 2024-06-30 | 2023-2024 | 154 | 153.8 | 0.72615 | 153.3 | 0 | 1267.2 | 211 | 1057 | Outages due to Unavailability of Transmission Line Daral Khwar HPC is interconnected to Madyan Grid (PESCO) via 132 KV D/C transmission line. During maintenance activities by PESCO in their transmission/ distribution network, the powerhouse remains shutdown due to unavailability of transmission line. | No remarks | 996.3 | 362 | 635 | 0.27191 | 0.66457 | -0.39266 | 0.83412 | Cost Pressure: Expenditure growth is higher than revenue growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Daral Khwar HPS | 36.6 | 2024-07-01 | 2025-06-30 | 2024-2025 | 6.18 | 5.7 | 0.19437 | 5.7 | -1 | 46.8 | 41 | 6 | Outages due to Unavailability of Transmission Line Daral Khwar HPC is interconnected to Madyan Grid (PESCO) via 132 KV D/C transmission line. During maintenance activities by PESCO in their transmission/ distribution network, the powerhouse remains shutdown due to unavailability of transmission line. | Till February 2025 | 1267.2 | 211 | 1057 | -0.96307 | -0.99432 | 0.031255 | 0.12821 | Efficient Plant: Revenue growth exceeds expenditure growth | 2 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Machai HPS | 2.6 | 2016-07-01 | 2017-06-30 | 2016-2017 | 15.784 | 0.26908 | 0.006707 | 0.26234 | 15.5149 | 0.12 | 9.96 | -9.84 | TL of the station was handed over to PESCO,but PESCO does not execute repair and maintenance of the line whenever a fault occurs. High busbar voltage of PESCO grid is responsible for the high stator winding temperature and less generation.Annual Canal Closure for a period of forty days,and weekly supply weekly closure schedule from late October to March every year. | The station synchronized with PESCO grid on 24-11-2016 | [5 empty] | 0 | -82 | Stable: Revenue and expenditure are growing at the same pace | 1.6 | Poor | 🔴 | Declining revenue or high expenditure with low profitability | Immediate management intervention required; perform financial and technical audit; reduce operational costs urgently; identify causes of low revenue; address outages and inefficiencies; consider restructuring or rehabilitation plan
Machai HPS | 2.6 | 2017-07-01 | 2018-06-30 | 2017-2018 | 15.784 | 4.6031 | 0.13249 | 4.4706 | 11.1809 | 1.26 | 18.98 | -17.72 | TL of the station was handed over to PESCO,but PESCO does not execute repair and maintenance of the line whenever a fault occurs. High busbar voltage of PESCO grid is responsible for the high stator winding temperature and less generation.Annual Canal Closure for a period of forty days,and weekly supply weekly closure schedule from late October to March every year. | EPA was signed between PEDO & PESCO on 08-08-2024.Invoices have been submitted to PESCO.All the arrears will be released to PEDO. Pre COD Tariff @Rs.0.2394 from 24-11-2016 to 21-05-2020 | 0.12 | 9.96 | -9.84 | 9.5 | 0.80081 | 8.6992 | -14.0635 | Efficient Plant: Revenue growth exceeds expenditure growth | 1.6 | Poor | 🔴 | Declining revenue or high expenditure with low profitability | Immediate management intervention required; perform financial and technical audit; reduce operational costs urgently; identify causes of low revenue; address outages and inefficiencies; consider restructuring or rehabilitation plan
Machai HPS | 2.6 | 2018-07-01 | 2019-06-30 | 2018-2019 | 15.784 | 5.7907 | 0.15812 | 5.6325 | 9.9933 | 1.59 | 18.36 | -16.77 | TL of the station was handed over to PESCO,but PESCO does not execute repair and maintenance of the line whenever a fault occurs. High busbar voltage of PESCO grid is responsible for the high stator winding temperature and less generation.Annual Canal Closure for a period of forty days,and weekly supply weekly closure schedule from late October to March every year. | No remarks | 1.26 | 18.98 | -17.72 | 0.2619 | -0.053612 | 0.31552 | -10.5472 | Efficient Plant: Revenue growth exceeds expenditure growth | 2.2 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Machai HPS | 2.6 | 2019-07-01 | 2020-06-30 | 2019-2020 | 15.784 | 5.0358 | 0.13905 | 4.8967 | 10.7482 | 8.42 | 24.68 | -16.26 | TL of the station was handed over to PESCO,but PESCO does not execute repair and maintenance of the line whenever a fault occurs. High busbar voltage of PESCO grid is responsible for the high stator winding temperature and less generation.Annual Canal Closure for a period of forty days,and weekly supply weekly closure schedule from late October to March every year. | 2019-21st May,2020 | 1.59 | 18.36 | -16.77 | 4.2956 | -0.030411 | 4.326 | -1.9311 | Efficient Plant: Revenue growth exceeds expenditure growth | 2.2 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Machai HPS | 2.6 | 2020-07-01 | 2021-06-30 | 2020-2021 | 15.784 | 7.1254 | 0.19438 | 6.931 | 8.6586 | 38.2 | 27.51 | 10.69 | TL of the station was handed over to PESCO,but PESCO does not execute repair and maintenance of the line whenever a fault occurs. High busbar voltage of PESCO grid is responsible for the high stator winding temperature and less generation.Annual Canal Closure for a period of forty days,and weekly supply weekly closure schedule from late October to March every year. | Post COD Tariff @Rs.4.6710 from 22-05-2020 | 8.42 | 24.68 | -16.26 | 3.5368 | -1.6574 | 5.1943 | 0.27984 | Efficient Plant: Revenue growth exceeds expenditure growth | 3 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Machai HPS | 2.6 | 2021-07-01 | 2022-06-30 | 2021-2022 | 15.784 | 9.0969 | 0.24032 | 8.8566 | 6.6871 | 48.82 | 36.28 | 12.54 | TL of the station was handed over to PESCO,but PESCO does not execute repair and maintenance of the line whenever a fault occurs. High busbar voltage of PESCO grid is responsible for the high stator winding temperature and less generation.Annual Canal Closure for a period of forty days,and weekly supply weekly closure schedule from late October to March every year. | No remarks | 38.2 | 27.51 | 10.69 | 0.27801 | 0.17306 | 0.10495 | 0.25686 | Efficient Plant: Revenue growth exceeds expenditure growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Machai HPS | 2.6 | 2022-07-01 | 2023-06-30 | 2022-2023 | 15.784 | 7.1128 | 0.20582 | 6.907 | 8.6712 | 38.07 | 35.78 | 2.29 | TL of the station was handed over to PESCO,but PESCO does not execute repair and maintenance of the line whenever a fault occurs. High busbar voltage of PESCO grid is responsible for the high stator winding temperature and less generation.Annual Canal Closure for a period of forty days,and weekly supply weekly closure schedule from late October to March every year. | No remarks | 48.82 | 36.28 | 12.54 | -0.2202 | -0.81738 | 0.59719 | 0.060152 | Efficient Plant: Revenue growth exceeds expenditure growth | 1.6 | Poor | 🔴 | Declining revenue or high expenditure with low profitability | Immediate management intervention required; perform financial and technical audit; reduce operational costs urgently; identify causes of low revenue; address outages and inefficiencies; consider restructuring or rehabilitation plan
Machai HPS | 2.6 | 2023-07-01 | 2024-06-30 | 2023-2024 | 15.784 | 7.1285 | 0.22927 | 6.8988 | 8.6555 | 38.02 | 70.31 | -32.29 | TL of the station was handed over to PESCO,but PESCO does not execute repair and maintenance of the line whenever a fault occurs. High busbar voltage of PESCO grid is responsible for the high stator winding temperature and less generation.Annual Canal Closure for a period of forty days,and weekly supply weekly closure schedule from late October to March every year. | No remarks | 38.07 | 35.78 | 2.29 | -0.0013134 | -15.1004 | 15.0991 | -0.84929 | Efficient Plant: Revenue growth exceeds expenditure growth | 1.6 | Poor | 🔴 | Declining revenue or high expenditure with low profitability | Immediate management intervention required; perform financial and technical audit; reduce operational costs urgently; identify causes of low revenue; address outages and inefficiencies; consider restructuring or rehabilitation plan
Machai HPS | 2.6 | 2024-07-01 | 2025-06-30 | 2024-2025 | 15.784 | 3.5706 | 0.13803 | 3.4326 | 12.2134 | 18.91 | 50.37 | -31.46 | TL of the station was handed over to PESCO,but PESCO does not execute repair and maintenance of the line whenever a fault occurs. High busbar voltage of PESCO grid is responsible for the high stator winding temperature and less generation.Annual Canal Closure for a period of forty days,and weekly supply weekly closure schedule from late October to March every year. | No remarks | 38.02 | 70.31 | -32.29 | -0.50263 | -0.025705 | -0.47693 | -1.6637 | Cost Pressure: Expenditure growth is higher than revenue growth | 1.6 | Poor | 🔴 | Declining revenue or high expenditure with low profitability | Immediate management intervention required; perform financial and technical audit; reduce operational costs urgently; identify causes of low revenue; address outages and inefficiencies; consider restructuring or rehabilitation plan
Malakand-3 HPS | 81 | 2008-07-01 | 2009-06-30 | 2008-2009 | 549.909 | 307.611 | 0.757 | 306.854 | -242.298 | 1246.8201 | 98.8558 | 1147.9642 | Less power generation is due to less hydrology recieved. Arrival of bed load and suspended load sediments and trashes in river flow resulting in erosion of under water parts of turbines and chocking of trash racks and coolong water system. The data is till Feb-2025 | No remarks | [5 empty] | 0 | 0.92071 | Stable: Revenue and expenditure are growing at the same pace | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Malakand-3 HPS | 81 | 2009-07-01 | 2010-06-30 | 2009-2010 | 549.909 | 431.268 | 1.431 | 429.837 | -118.641 | 1831.5642 | 153.2781 | 1678.286 | Less power generation is due to less hydrology recieved. Arrival of bed load and suspended load sediments and trashes in river flow resulting in erosion of under water parts of turbines and chocking of trash racks and coolong water system. The data is till Feb-2025 | No remarks | 1246.8201 | 98.8558 | 1147.9642 | 0.46899 | 0.46197 | 0.0070212 | 0.91631 | Efficient Plant: Revenue growth exceeds expenditure growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Malakand-3 HPS | 81 | 2010-07-01 | 2011-06-30 | 2010-2011 | 549.909 | 292.935 | 1.289 | 291.646 | -256.974 | 3328.9661 | 274.9715 | 3053.9946 | Less power generation is due to less hydrology recieved. Arrival of bed load and suspended load sediments and trashes in river flow resulting in erosion of under water parts of turbines and chocking of trash racks and coolong water system. The data is till Feb-2025 | No remarks | 1831.5642 | 153.2781 | 1678.286 | 0.81755 | 0.81971 | -0.0021568 | 0.9174 | Cost Pressure: Expenditure growth is higher than revenue growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Malakand-3 HPS | 81 | 2011-07-01 | 2012-06-30 | 2011-2012 | 549.909 | 338.245 | 1.477 | 336.768 | -211.664 | 2368.954 | 326.6028 | 2042.3512 | Less power generation is due to less hydrology recieved. Arrival of bed load and suspended load sediments and trashes in river flow resulting in erosion of under water parts of turbines and chocking of trash racks and coolong water system. The data is till Feb-2025 | No remarks | 3328.9661 | 274.9715 | 3053.9946 | -0.28838 | -0.33125 | 0.042871 | 0.86213 | Efficient Plant: Revenue growth exceeds expenditure growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Malakand-3 HPS | 81 | 2012-07-01 | 2013-06-30 | 2012-2013 | 549.909 | 396.697 | 1.591 | 395.106 | -153.212 | 2558.9429 | 406.3185 | 2152.6245 | Less power generation is due to less hydrology recieved. Arrival of bed load and suspended load sediments and trashes in river flow resulting in erosion of under water parts of turbines and chocking of trash racks and coolong water system. The data is till Feb-2025 | No remarks | 2368.954 | 326.6028 | 2042.3512 | 0.0802 | 0.053993 | 0.026206 | 0.84122 | Efficient Plant: Revenue growth exceeds expenditure growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Malakand-3 HPS | 81 | 2013-07-01 | 2014-06-30 | 2013-2014 | 549.909 | 390.657 | 1.658 | 388.999 | -159.252 | 2382.0117 | 273.0379 | 2108.9738 | Less power generation is due to less hydrology recieved. Arrival of bed load and suspended load sediments and trashes in river flow resulting in erosion of under water parts of turbines and chocking of trash racks and coolong water system. The data is till Feb-2025 | No remarks | 2558.9429 | 406.3185 | 2152.6245 | -0.069142 | -0.020278 | -0.048864 | 0.88538 | Cost Pressure: Expenditure growth is higher than revenue growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Malakand-3 HPS | 81 | 2014-07-01 | 2015-06-30 | 2014-2015 | 549.909 | 358.02 | 1.483 | 356.537 | -191.889 | 2623.3393 | 235.1689 | 2388.1704 | Less power generation is due to less hydrology recieved. Arrival of bed load and suspended load sediments and trashes in river flow resulting in erosion of under water parts of turbines and chocking of trash racks and coolong water system. The data is till Feb-2025 | No remarks | 2382.0117 | 273.0379 | 2108.9738 | 0.10131 | 0.13239 | -0.031073 | 0.91036 | Cost Pressure: Expenditure growth is higher than revenue growth | 2.7 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Malakand-3 HPS | 81 | 2015-07-01 | 2016-06-30 | 2015-2016 | 549.909 | 440.799 | 1.881 | 438.918 | -109.11 | 2340.1747 | 262.7354 | 2077.4393 | Less power generation is due to less hydrology recieved. Arrival of bed load and suspended load sediments and trashes in river flow resulting in erosion of under water parts of turbines and chocking of trash racks and coolong water system. The data is till Feb-2025 | No remarks | 2623.3393 | 235.1689 | 2388.1704 | -0.10794 | -0.13011 | 0.022172 | 0.88773 | Efficient Plant: Revenue growth exceeds expenditure growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Malakand-3 HPS | 81 | 2016-07-01 | 2017-06-30 | 2016-2017 | 549.909 | 428.387 | 2.037 | 426.35 | -121.522 | 2302.2981 | 250.6826 | 2051.6155 | Less power generation is due to less hydrology recieved. Arrival of bed load and suspended load sediments and trashes in river flow resulting in erosion of under water parts of turbines and chocking of trash racks and coolong water system. The data is till Feb-2025 | No remarks | 2340.1747 | 262.7354 | 2077.4393 | -0.016185 | -0.012431 | -0.0037548 | 0.89112 | Cost Pressure: Expenditure growth is higher than revenue growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Malakand-3 HPS | 81 | 2017-07-01 | 2018-06-30 | 2017-2018 | 549.909 | 364.175 | 2.063 | 362.112 | -185.734 | 2660.2076 | 167.6764 | 2492.5312 | Less power generation is due to less hydrology recieved. Arrival of bed load and suspended load sediments and trashes in river flow resulting in erosion of under water parts of turbines and chocking of trash racks and coolong water system. The data is till Feb-2025 | No remarks | 2302.2981 | 250.6826 | 2051.6155 | 0.15546 | 0.21491 | -0.059454 | 0.93697 | Cost Pressure: Expenditure growth is higher than revenue growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Malakand-3 HPS | 81 | 2018-07-01 | 2019-06-30 | 2018-2019 | 549.909 | 401.28 | 2.03 | 399.25 | -148.629 | 1728.9795 | 249.5758 | 1479.4037 | Less power generation is due to less hydrology recieved. Arrival of bed load and suspended load sediments and trashes in river flow resulting in erosion of under water parts of turbines and chocking of trash racks and coolong water system. The data is till Feb-2025 | No remarks | 2660.2076 | 167.6764 | 2492.5312 | -0.35006 | -0.40647 | 0.056407 | 0.85565 | Efficient Plant: Revenue growth exceeds expenditure growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Malakand-3 HPS | 81 | 2019-07-01 | 2020-06-30 | 2019-2020 | 549.909 | 410.672 | 1.984 | 408.526 | -139.237 | 4221.8525 | 273.6079 | 3948.2446 | Less power generation is due to less hydrology recieved. Arrival of bed load and suspended load sediments and trashes in river flow resulting in erosion of under water parts of turbines and chocking of trash racks and coolong water system. The data is till Feb-2025 | No remarks | 1728.9795 | 249.5758 | 1479.4037 | 1.4418 | 1.6688 | -0.22699 | 0.93519 | Cost Pressure: Expenditure growth is higher than revenue growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Malakand-3 HPS | 81 | 2020-07-01 | 2021-06-30 | 2020-2021 | 549.909 | 323.63 | 2.063 | 321.562 | -226.279 | 1644.0164 | 309.9057 | 1334.1107 | Less power generation is due to less hydrology recieved. Arrival of bed load and suspended load sediments and trashes in river flow resulting in erosion of under water parts of turbines and chocking of trash racks and coolong water system. The data is till Feb-2025 | No remarks | 4221.8525 | 273.6079 | 3948.2446 | -0.61059 | -0.6621 | 0.051507 | 0.81149 | Efficient Plant: Revenue growth exceeds expenditure growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Malakand-3 HPS | 81 | 2021-07-01 | 2022-06-30 | 2021-2022 | 549.909 | 355.824 | 1.95 | 353.874 | -194.085 | 1528.4029 | 270.0639 | 1258.339 | Less power generation is due to less hydrology recieved. Arrival of bed load and suspended load sediments and trashes in river flow resulting in erosion of under water parts of turbines and chocking of trash racks and coolong water system. The data is till Feb-2025 | No remarks | 1644.0164 | 309.9057 | 1334.1107 | -0.070324 | -0.056796 | -0.013528 | 0.8233 | Cost Pressure: Expenditure growth is higher than revenue growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Malakand-3 HPS | 81 | 2022-07-01 | 2023-06-30 | 2022-2023 | 549.909 | 269.524 | 1.756 | 267.768 | -280.385 | 5919.1613 | 524.5988 | 5394.5625 | Less power generation is due to less hydrology recieved. Arrival of bed load and suspended load sediments and trashes in river flow resulting in erosion of under water parts of turbines and chocking of trash racks and coolong water system. The data is till Feb-2025 | No remarks | 1528.4029 | 270.0639 | 1258.339 | 2.8728 | 3.2871 | -0.41427 | 0.91137 | Cost Pressure: Expenditure growth is higher than revenue growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Malakand-3 HPS | 81 | 2023-07-01 | 2024-06-30 | 2023-2024 | 549.909 | 223.256 | 1.677 | 221.59 | -326.653 | 5185.6961 | 918.0763 | 4267.6198 | Less power generation is due to less hydrology recieved. Arrival of bed load and suspended load sediments and trashes in river flow resulting in erosion of under water parts of turbines and chocking of trash racks and coolong water system. The data is till Feb-2025 | No remarks | 5919.1613 | 524.5988 | 5394.5625 | -0.12391 | -0.2089 | 0.08499 | 0.82296 | Efficient Plant: Revenue growth exceeds expenditure growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Malakand-3 HPS | 81 | 2024-07-01 | 2025-06-30 | 2024-2025 | 549.909 | 105.446 | 0.788 | 104.658 | -444.463 | 2027.7391 | 165.4728 | 1862.2663 | Less power generation is due to less hydrology recieved. Arrival of bed load and suspended load sediments and trashes in river flow resulting in erosion of under water parts of turbines and chocking of trash racks and coolong water system. The data is till Feb-2025 | No remarks | 5185.6961 | 918.0763 | 4267.6198 | -0.60897 | -0.56363 | -0.045346 | 0.9184 | Cost Pressure: Expenditure growth is higher than revenue growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Pehur HPS | 18 | 2010-07-01 | 2011-06-30 | 2010-2011 | 57.7 | 40.3965 | 1.7239 | 38.6726 | 1969.6035 | 42.3 | 37 | 5.3 | Pehur Hydropower Complex is constructed at the out let of Gandaf Tunnel emanating from Tarbela Reservoir to feed the Pehur High level canal PHLC located in District Swabi. Pehur HPC is completely dependent on Irrigation PHLC canal therefore, during canal closures, the plant generation is nil. Also, it varies with the variation in the available hydrology of Tarbela reservoir. Generally the head for unit # 1 & 2 i.e. (44 m & above) is available in the month of July each year & the head increases to its maximum day by day up to mid-August. The maximum head range 44 to 85 meter for unit 1 & 2 is available up to end of December. During these months though the head for both units 1 & 2 head is available but the plant cannot be operated to its full capability because of water flow constraints in the canal. During the month of July / August the plant operation is affected due to heavy raining and flood & the plant is often operated at low loads. From September onward to December the irrigation demand increases but capability of units drop due to reduction in head. In November / December the plant operation is affected because of water flow restriction in the canal & as such generation is affected. In January each year the plant is shut down for canal closer. The canal closure period is always extended sometimes for more than a month & the plant remains shutdown during this period. In February generally the head starts decreasing & the low head machine unit # 3 is taken on bar. Due to increase in irrigation demand from March/April onward the head further decreases and accordingly the capability of unit # 3 decreases. The irrigation valves are also operated to meet the irrigation demand which further affect the capability of unit # 3 & the generation is affected. | No remarks | [5 empty] | 0 | 0.1253 | Stable: Revenue and expenditure are growing at the same pace | 2 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Pehur HPS | 18 | 2011-07-01 | 2012-06-30 | 2011-2012 | 57.7 | 47.5688 | 1.7628 | 45.806 | 1963.4312 | 167.71 | 78.61 | 89.1 | Pehur Hydropower Complex is constructed at the out let of Gandaf Tunnel emanating from Tarbela Reservoir to feed the Pehur High level canal PHLC located in District Swabi. Pehur HPC is completely dependent on Irrigation PHLC canal therefore, during canal closures, the plant generation is nil. Also, it varies with the variation in the available hydrology of Tarbela reservoir. Generally the head for unit # 1 & 2 i.e. (44 m & above) is available in the month of July each year & the head increases to its maximum day by day up to mid-August. The maximum head range 44 to 85 meter for unit 1 & 2 is available up to end of December. During these months though the head for both units 1 & 2 head is available but the plant cannot be operated to its full capability because of water flow constraints in the canal. During the month of July / August the plant operation is affected due to heavy raining and flood & the plant is often operated at low loads. From September onward to December the irrigation demand increases but capability of units drop due to reduction in head. In November / December the plant operation is affected because of water flow restriction in the canal & as such generation is affected. In January each year the plant is shut down for canal closer. The canal closure period is always extended sometimes for more than a month & the plant remains shutdown during this period. In February generally the head starts decreasing & the low head machine unit # 3 is taken on bar. Due to increase in irrigation demand from March/April onward the head further decreases and accordingly the capability of unit # 3 decreases. The irrigation valves are also operated to meet the irrigation demand which further affect the capability of unit # 3 & the generation is affected. | No remarks | 42.3 | 37 | 5.3 | 2.9648 | 15.8113 | -12.8465 | 0.53127 | Cost Pressure: Expenditure growth is higher than revenue growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Pehur HPS | 18 | 2012-07-01 | 2013-06-30 | 2012-2013 | 57.7 | 44.0955 | 2.0579 | 42.0376 | 1967.9045 | 170.52 | 67.22 | 103.3 | Pehur Hydropower Complex is constructed at the out let of Gandaf Tunnel emanating from Tarbela Reservoir to feed the Pehur High level canal PHLC located in District Swabi. Pehur HPC is completely dependent on Irrigation PHLC canal therefore, during canal closures, the plant generation is nil. Also, it varies with the variation in the available hydrology of Tarbela reservoir. Generally the head for unit # 1 & 2 i.e. (44 m & above) is available in the month of July each year & the head increases to its maximum day by day up to mid-August. The maximum head range 44 to 85 meter for unit 1 & 2 is available up to end of December. During these months though the head for both units 1 & 2 head is available but the plant cannot be operated to its full capability because of water flow constraints in the canal. During the month of July / August the plant operation is affected due to heavy raining and flood & the plant is often operated at low loads. From September onward to December the irrigation demand increases but capability of units drop due to reduction in head. In November / December the plant operation is affected because of water flow restriction in the canal & as such generation is affected. In January each year the plant is shut down for canal closer. The canal closure period is always extended sometimes for more than a month & the plant remains shutdown during this period. In February generally the head starts decreasing & the low head machine unit # 3 is taken on bar. Due to increase in irrigation demand from March/April onward the head further decreases and accordingly the capability of unit # 3 decreases. The irrigation valves are also operated to meet the irrigation demand which further affect the capability of unit # 3 & the generation is affected. | No remarks | 167.71 | 78.61 | 89.1 | 0.016755 | 0.15937 | -0.14262 | 0.60579 | Cost Pressure: Expenditure growth is higher than revenue growth | 2.1 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Pehur HPS | 18 | 2013-07-01 | 2014-06-30 | 2013-2014 | 57.7 | 53.6149 | 2.4683 | 51.1466 | 4.0851 | 182.26 | 72.53 | 109.73 | Pehur Hydropower Complex is constructed at the out let of Gandaf Tunnel emanating from Tarbela Reservoir to feed the Pehur High level canal PHLC located in District Swabi. Pehur HPC is completely dependent on Irrigation PHLC canal therefore, during canal closures, the plant generation is nil. Also, it varies with the variation in the available hydrology of Tarbela reservoir. Generally the head for unit # 1 & 2 i.e. (44 m & above) is available in the month of July each year & the head increases to its maximum day by day up to mid-August. The maximum head range 44 to 85 meter for unit 1 & 2 is available up to end of December. During these months though the head for both units 1 & 2 head is available but the plant cannot be operated to its full capability because of water flow constraints in the canal. During the month of July / August the plant operation is affected due to heavy raining and flood & the plant is often operated at low loads. From September onward to December the irrigation demand increases but capability of units drop due to reduction in head. In November / December the plant operation is affected because of water flow restriction in the canal & as such generation is affected. In January each year the plant is shut down for canal closer. The canal closure period is always extended sometimes for more than a month & the plant remains shutdown during this period. In February generally the head starts decreasing & the low head machine unit # 3 is taken on bar. Due to increase in irrigation demand from March/April onward the head further decreases and accordingly the capability of unit # 3 decreases. The irrigation valves are also operated to meet the irrigation demand which further affect the capability of unit # 3 & the generation is affected. | No remarks | 170.52 | 67.22 | 103.3 | 0.068848 | 0.062246 | 0.0066023 | 0.60205 | Efficient Plant: Revenue growth exceeds expenditure growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Pehur HPS | 18 | 2014-07-01 | 2015-06-30 | 2014-2015 | 57.7 | 49.2615 | 2.5944 | 46.6679 | 8.4385 | 205.89 | 62.78 | 143.11 | Pehur Hydropower Complex is constructed at the out let of Gandaf Tunnel emanating from Tarbela Reservoir to feed the Pehur High level canal PHLC located in District Swabi. Pehur HPC is completely dependent on Irrigation PHLC canal therefore, during canal closures, the plant generation is nil. Also, it varies with the variation in the available hydrology of Tarbela reservoir. Generally the head for unit # 1 & 2 i.e. (44 m & above) is available in the month of July each year & the head increases to its maximum day by day up to mid-August. The maximum head range 44 to 85 meter for unit 1 & 2 is available up to end of December. During these months though the head for both units 1 & 2 head is available but the plant cannot be operated to its full capability because of water flow constraints in the canal. During the month of July / August the plant operation is affected due to heavy raining and flood & the plant is often operated at low loads. From September onward to December the irrigation demand increases but capability of units drop due to reduction in head. In November / December the plant operation is affected because of water flow restriction in the canal & as such generation is affected. In January each year the plant is shut down for canal closer. The canal closure period is always extended sometimes for more than a month & the plant remains shutdown during this period. In February generally the head starts decreasing & the low head machine unit # 3 is taken on bar. Due to increase in irrigation demand from March/April onward the head further decreases and accordingly the capability of unit # 3 decreases. The irrigation valves are also operated to meet the irrigation demand which further affect the capability of unit # 3 & the generation is affected. | No remarks | 182.26 | 72.53 | 109.73 | 0.12965 | 0.3042 | -0.17455 | 0.69508 | Cost Pressure: Expenditure growth is higher than revenue growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Pehur HPS | 18 | 2015-07-01 | 2016-06-30 | 2015-2016 | 57.7 | 46.3144 | 2.6511 | 43.6633 | 11.3856 | 198.53 | 72.71 | 125.82 | Pehur Hydropower Complex is constructed at the out let of Gandaf Tunnel emanating from Tarbela Reservoir to feed the Pehur High level canal PHLC located in District Swabi. Pehur HPC is completely dependent on Irrigation PHLC canal therefore, during canal closures, the plant generation is nil. Also, it varies with the variation in the available hydrology of Tarbela reservoir. Generally the head for unit # 1 & 2 i.e. (44 m & above) is available in the month of July each year & the head increases to its maximum day by day up to mid-August. The maximum head range 44 to 85 meter for unit 1 & 2 is available up to end of December. During these months though the head for both units 1 & 2 head is available but the plant cannot be operated to its full capability because of water flow constraints in the canal. During the month of July / August the plant operation is affected due to heavy raining and flood & the plant is often operated at low loads. From September onward to December the irrigation demand increases but capability of units drop due to reduction in head. In November / December the plant operation is affected because of water flow restriction in the canal & as such generation is affected. In January each year the plant is shut down for canal closer. The canal closure period is always extended sometimes for more than a month & the plant remains shutdown during this period. In February generally the head starts decreasing & the low head machine unit # 3 is taken on bar. Due to increase in irrigation demand from March/April onward the head further decreases and accordingly the capability of unit # 3 decreases. The irrigation valves are also operated to meet the irrigation demand which further affect the capability of unit # 3 & the generation is affected. | No remarks | 205.89 | 62.78 | 143.11 | -0.035747 | -0.12082 | 0.085069 | 0.63376 | Efficient Plant: Revenue growth exceeds expenditure growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Pehur HPS | 18 | 2016-07-01 | 2017-06-30 | 2016-2017 | 57.7 | 48.3879 | 3.0265 | 45.3614 | 9.3121 | 162.32 | 69.35 | 92.97 | Pehur Hydropower Complex is constructed at the out let of Gandaf Tunnel emanating from Tarbela Reservoir to feed the Pehur High level canal PHLC located in District Swabi. Pehur HPC is completely dependent on Irrigation PHLC canal therefore, during canal closures, the plant generation is nil. Also, it varies with the variation in the available hydrology of Tarbela reservoir. Generally the head for unit # 1 & 2 i.e. (44 m & above) is available in the month of July each year & the head increases to its maximum day by day up to mid-August. The maximum head range 44 to 85 meter for unit 1 & 2 is available up to end of December. During these months though the head for both units 1 & 2 head is available but the plant cannot be operated to its full capability because of water flow constraints in the canal. During the month of July / August the plant operation is affected due to heavy raining and flood & the plant is often operated at low loads. From September onward to December the irrigation demand increases but capability of units drop due to reduction in head. In November / December the plant operation is affected because of water flow restriction in the canal & as such generation is affected. In January each year the plant is shut down for canal closer. The canal closure period is always extended sometimes for more than a month & the plant remains shutdown during this period. In February generally the head starts decreasing & the low head machine unit # 3 is taken on bar. Due to increase in irrigation demand from March/April onward the head further decreases and accordingly the capability of unit # 3 decreases. The irrigation valves are also operated to meet the irrigation demand which further affect the capability of unit # 3 & the generation is affected. | No remarks | 198.53 | 72.71 | 125.82 | -0.18239 | -0.26109 | 0.078697 | 0.57276 | Efficient Plant: Revenue growth exceeds expenditure growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Pehur HPS | 18 | 2017-07-01 | 2018-06-30 | 2017-2018 | 57.7 | 37.5331 | 3.17 | 34.3631 | 20.1669 | 181.84 | 57.61 | 124.23 | Pehur Hydropower Complex is constructed at the out let of Gandaf Tunnel emanating from Tarbela Reservoir to feed the Pehur High level canal PHLC located in District Swabi. Pehur HPC is completely dependent on Irrigation PHLC canal therefore, during canal closures, the plant generation is nil. Also, it varies with the variation in the available hydrology of Tarbela reservoir. Generally the head for unit # 1 & 2 i.e. (44 m & above) is available in the month of July each year & the head increases to its maximum day by day up to mid-August. The maximum head range 44 to 85 meter for unit 1 & 2 is available up to end of December. During these months though the head for both units 1 & 2 head is available but the plant cannot be operated to its full capability because of water flow constraints in the canal. During the month of July / August the plant operation is affected due to heavy raining and flood & the plant is often operated at low loads. From September onward to December the irrigation demand increases but capability of units drop due to reduction in head. In November / December the plant operation is affected because of water flow restriction in the canal & as such generation is affected. In January each year the plant is shut down for canal closer. The canal closure period is always extended sometimes for more than a month & the plant remains shutdown during this period. In February generally the head starts decreasing & the low head machine unit # 3 is taken on bar. Due to increase in irrigation demand from March/April onward the head further decreases and accordingly the capability of unit # 3 decreases. The irrigation valves are also operated to meet the irrigation demand which further affect the capability of unit # 3 & the generation is affected. | No remarks | 162.32 | 69.35 | 92.97 | 0.12026 | 0.33624 | -0.21598 | 0.68318 | Cost Pressure: Expenditure growth is higher than revenue growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Pehur HPS | 18 | 2018-07-01 | 2019-06-30 | 2018-2019 | 57.7 | 38.5101 | 3.6927 | 34.8174 | 19.1899 | 134.14 | 82.09 | 52.05 | Pehur Hydropower Complex is constructed at the out let of Gandaf Tunnel emanating from Tarbela Reservoir to feed the Pehur High level canal PHLC located in District Swabi. Pehur HPC is completely dependent on Irrigation PHLC canal therefore, during canal closures, the plant generation is nil. Also, it varies with the variation in the available hydrology of Tarbela reservoir. Generally the head for unit # 1 & 2 i.e. (44 m & above) is available in the month of July each year & the head increases to its maximum day by day up to mid-August. The maximum head range 44 to 85 meter for unit 1 & 2 is available up to end of December. During these months though the head for both units 1 & 2 head is available but the plant cannot be operated to its full capability because of water flow constraints in the canal. During the month of July / August the plant operation is affected due to heavy raining and flood & the plant is often operated at low loads. From September onward to December the irrigation demand increases but capability of units drop due to reduction in head. In November / December the plant operation is affected because of water flow restriction in the canal & as such generation is affected. In January each year the plant is shut down for canal closer. The canal closure period is always extended sometimes for more than a month & the plant remains shutdown during this period. In February generally the head starts decreasing & the low head machine unit # 3 is taken on bar. Due to increase in irrigation demand from March/April onward the head further decreases and accordingly the capability of unit # 3 decreases. The irrigation valves are also operated to meet the irrigation demand which further affect the capability of unit # 3 & the generation is affected. | No remarks | 181.84 | 57.61 | 124.23 | -0.26232 | -0.58102 | 0.3187 | 0.38803 | Efficient Plant: Revenue growth exceeds expenditure growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Pehur HPS | 18 | 2019-07-01 | 2020-06-30 | 2019-2020 | 57.7 | 47.8957 | 1.6647 | 46.231 | 9.8043 | 150.3 | 72.84 | 77.46 | Pehur Hydropower Complex is constructed at the out let of Gandaf Tunnel emanating from Tarbela Reservoir to feed the Pehur High level canal PHLC located in District Swabi. Pehur HPC is completely dependent on Irrigation PHLC canal therefore, during canal closures, the plant generation is nil. Also, it varies with the variation in the available hydrology of Tarbela reservoir. Generally the head for unit # 1 & 2 i.e. (44 m & above) is available in the month of July each year & the head increases to its maximum day by day up to mid-August. The maximum head range 44 to 85 meter for unit 1 & 2 is available up to end of December. During these months though the head for both units 1 & 2 head is available but the plant cannot be operated to its full capability because of water flow constraints in the canal. During the month of July / August the plant operation is affected due to heavy raining and flood & the plant is often operated at low loads. From September onward to December the irrigation demand increases but capability of units drop due to reduction in head. In November / December the plant operation is affected because of water flow restriction in the canal & as such generation is affected. In January each year the plant is shut down for canal closer. The canal closure period is always extended sometimes for more than a month & the plant remains shutdown during this period. In February generally the head starts decreasing & the low head machine unit # 3 is taken on bar. Due to increase in irrigation demand from March/April onward the head further decreases and accordingly the capability of unit # 3 decreases. The irrigation valves are also operated to meet the irrigation demand which further affect the capability of unit # 3 & the generation is affected. | No remarks | 134.14 | 82.09 | 52.05 | 0.12047 | 0.48818 | -0.36771 | 0.51537 | Cost Pressure: Expenditure growth is higher than revenue growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Pehur HPS | 18 | 2020-07-01 | 2021-06-30 | 2020-2021 | 57.7 | 50.5815 | 1.4795 | 49.102 | 7.1185 | 210.75 | 64.67 | 146.08 | Pehur Hydropower Complex is constructed at the out let of Gandaf Tunnel emanating from Tarbela Reservoir to feed the Pehur High level canal PHLC located in District Swabi. Pehur HPC is completely dependent on Irrigation PHLC canal therefore, during canal closures, the plant generation is nil. Also, it varies with the variation in the available hydrology of Tarbela reservoir. Generally the head for unit # 1 & 2 i.e. (44 m & above) is available in the month of July each year & the head increases to its maximum day by day up to mid-August. The maximum head range 44 to 85 meter for unit 1 & 2 is available up to end of December. During these months though the head for both units 1 & 2 head is available but the plant cannot be operated to its full capability because of water flow constraints in the canal. During the month of July / August the plant operation is affected due to heavy raining and flood & the plant is often operated at low loads. From September onward to December the irrigation demand increases but capability of units drop due to reduction in head. In November / December the plant operation is affected because of water flow restriction in the canal & as such generation is affected. In January each year the plant is shut down for canal closer. The canal closure period is always extended sometimes for more than a month & the plant remains shutdown during this period. In February generally the head starts decreasing & the low head machine unit # 3 is taken on bar. Due to increase in irrigation demand from March/April onward the head further decreases and accordingly the capability of unit # 3 decreases. The irrigation valves are also operated to meet the irrigation demand which further affect the capability of unit # 3 & the generation is affected. | No remarks | 150.3 | 72.84 | 77.46 | 0.4022 | 0.88588 | -0.48368 | 0.69314 | Cost Pressure: Expenditure growth is higher than revenue growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Pehur HPS | 18 | 2021-07-01 | 2022-06-30 | 2021-2022 | 57.7 | 55.2535 | 1.4106 | 53.842 | 2.4465 | 448.44 | 88.57 | 359.87 | Pehur Hydropower Complex is constructed at the out let of Gandaf Tunnel emanating from Tarbela Reservoir to feed the Pehur High level canal PHLC located in District Swabi. Pehur HPC is completely dependent on Irrigation PHLC canal therefore, during canal closures, the plant generation is nil. Also, it varies with the variation in the available hydrology of Tarbela reservoir. Generally the head for unit # 1 & 2 i.e. (44 m & above) is available in the month of July each year & the head increases to its maximum day by day up to mid-August. The maximum head range 44 to 85 meter for unit 1 & 2 is available up to end of December. During these months though the head for both units 1 & 2 head is available but the plant cannot be operated to its full capability because of water flow constraints in the canal. During the month of July / August the plant operation is affected due to heavy raining and flood & the plant is often operated at low loads. From September onward to December the irrigation demand increases but capability of units drop due to reduction in head. In November / December the plant operation is affected because of water flow restriction in the canal & as such generation is affected. In January each year the plant is shut down for canal closer. The canal closure period is always extended sometimes for more than a month & the plant remains shutdown during this period. In February generally the head starts decreasing & the low head machine unit # 3 is taken on bar. Due to increase in irrigation demand from March/April onward the head further decreases and accordingly the capability of unit # 3 decreases. The irrigation valves are also operated to meet the irrigation demand which further affect the capability of unit # 3 & the generation is affected. | No remarks | 210.75 | 64.67 | 146.08 | 1.1278 | 1.4635 | -0.33568 | 0.80249 | Cost Pressure: Expenditure growth is higher than revenue growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Pehur HPS | 18 | 2022-07-01 | 2023-06-30 | 2022-2023 | 57.7 | 43.471 | 1.2521 | 42.22 | 14.229 | 418.7 | 77.9 | 340.8 | Pehur Hydropower Complex is constructed at the out let of Gandaf Tunnel emanating from Tarbela Reservoir to feed the Pehur High level canal PHLC located in District Swabi. Pehur HPC is completely dependent on Irrigation PHLC canal therefore, during canal closures, the plant generation is nil. Also, it varies with the variation in the available hydrology of Tarbela reservoir. Generally the head for unit # 1 & 2 i.e. (44 m & above) is available in the month of July each year & the head increases to its maximum day by day up to mid-August. The maximum head range 44 to 85 meter for unit 1 & 2 is available up to end of December. During these months though the head for both units 1 & 2 head is available but the plant cannot be operated to its full capability because of water flow constraints in the canal. During the month of July / August the plant operation is affected due to heavy raining and flood & the plant is often operated at low loads. From September onward to December the irrigation demand increases but capability of units drop due to reduction in head. In November / December the plant operation is affected because of water flow restriction in the canal & as such generation is affected. In January each year the plant is shut down for canal closer. The canal closure period is always extended sometimes for more than a month & the plant remains shutdown during this period. In February generally the head starts decreasing & the low head machine unit # 3 is taken on bar. Due to increase in irrigation demand from March/April onward the head further decreases and accordingly the capability of unit # 3 decreases. The irrigation valves are also operated to meet the irrigation demand which further affect the capability of unit # 3 & the generation is affected. | No remarks | 448.44 | 88.57 | 359.87 | -0.066319 | -0.052991 | -0.013327 | 0.81395 | Cost Pressure: Expenditure growth is higher than revenue growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Pehur HPS | 18 | 2023-07-01 | 2024-06-30 | 2023-2024 | 57.7 | 56.5708 | 1.5628 | 55.008 | 1.1292 | 484 | 111.98 | 372.02 | Pehur Hydropower Complex is constructed at the out let of Gandaf Tunnel emanating from Tarbela Reservoir to feed the Pehur High level canal PHLC located in District Swabi. Pehur HPC is completely dependent on Irrigation PHLC canal therefore, during canal closures, the plant generation is nil. Also, it varies with the variation in the available hydrology of Tarbela reservoir. Generally the head for unit # 1 & 2 i.e. (44 m & above) is available in the month of July each year & the head increases to its maximum day by day up to mid-August. The maximum head range 44 to 85 meter for unit 1 & 2 is available up to end of December. During these months though the head for both units 1 & 2 head is available but the plant cannot be operated to its full capability because of water flow constraints in the canal. During the month of July / August the plant operation is affected due to heavy raining and flood & the plant is often operated at low loads. From September onward to December the irrigation demand increases but capability of units drop due to reduction in head. In November / December the plant operation is affected because of water flow restriction in the canal & as such generation is affected. In January each year the plant is shut down for canal closer. The canal closure period is always extended sometimes for more than a month & the plant remains shutdown during this period. In February generally the head starts decreasing & the low head machine unit # 3 is taken on bar. Due to increase in irrigation demand from March/April onward the head further decreases and accordingly the capability of unit # 3 decreases. The irrigation valves are also operated to meet the irrigation demand which further affect the capability of unit # 3 & the generation is affected. | No remarks | 418.7 | 77.9 | 340.8 | 0.15596 | 0.091608 | 0.064351 | 0.76864 | Efficient Plant: Revenue growth exceeds expenditure growth | 2.7 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Pehur HPS | 18 | 2024-07-01 | 2025-06-30 | 2024-2025 | 57.7 | 47.2701 | 1.6756 | 45.682 | 10.4299 | 643.71 | 159.2 | 484.51 | Pehur Hydropower Complex is constructed at the out let of Gandaf Tunnel emanating from Tarbela Reservoir to feed the Pehur High level canal PHLC located in District Swabi. Pehur HPC is completely dependent on Irrigation PHLC canal therefore, during canal closures, the plant generation is nil. Also, it varies with the variation in the available hydrology of Tarbela reservoir. Generally the head for unit # 1 & 2 i.e. (44 m & above) is available in the month of July each year & the head increases to its maximum day by day up to mid-August. The maximum head range 44 to 85 meter for unit 1 & 2 is available up to end of December. During these months though the head for both units 1 & 2 head is available but the plant cannot be operated to its full capability because of water flow constraints in the canal. During the month of July / August the plant operation is affected due to heavy raining and flood & the plant is often operated at low loads. From September onward to December the irrigation demand increases but capability of units drop due to reduction in head. In November / December the plant operation is affected because of water flow restriction in the canal & as such generation is affected. In January each year the plant is shut down for canal closer. The canal closure period is always extended sometimes for more than a month & the plant remains shutdown during this period. In February generally the head starts decreasing & the low head machine unit # 3 is taken on bar. Due to increase in irrigation demand from March/April onward the head further decreases and accordingly the capability of unit # 3 decreases. The irrigation valves are also operated to meet the irrigation demand which further affect the capability of unit # 3 & the generation is affected. | No remarks | 484 | 111.98 | 372.02 | 0.32998 | 0.30238 | 0.027603 | 0.75268 | Efficient Plant: Revenue growth exceeds expenditure growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Ranolia HPS | 10.2 | 2014-07-01 | 2015-06-30 | 2014-2015 | 100.5 | 0 | 0 | 0 | 100.5 | 0 | 38.553 | -38.553 | Project in Non Operational since 26 August 2022. After the 2022 flood, Ranolia HPC suffered extensive damage and required significant rehabilitation. Since the PC-1 had not been approved at the time, all essential rehabilitation work was carried out using the O&M budget. | Post COD Tariff @ Rs.4.1245 COD: 12-09-2021 | [5 empty] | 0 |  | Stable: Revenue and expenditure are growing at the same pace |  | Not available (insufficient data) | Not available (insufficient data) | Not available (insufficient data) | Not available (insufficient data)
Ranolia HPS | 10.2 | 2015-07-01 | 2016-06-30 | 2015-2016 | 100.5 | 0 | 0 | 0 | 100.5 | 0 | 22.1157 | -22.1157 | Project in Non Operational since 26 August 2022. After the 2022 flood, Ranolia HPC suffered extensive damage and required significant rehabilitation. Since the PC-1 had not been approved at the time, all essential rehabilitation work was carried out using the O&M budget. | Post COD Tariff @ Rs.4.1245 COD: 12-09-2021 | 0 | 38.553 | -38.553 |  | -0.42636 | 0.42636 |  | Efficient Plant: Revenue growth exceeds expenditure growth |  | Not available (insufficient data) | Not available (insufficient data) | Not available (insufficient data) | Not available (insufficient data)
Ranolia HPS | 10.2 | 2016-07-01 | 2017-06-30 | 2016-2017 | 100.5 | 0 | 0 | 0 | 100.5 | 0 | 48.807 | -48.807 | Project in Non Operational since 26 August 2022. After the 2022 flood, Ranolia HPC suffered extensive damage and required significant rehabilitation. Since the PC-1 had not been approved at the time, all essential rehabilitation work was carried out using the O&M budget. | Post COD Tariff @ Rs.4.1245 COD: 12-09-2021 | 0 | 22.1157 | -22.1157 |  | 1.2069 | -1.2069 |  | Cost Pressure: Expenditure growth is higher than revenue growth |  | Not available (insufficient data) | Not available (insufficient data) | Not available (insufficient data) | Not available (insufficient data)
Ranolia HPS | 10.2 | 2017-07-01 | 2018-06-30 | 2017-2018 | 100.5 | 0 | 0 | 0 | 100.5 | 0 | 32.6078 | -32.6078 | Project in Non Operational since 26 August 2022. After the 2022 flood, Ranolia HPC suffered extensive damage and required significant rehabilitation. Since the PC-1 had not been approved at the time, all essential rehabilitation work was carried out using the O&M budget. | Post COD Tariff @ Rs.4.1245 COD: 12-09-2021 | 0 | 48.807 | -48.807 |  | -0.3319 | 0.3319 |  | Efficient Plant: Revenue growth exceeds expenditure growth |  | Not available (insufficient data) | Not available (insufficient data) | Not available (insufficient data) | Not available (insufficient data)
Ranolia HPS | 10.2 | 2018-07-01 | 2019-06-30 | 2018-2019 | 100.5 | 0 | 0 | 0 | 100.5 | 0 | 23.4 | -23.4 | Project in Non Operational since 26 August 2022. After the 2022 flood, Ranolia HPC suffered extensive damage and required significant rehabilitation. Since the PC-1 had not been approved at the time, all essential rehabilitation work was carried out using the O&M budget. | Post COD Tariff @ Rs.4.1245 COD: 12-09-2021 | 0 | 32.6078 | -32.6078 |  | -0.28238 | 0.28238 |  | Efficient Plant: Revenue growth exceeds expenditure growth |  | Not available (insufficient data) | Not available (insufficient data) | Not available (insufficient data) | Not available (insufficient data)
Ranolia HPS | 10.2 | 2019-07-01 | 2020-06-30 | 2019-2020 | 100.5 | 11.4572 | 0.055074 | 11.4 | 89.0428 | 0 | 36.1102 | -36.1102 | Project in Non Operational since 26 August 2022. After the 2022 flood, Ranolia HPC suffered extensive damage and required significant rehabilitation. Since the PC-1 had not been approved at the time, all essential rehabilitation work was carried out using the O&M budget. | Post COD Tariff @ Rs.4.1245 COD: 12-09-2021 | 0 | 23.4 | -23.4 |  | 0.54317 | -0.54317 |  | Cost Pressure: Expenditure growth is higher than revenue growth |  | Not available (insufficient data) | Not available (insufficient data) | Not available (insufficient data) | Not available (insufficient data)
Ranolia HPS | 10.2 | 2020-07-01 | 2021-06-30 | 2020-2021 | 100.5 | 35.1901 | 0.16398 | 35.03 | 65.3099 | 0 | 42.3489 | -42.3489 | Project in Non Operational since 26 August 2022. After the 2022 flood, Ranolia HPC suffered extensive damage and required significant rehabilitation. Since the PC-1 had not been approved at the time, all essential rehabilitation work was carried out using the O&M budget. | Post COD Tariff @ Rs.4.1245 COD: 12-09-2021 | 0 | 36.1102 | -36.1102 |  | 0.17277 | -0.17277 |  | Cost Pressure: Expenditure growth is higher than revenue growth |  | Not available (insufficient data) | Not available (insufficient data) | Not available (insufficient data) | Not available (insufficient data)
Ranolia HPS | 10.2 | 2021-07-01 | 2022-06-30 | 2021-2022 | 100.5 | 32.8746 | 0.19576 | 32.68 | 67.6254 | 71.8477 | 98.3232 | -26.4755 | Project in Non Operational since 26 August 2022. After the 2022 flood, Ranolia HPC suffered extensive damage and required significant rehabilitation. Since the PC-1 had not been approved at the time, all essential rehabilitation work was carried out using the O&M budget. | Post COD Tariff @ Rs.4.1245 COD: 12-09-2021 | 0 | 42.3489 | -42.3489 |  | -0.37482 | 0.37482 | -0.3685 | Efficient Plant: Revenue growth exceeds expenditure growth | 2.2 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Ranolia HPS | 10.2 | 2022-07-01 | 2023-06-30 | 2022-2023 | 100.5 | 30.2423 | 0.019561 | 30.22 | 70.2577 | 27.6873 | 47.3891 | -19.7018 | Project in Non Operational since 26 August 2022. After the 2022 flood, Ranolia HPC suffered extensive damage and required significant rehabilitation. Since the PC-1 had not been approved at the time, all essential rehabilitation work was carried out using the O&M budget. | Post COD Tariff @ Rs.4.1245 COD: 12-09-2021 | 71.8477 | 98.3232 | -26.4755 | -0.61464 | -0.25585 | -0.35879 | -0.71158 | Cost Pressure: Expenditure growth is higher than revenue growth | 1.6 | Poor | 🔴 | Declining revenue or high expenditure with low profitability | Immediate management intervention required; perform financial and technical audit; reduce operational costs urgently; identify causes of low revenue; address outages and inefficiencies; consider restructuring or rehabilitation plan
Ranolia HPS | 10.2 | 2023-07-01 | 2024-06-30 | 2023-2024 | 100.5 | 0 | 0 | 0 | 100.5 | 0 | 108.8427 | -108.8427 | Project in Non Operational since 26 August 2022. After the 2022 flood, Ranolia HPC suffered extensive damage and required significant rehabilitation. Since the PC-1 had not been approved at the time, all essential rehabilitation work was carried out using the O&M budget. | Post COD Tariff @ Rs.4.1245 COD: 12-09-2021 | 27.6873 | 47.3891 | -19.7018 | -1 | 4.5245 | -5.5245 |  | Cost Pressure: Expenditure growth is higher than revenue growth |  | Not available (insufficient data) | Not available (insufficient data) | Not available (insufficient data) | Not available (insufficient data)
Reshun HPS | 4.2 | 2008-07-01 | 2009-06-30 | 2008-2009 | 25 | 10 | 0.02 | 9.98 | 15 | 25 | 19.95 | 5.05 | The Reshun Hydropower Plant (HPP), operational since 1999, has been providing electricity to over 19,000 off-grid consumers. However, due to a sustained overload demand exceeding its installed capacity of 4.2 MW, systemic load shedding became inevitable, necessitating compensatory measures. During the Prime Minister’s inauguration of the Golen Gol HPP, the PESCO electricity supply was integrated into the Reshun HPP Transmission Line via the Jutilusht Grid. This unplanned interconnection compelled Reshun HPP consumers to bear unanticipated operational expenditures, as the existing infrastructure was not designed to accommodate external grid injection. Furthermore, the plant’s operational viability was severely compromised by catastrophic flooding in 2015, resulting in a complete generation halt until its rehabilitation. This six-year operational disruption caused significant generation deficits and cumulative revenue losses, exacerbating financial strain on both the facility and its consumer base. Flash floods and Glacial Lake Outburst Floods (GLOF) in 2024 and specifically July-August 2024 floods have resulted in damages to the protection wall and allied civil structures of the power plant thereby resulted in the generation loss in shape of time-to-time shutdown of one or two units out of total three units. Also, in the aftermaths of these floods comparatively less hydrology has been recorded which did not allow electricity generation as per its installed capacity. After the diversion of pipeline from Shakagol to reservoir and rehabilitation of RCC Protection/retaining wall of the power plant, the forecasted energy target can be achieved. | No remarks | [5 empty] | 0 | 0.202 | Stable: Revenue and expenditure are growing at the same pace | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Reshun HPS | 4.2 | 2009-07-01 | 2010-06-30 | 2009-2010 | 25 | 11.76 | 0.024 | 11.736 | 13.24 | 32 | 7.59 | 24.41 | The Reshun Hydropower Plant (HPP), operational since 1999, has been providing electricity to over 19,000 off-grid consumers. However, due to a sustained overload demand exceeding its installed capacity of 4.2 MW, systemic load shedding became inevitable, necessitating compensatory measures. During the Prime Minister’s inauguration of the Golen Gol HPP, the PESCO electricity supply was integrated into the Reshun HPP Transmission Line via the Jutilusht Grid. This unplanned interconnection compelled Reshun HPP consumers to bear unanticipated operational expenditures, as the existing infrastructure was not designed to accommodate external grid injection. Furthermore, the plant’s operational viability was severely compromised by catastrophic flooding in 2015, resulting in a complete generation halt until its rehabilitation. This six-year operational disruption caused significant generation deficits and cumulative revenue losses, exacerbating financial strain on both the facility and its consumer base. Flash floods and Glacial Lake Outburst Floods (GLOF) in 2024 and specifically July-August 2024 floods have resulted in damages to the protection wall and allied civil structures of the power plant thereby resulted in the generation loss in shape of time-to-time shutdown of one or two units out of total three units. Also, in the aftermaths of these floods comparatively less hydrology has been recorded which did not allow electricity generation as per its installed capacity. After the diversion of pipeline from Shakagol to reservoir and rehabilitation of RCC Protection/retaining wall of the power plant, the forecasted energy target can be achieved. | No remarks | 25 | 19.95 | 5.05 | 0.28 | 3.8337 | -3.5537 | 0.76281 | Cost Pressure: Expenditure growth is higher than revenue growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Reshun HPS | 4.2 | 2010-07-01 | 2011-06-30 | 2010-2011 | 25 | 12.21 | 0.024 | 12.186 | 12.79 | 34.35 | 19.68 | 14.67 | The Reshun Hydropower Plant (HPP), operational since 1999, has been providing electricity to over 19,000 off-grid consumers. However, due to a sustained overload demand exceeding its installed capacity of 4.2 MW, systemic load shedding became inevitable, necessitating compensatory measures. During the Prime Minister’s inauguration of the Golen Gol HPP, the PESCO electricity supply was integrated into the Reshun HPP Transmission Line via the Jutilusht Grid. This unplanned interconnection compelled Reshun HPP consumers to bear unanticipated operational expenditures, as the existing infrastructure was not designed to accommodate external grid injection. Furthermore, the plant’s operational viability was severely compromised by catastrophic flooding in 2015, resulting in a complete generation halt until its rehabilitation. This six-year operational disruption caused significant generation deficits and cumulative revenue losses, exacerbating financial strain on both the facility and its consumer base. Flash floods and Glacial Lake Outburst Floods (GLOF) in 2024 and specifically July-August 2024 floods have resulted in damages to the protection wall and allied civil structures of the power plant thereby resulted in the generation loss in shape of time-to-time shutdown of one or two units out of total three units. Also, in the aftermaths of these floods comparatively less hydrology has been recorded which did not allow electricity generation as per its installed capacity. After the diversion of pipeline from Shakagol to reservoir and rehabilitation of RCC Protection/retaining wall of the power plant, the forecasted energy target can be achieved. | No remarks | 32 | 7.59 | 24.41 | 0.073438 | -0.39902 | 0.47245 | 0.42707 | Efficient Plant: Revenue growth exceeds expenditure growth | 2.7 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Reshun HPS | 4.2 | 2011-07-01 | 2012-06-30 | 2011-2012 | 25 | 12.52 | 0.025 | 12.495 | 12.48 | 34.91 | 57.61 | -22.7 | The Reshun Hydropower Plant (HPP), operational since 1999, has been providing electricity to over 19,000 off-grid consumers. However, due to a sustained overload demand exceeding its installed capacity of 4.2 MW, systemic load shedding became inevitable, necessitating compensatory measures. During the Prime Minister’s inauguration of the Golen Gol HPP, the PESCO electricity supply was integrated into the Reshun HPP Transmission Line via the Jutilusht Grid. This unplanned interconnection compelled Reshun HPP consumers to bear unanticipated operational expenditures, as the existing infrastructure was not designed to accommodate external grid injection. Furthermore, the plant’s operational viability was severely compromised by catastrophic flooding in 2015, resulting in a complete generation halt until its rehabilitation. This six-year operational disruption caused significant generation deficits and cumulative revenue losses, exacerbating financial strain on both the facility and its consumer base. Flash floods and Glacial Lake Outburst Floods (GLOF) in 2024 and specifically July-August 2024 floods have resulted in damages to the protection wall and allied civil structures of the power plant thereby resulted in the generation loss in shape of time-to-time shutdown of one or two units out of total three units. Also, in the aftermaths of these floods comparatively less hydrology has been recorded which did not allow electricity generation as per its installed capacity. After the diversion of pipeline from Shakagol to reservoir and rehabilitation of RCC Protection/retaining wall of the power plant, the forecasted energy target can be achieved. | No remarks | 34.35 | 19.68 | 14.67 | 0.016303 | -2.5474 | 2.5637 | -0.65024 | Efficient Plant: Revenue growth exceeds expenditure growth | 1.9 | Poor | 🔴 | Declining revenue or high expenditure with low profitability | Immediate management intervention required; perform financial and technical audit; reduce operational costs urgently; identify causes of low revenue; address outages and inefficiencies; consider restructuring or rehabilitation plan
Reshun HPS | 4.2 | 2012-07-01 | 2013-06-30 | 2012-2013 | 25 | 13.59 | 0.027 | 13.563 | 11.41 | 42.95 | 28.5 | 14.45 | The Reshun Hydropower Plant (HPP), operational since 1999, has been providing electricity to over 19,000 off-grid consumers. However, due to a sustained overload demand exceeding its installed capacity of 4.2 MW, systemic load shedding became inevitable, necessitating compensatory measures. During the Prime Minister’s inauguration of the Golen Gol HPP, the PESCO electricity supply was integrated into the Reshun HPP Transmission Line via the Jutilusht Grid. This unplanned interconnection compelled Reshun HPP consumers to bear unanticipated operational expenditures, as the existing infrastructure was not designed to accommodate external grid injection. Furthermore, the plant’s operational viability was severely compromised by catastrophic flooding in 2015, resulting in a complete generation halt until its rehabilitation. This six-year operational disruption caused significant generation deficits and cumulative revenue losses, exacerbating financial strain on both the facility and its consumer base. Flash floods and Glacial Lake Outburst Floods (GLOF) in 2024 and specifically July-August 2024 floods have resulted in damages to the protection wall and allied civil structures of the power plant thereby resulted in the generation loss in shape of time-to-time shutdown of one or two units out of total three units. Also, in the aftermaths of these floods comparatively less hydrology has been recorded which did not allow electricity generation as per its installed capacity. After the diversion of pipeline from Shakagol to reservoir and rehabilitation of RCC Protection/retaining wall of the power plant, the forecasted energy target can be achieved. | No remarks | 34.91 | 57.61 | -22.7 | 0.23031 | -1.6366 | 1.8669 | 0.33644 | Efficient Plant: Revenue growth exceeds expenditure growth | 3 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Reshun HPS | 4.2 | 2013-07-01 | 2014-06-30 | 2013-2014 | 25 | 11.52 | 0.023 | 11.497 | 13.48 | 40.6 | 51.15 | -10.55 | The Reshun Hydropower Plant (HPP), operational since 1999, has been providing electricity to over 19,000 off-grid consumers. However, due to a sustained overload demand exceeding its installed capacity of 4.2 MW, systemic load shedding became inevitable, necessitating compensatory measures. During the Prime Minister’s inauguration of the Golen Gol HPP, the PESCO electricity supply was integrated into the Reshun HPP Transmission Line via the Jutilusht Grid. This unplanned interconnection compelled Reshun HPP consumers to bear unanticipated operational expenditures, as the existing infrastructure was not designed to accommodate external grid injection. Furthermore, the plant’s operational viability was severely compromised by catastrophic flooding in 2015, resulting in a complete generation halt until its rehabilitation. This six-year operational disruption caused significant generation deficits and cumulative revenue losses, exacerbating financial strain on both the facility and its consumer base. Flash floods and Glacial Lake Outburst Floods (GLOF) in 2024 and specifically July-August 2024 floods have resulted in damages to the protection wall and allied civil structures of the power plant thereby resulted in the generation loss in shape of time-to-time shutdown of one or two units out of total three units. Also, in the aftermaths of these floods comparatively less hydrology has been recorded which did not allow electricity generation as per its installed capacity. After the diversion of pipeline from Shakagol to reservoir and rehabilitation of RCC Protection/retaining wall of the power plant, the forecasted energy target can be achieved. | No remarks | 42.95 | 28.5 | 14.45 | -0.054715 | -1.7301 | 1.6754 | -0.25985 | Efficient Plant: Revenue growth exceeds expenditure growth | 1.6 | Poor | 🔴 | Declining revenue or high expenditure with low profitability | Immediate management intervention required; perform financial and technical audit; reduce operational costs urgently; identify causes of low revenue; address outages and inefficiencies; consider restructuring or rehabilitation plan
Reshun HPS | 4.2 | 2014-07-01 | 2015-06-30 | 2014-2015 | 25 | 12.2 | 0.024 | 12.176 | 12.8 | 45.74 | 29.62 | 16.12 | The Reshun Hydropower Plant (HPP), operational since 1999, has been providing electricity to over 19,000 off-grid consumers. However, due to a sustained overload demand exceeding its installed capacity of 4.2 MW, systemic load shedding became inevitable, necessitating compensatory measures. During the Prime Minister’s inauguration of the Golen Gol HPP, the PESCO electricity supply was integrated into the Reshun HPP Transmission Line via the Jutilusht Grid. This unplanned interconnection compelled Reshun HPP consumers to bear unanticipated operational expenditures, as the existing infrastructure was not designed to accommodate external grid injection. Furthermore, the plant’s operational viability was severely compromised by catastrophic flooding in 2015, resulting in a complete generation halt until its rehabilitation. This six-year operational disruption caused significant generation deficits and cumulative revenue losses, exacerbating financial strain on both the facility and its consumer base. Flash floods and Glacial Lake Outburst Floods (GLOF) in 2024 and specifically July-August 2024 floods have resulted in damages to the protection wall and allied civil structures of the power plant thereby resulted in the generation loss in shape of time-to-time shutdown of one or two units out of total three units. Also, in the aftermaths of these floods comparatively less hydrology has been recorded which did not allow electricity generation as per its installed capacity. After the diversion of pipeline from Shakagol to reservoir and rehabilitation of RCC Protection/retaining wall of the power plant, the forecasted energy target can be achieved. | No remarks | 40.6 | 51.15 | -10.55 | 0.1266 | -2.528 | 2.6546 | 0.35243 | Efficient Plant: Revenue growth exceeds expenditure growth | 3 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Reshun HPS | 4.2 | 2015-07-01 | 2016-06-30 | 2015-2016 | 25 | 0 | 0 | 0 | 25 | 2.48 | 37.46 | -34.99 | The Reshun Hydropower Plant (HPP), operational since 1999, has been providing electricity to over 19,000 off-grid consumers. However, due to a sustained overload demand exceeding its installed capacity of 4.2 MW, systemic load shedding became inevitable, necessitating compensatory measures. During the Prime Minister’s inauguration of the Golen Gol HPP, the PESCO electricity supply was integrated into the Reshun HPP Transmission Line via the Jutilusht Grid. This unplanned interconnection compelled Reshun HPP consumers to bear unanticipated operational expenditures, as the existing infrastructure was not designed to accommodate external grid injection. Furthermore, the plant’s operational viability was severely compromised by catastrophic flooding in 2015, resulting in a complete generation halt until its rehabilitation. This six-year operational disruption caused significant generation deficits and cumulative revenue losses, exacerbating financial strain on both the facility and its consumer base. Flash floods and Glacial Lake Outburst Floods (GLOF) in 2024 and specifically July-August 2024 floods have resulted in damages to the protection wall and allied civil structures of the power plant thereby resulted in the generation loss in shape of time-to-time shutdown of one or two units out of total three units. Also, in the aftermaths of these floods comparatively less hydrology has been recorded which did not allow electricity generation as per its installed capacity. After the diversion of pipeline from Shakagol to reservoir and rehabilitation of RCC Protection/retaining wall of the power plant, the forecasted energy target can be achieved. | No remarks | 45.74 | 29.62 | 16.12 | -0.94578 | -3.1706 | 2.2248 | -14.1089 | Efficient Plant: Revenue growth exceeds expenditure growth | 1.6 | Poor | 🔴 | Declining revenue or high expenditure with low profitability | Immediate management intervention required; perform financial and technical audit; reduce operational costs urgently; identify causes of low revenue; address outages and inefficiencies; consider restructuring or rehabilitation plan
Reshun HPS | 4.2 | 2016-07-01 | 2017-06-30 | 2016-2017 | 25 | 0 | 0 | 0 | 25 | 0 | 23.74 | -23.74 | The Reshun Hydropower Plant (HPP), operational since 1999, has been providing electricity to over 19,000 off-grid consumers. However, due to a sustained overload demand exceeding its installed capacity of 4.2 MW, systemic load shedding became inevitable, necessitating compensatory measures. During the Prime Minister’s inauguration of the Golen Gol HPP, the PESCO electricity supply was integrated into the Reshun HPP Transmission Line via the Jutilusht Grid. This unplanned interconnection compelled Reshun HPP consumers to bear unanticipated operational expenditures, as the existing infrastructure was not designed to accommodate external grid injection. Furthermore, the plant’s operational viability was severely compromised by catastrophic flooding in 2015, resulting in a complete generation halt until its rehabilitation. This six-year operational disruption caused significant generation deficits and cumulative revenue losses, exacerbating financial strain on both the facility and its consumer base. Flash floods and Glacial Lake Outburst Floods (GLOF) in 2024 and specifically July-August 2024 floods have resulted in damages to the protection wall and allied civil structures of the power plant thereby resulted in the generation loss in shape of time-to-time shutdown of one or two units out of total three units. Also, in the aftermaths of these floods comparatively less hydrology has been recorded which did not allow electricity generation as per its installed capacity. After the diversion of pipeline from Shakagol to reservoir and rehabilitation of RCC Protection/retaining wall of the power plant, the forecasted energy target can be achieved. | No remarks | 2.48 | 37.46 | -34.99 | -1 | -0.32152 | -0.67848 |  | Cost Pressure: Expenditure growth is higher than revenue growth |  | Not available (insufficient data) | Not available (insufficient data) | Not available (insufficient data) | Not available (insufficient data)
Reshun HPS | 4.2 | 2017-07-01 | 2018-06-30 | 2017-2018 | 25 | 0 | 0 | 0 | 25 | 0 | 23.66 | -23.66 | The Reshun Hydropower Plant (HPP), operational since 1999, has been providing electricity to over 19,000 off-grid consumers. However, due to a sustained overload demand exceeding its installed capacity of 4.2 MW, systemic load shedding became inevitable, necessitating compensatory measures. During the Prime Minister’s inauguration of the Golen Gol HPP, the PESCO electricity supply was integrated into the Reshun HPP Transmission Line via the Jutilusht Grid. This unplanned interconnection compelled Reshun HPP consumers to bear unanticipated operational expenditures, as the existing infrastructure was not designed to accommodate external grid injection. Furthermore, the plant’s operational viability was severely compromised by catastrophic flooding in 2015, resulting in a complete generation halt until its rehabilitation. This six-year operational disruption caused significant generation deficits and cumulative revenue losses, exacerbating financial strain on both the facility and its consumer base. Flash floods and Glacial Lake Outburst Floods (GLOF) in 2024 and specifically July-August 2024 floods have resulted in damages to the protection wall and allied civil structures of the power plant thereby resulted in the generation loss in shape of time-to-time shutdown of one or two units out of total three units. Also, in the aftermaths of these floods comparatively less hydrology has been recorded which did not allow electricity generation as per its installed capacity. After the diversion of pipeline from Shakagol to reservoir and rehabilitation of RCC Protection/retaining wall of the power plant, the forecasted energy target can be achieved. | No remarks | 0 | 23.74 | -23.74 |  | -0.0033698 | 0.0033698 |  | Efficient Plant: Revenue growth exceeds expenditure growth |  | Not available (insufficient data) | Not available (insufficient data) | Not available (insufficient data) | Not available (insufficient data)
Reshun HPS | 4.2 | 2018-07-01 | 2019-06-30 | 2018-2019 | 25 | 21 | 0.042 | 20.958 | 4 | 86.56 | 49.5 | 37.05 | The Reshun Hydropower Plant (HPP), operational since 1999, has been providing electricity to over 19,000 off-grid consumers. However, due to a sustained overload demand exceeding its installed capacity of 4.2 MW, systemic load shedding became inevitable, necessitating compensatory measures. During the Prime Minister’s inauguration of the Golen Gol HPP, the PESCO electricity supply was integrated into the Reshun HPP Transmission Line via the Jutilusht Grid. This unplanned interconnection compelled Reshun HPP consumers to bear unanticipated operational expenditures, as the existing infrastructure was not designed to accommodate external grid injection. Furthermore, the plant’s operational viability was severely compromised by catastrophic flooding in 2015, resulting in a complete generation halt until its rehabilitation. This six-year operational disruption caused significant generation deficits and cumulative revenue losses, exacerbating financial strain on both the facility and its consumer base. Flash floods and Glacial Lake Outburst Floods (GLOF) in 2024 and specifically July-August 2024 floods have resulted in damages to the protection wall and allied civil structures of the power plant thereby resulted in the generation loss in shape of time-to-time shutdown of one or two units out of total three units. Also, in the aftermaths of these floods comparatively less hydrology has been recorded which did not allow electricity generation as per its installed capacity. After the diversion of pipeline from Shakagol to reservoir and rehabilitation of RCC Protection/retaining wall of the power plant, the forecasted energy target can be achieved. | No remarks | 0 | 23.66 | -23.66 |  | -2.5659 | 2.5659 | 0.42803 | Efficient Plant: Revenue growth exceeds expenditure growth | 3 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Reshun HPS | 4.2 | 2019-07-01 | 2020-06-30 | 2019-2020 | 25 | 23.9 | 0.048 | 23.852 | 1.1 | 92.39 | 48.01 | 44.37 | The Reshun Hydropower Plant (HPP), operational since 1999, has been providing electricity to over 19,000 off-grid consumers. However, due to a sustained overload demand exceeding its installed capacity of 4.2 MW, systemic load shedding became inevitable, necessitating compensatory measures. During the Prime Minister’s inauguration of the Golen Gol HPP, the PESCO electricity supply was integrated into the Reshun HPP Transmission Line via the Jutilusht Grid. This unplanned interconnection compelled Reshun HPP consumers to bear unanticipated operational expenditures, as the existing infrastructure was not designed to accommodate external grid injection. Furthermore, the plant’s operational viability was severely compromised by catastrophic flooding in 2015, resulting in a complete generation halt until its rehabilitation. This six-year operational disruption caused significant generation deficits and cumulative revenue losses, exacerbating financial strain on both the facility and its consumer base. Flash floods and Glacial Lake Outburst Floods (GLOF) in 2024 and specifically July-August 2024 floods have resulted in damages to the protection wall and allied civil structures of the power plant thereby resulted in the generation loss in shape of time-to-time shutdown of one or two units out of total three units. Also, in the aftermaths of these floods comparatively less hydrology has been recorded which did not allow electricity generation as per its installed capacity. After the diversion of pipeline from Shakagol to reservoir and rehabilitation of RCC Protection/retaining wall of the power plant, the forecasted energy target can be achieved. | No remarks | 86.56 | 49.5 | 37.05 | 0.067352 | 0.19757 | -0.13022 | 0.48025 | Cost Pressure: Expenditure growth is higher than revenue growth | 2.1 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Reshun HPS | 4.2 | 2020-07-01 | 2021-06-30 | 2020-2021 | 25 | 30.8 | 0.062 | 30.738 | -5.8 | 114.71 | 42.03 | 72.69 | The Reshun Hydropower Plant (HPP), operational since 1999, has been providing electricity to over 19,000 off-grid consumers. However, due to a sustained overload demand exceeding its installed capacity of 4.2 MW, systemic load shedding became inevitable, necessitating compensatory measures. During the Prime Minister’s inauguration of the Golen Gol HPP, the PESCO electricity supply was integrated into the Reshun HPP Transmission Line via the Jutilusht Grid. This unplanned interconnection compelled Reshun HPP consumers to bear unanticipated operational expenditures, as the existing infrastructure was not designed to accommodate external grid injection. Furthermore, the plant’s operational viability was severely compromised by catastrophic flooding in 2015, resulting in a complete generation halt until its rehabilitation. This six-year operational disruption caused significant generation deficits and cumulative revenue losses, exacerbating financial strain on both the facility and its consumer base. Flash floods and Glacial Lake Outburst Floods (GLOF) in 2024 and specifically July-August 2024 floods have resulted in damages to the protection wall and allied civil structures of the power plant thereby resulted in the generation loss in shape of time-to-time shutdown of one or two units out of total three units. Also, in the aftermaths of these floods comparatively less hydrology has been recorded which did not allow electricity generation as per its installed capacity. After the diversion of pipeline from Shakagol to reservoir and rehabilitation of RCC Protection/retaining wall of the power plant, the forecasted energy target can be achieved. | No remarks | 92.39 | 48.01 | 44.37 | 0.24158 | 0.63827 | -0.39668 | 0.63368 | Cost Pressure: Expenditure growth is higher than revenue growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Reshun HPS | 4.2 | 2021-07-01 | 2022-06-30 | 2021-2022 | 25 | 33.2 | 0.066 | 33.134 | -8.2 | 129.13 | 56.13 | 73 | The Reshun Hydropower Plant (HPP), operational since 1999, has been providing electricity to over 19,000 off-grid consumers. However, due to a sustained overload demand exceeding its installed capacity of 4.2 MW, systemic load shedding became inevitable, necessitating compensatory measures. During the Prime Minister’s inauguration of the Golen Gol HPP, the PESCO electricity supply was integrated into the Reshun HPP Transmission Line via the Jutilusht Grid. This unplanned interconnection compelled Reshun HPP consumers to bear unanticipated operational expenditures, as the existing infrastructure was not designed to accommodate external grid injection. Furthermore, the plant’s operational viability was severely compromised by catastrophic flooding in 2015, resulting in a complete generation halt until its rehabilitation. This six-year operational disruption caused significant generation deficits and cumulative revenue losses, exacerbating financial strain on both the facility and its consumer base. Flash floods and Glacial Lake Outburst Floods (GLOF) in 2024 and specifically July-August 2024 floods have resulted in damages to the protection wall and allied civil structures of the power plant thereby resulted in the generation loss in shape of time-to-time shutdown of one or two units out of total three units. Also, in the aftermaths of these floods comparatively less hydrology has been recorded which did not allow electricity generation as per its installed capacity. After the diversion of pipeline from Shakagol to reservoir and rehabilitation of RCC Protection/retaining wall of the power plant, the forecasted energy target can be achieved. | No remarks | 114.71 | 42.03 | 72.69 | 0.12571 | 0.0042647 | 0.12144 | 0.56532 | Efficient Plant: Revenue growth exceeds expenditure growth | 3 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Reshun HPS | 4.2 | 2022-07-01 | 2023-06-30 | 2022-2023 | 25 | 25.94 | 0.052 | 25.888 | -0.94 | 155.54 | 119.84 | 35.7 | The Reshun Hydropower Plant (HPP), operational since 1999, has been providing electricity to over 19,000 off-grid consumers. However, due to a sustained overload demand exceeding its installed capacity of 4.2 MW, systemic load shedding became inevitable, necessitating compensatory measures. During the Prime Minister’s inauguration of the Golen Gol HPP, the PESCO electricity supply was integrated into the Reshun HPP Transmission Line via the Jutilusht Grid. This unplanned interconnection compelled Reshun HPP consumers to bear unanticipated operational expenditures, as the existing infrastructure was not designed to accommodate external grid injection. Furthermore, the plant’s operational viability was severely compromised by catastrophic flooding in 2015, resulting in a complete generation halt until its rehabilitation. This six-year operational disruption caused significant generation deficits and cumulative revenue losses, exacerbating financial strain on both the facility and its consumer base. Flash floods and Glacial Lake Outburst Floods (GLOF) in 2024 and specifically July-August 2024 floods have resulted in damages to the protection wall and allied civil structures of the power plant thereby resulted in the generation loss in shape of time-to-time shutdown of one or two units out of total three units. Also, in the aftermaths of these floods comparatively less hydrology has been recorded which did not allow electricity generation as per its installed capacity. After the diversion of pipeline from Shakagol to reservoir and rehabilitation of RCC Protection/retaining wall of the power plant, the forecasted energy target can be achieved. | No remarks | 129.13 | 56.13 | 73 | 0.20452 | -0.51096 | 0.71548 | 0.22952 | Efficient Plant: Revenue growth exceeds expenditure growth | 3 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Reshun HPS | 4.2 | 2023-07-01 | 2024-06-30 | 2023-2024 | 25 | 27.25 | 0.055 | 27.196 | -2.25 | 302.7 | 503.19 | -200.49 | The Reshun Hydropower Plant (HPP), operational since 1999, has been providing electricity to over 19,000 off-grid consumers. However, due to a sustained overload demand exceeding its installed capacity of 4.2 MW, systemic load shedding became inevitable, necessitating compensatory measures. During the Prime Minister’s inauguration of the Golen Gol HPP, the PESCO electricity supply was integrated into the Reshun HPP Transmission Line via the Jutilusht Grid. This unplanned interconnection compelled Reshun HPP consumers to bear unanticipated operational expenditures, as the existing infrastructure was not designed to accommodate external grid injection. Furthermore, the plant’s operational viability was severely compromised by catastrophic flooding in 2015, resulting in a complete generation halt until its rehabilitation. This six-year operational disruption caused significant generation deficits and cumulative revenue losses, exacerbating financial strain on both the facility and its consumer base. Flash floods and Glacial Lake Outburst Floods (GLOF) in 2024 and specifically July-August 2024 floods have resulted in damages to the protection wall and allied civil structures of the power plant thereby resulted in the generation loss in shape of time-to-time shutdown of one or two units out of total three units. Also, in the aftermaths of these floods comparatively less hydrology has been recorded which did not allow electricity generation as per its installed capacity. After the diversion of pipeline from Shakagol to reservoir and rehabilitation of RCC Protection/retaining wall of the power plant, the forecasted energy target can be achieved. | No remarks | 155.54 | 119.84 | 35.7 | 0.94612 | -6.616 | 7.5621 | -0.66234 | Efficient Plant: Revenue growth exceeds expenditure growth | 2.2 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Reshun HPS | 4.2 | 2024-07-01 | 2025-06-30 | 2024-2025 | 25 | 20.79 | 0.042 | 20.748 | 4.21 | 156 | 650 | -494 | The Reshun Hydropower Plant (HPP), operational since 1999, has been providing electricity to over 19,000 off-grid consumers. However, due to a sustained overload demand exceeding its installed capacity of 4.2 MW, systemic load shedding became inevitable, necessitating compensatory measures. During the Prime Minister’s inauguration of the Golen Gol HPP, the PESCO electricity supply was integrated into the Reshun HPP Transmission Line via the Jutilusht Grid. This unplanned interconnection compelled Reshun HPP consumers to bear unanticipated operational expenditures, as the existing infrastructure was not designed to accommodate external grid injection. Furthermore, the plant’s operational viability was severely compromised by catastrophic flooding in 2015, resulting in a complete generation halt until its rehabilitation. This six-year operational disruption caused significant generation deficits and cumulative revenue losses, exacerbating financial strain on both the facility and its consumer base. Flash floods and Glacial Lake Outburst Floods (GLOF) in 2024 and specifically July-August 2024 floods have resulted in damages to the protection wall and allied civil structures of the power plant thereby resulted in the generation loss in shape of time-to-time shutdown of one or two units out of total three units. Also, in the aftermaths of these floods comparatively less hydrology has been recorded which did not allow electricity generation as per its installed capacity. After the diversion of pipeline from Shakagol to reservoir and rehabilitation of RCC Protection/retaining wall of the power plant, the forecasted energy target can be achieved. | No remarks | 302.7 | 503.19 | -200.49 | -0.48464 | 1.464 | -1.9486 | -3.1667 | Cost Pressure: Expenditure growth is higher than revenue growth | 1 | Poor | 🔴 | Declining revenue or high expenditure with low profitability | Immediate management intervention required; perform financial and technical audit; reduce operational costs urgently; identify causes of low revenue; address outages and inefficiencies; consider restructuring or rehabilitation plan
Shishi HPS | 1.8 | 2011-07-01 | 2012-06-30 | 2011-2012 | 8 | 5.98 | 0.01196 | 5.968 | 2.02 | 17.93 | 20.47 | -2.54 | Shishi HPC generates electricity as per the required load demand of one out of three feeders of Shishi, lower Chitral district, for which it has been mandated under the agreement between PEDO & PESCO. The maximum demand of that feeder is 800 kW while its average load demand is 400 kW therefore; it cannot exceed its energy generation beyond feeder load demand. Moreover, besides low flow season in winters, in high flow season, due to excessive hydrology, the power plant is mostly kept shutdown due to abnormal sand and gravel in the Shishi intake which results in damage to the runner blades. It is pertinent to mention that during the floods season, the power plant do not generate electricity ultimately resulting in plant shutdown to further prevent mechanical stress and damage to the plant machinery thereby it avoids optimal energy production. | No remarks | [5 empty] | 0 | -0.14166 | Stable: Revenue and expenditure are growing at the same pace | 1.6 | Poor | 🔴 | Declining revenue or high expenditure with low profitability | Immediate management intervention required; perform financial and technical audit; reduce operational costs urgently; identify causes of low revenue; address outages and inefficiencies; consider restructuring or rehabilitation plan
Shishi HPS | 1.8 | 2012-07-01 | 2013-06-30 | 2012-2013 | 8 | 4.17 | 0.00834 | 4.1617 | 3.83 | 12.51 | 21.58 | -9.07 | Shishi HPC generates electricity as per the required load demand of one out of three feeders of Shishi, lower Chitral district, for which it has been mandated under the agreement between PEDO & PESCO. The maximum demand of that feeder is 800 kW while its average load demand is 400 kW therefore; it cannot exceed its energy generation beyond feeder load demand. Moreover, besides low flow season in winters, in high flow season, due to excessive hydrology, the power plant is mostly kept shutdown due to abnormal sand and gravel in the Shishi intake which results in damage to the runner blades. It is pertinent to mention that during the floods season, the power plant do not generate electricity ultimately resulting in plant shutdown to further prevent mechanical stress and damage to the plant machinery thereby it avoids optimal energy production. | No remarks | 17.93 | 20.47 | -2.54 | -0.30229 | 2.5709 | -2.8732 | -0.72502 | Cost Pressure: Expenditure growth is higher than revenue growth | 1 | Poor | 🔴 | Declining revenue or high expenditure with low profitability | Immediate management intervention required; perform financial and technical audit; reduce operational costs urgently; identify causes of low revenue; address outages and inefficiencies; consider restructuring or rehabilitation plan
Shishi HPS | 1.8 | 2013-07-01 | 2014-06-30 | 2013-2014 | 8 | 5 | 0.01 | 4.99 | 3 | 15 | 27.65 | -12.65 | Shishi HPC generates electricity as per the required load demand of one out of three feeders of Shishi, lower Chitral district, for which it has been mandated under the agreement between PEDO & PESCO. The maximum demand of that feeder is 800 kW while its average load demand is 400 kW therefore; it cannot exceed its energy generation beyond feeder load demand. Moreover, besides low flow season in winters, in high flow season, due to excessive hydrology, the power plant is mostly kept shutdown due to abnormal sand and gravel in the Shishi intake which results in damage to the runner blades. It is pertinent to mention that during the floods season, the power plant do not generate electricity ultimately resulting in plant shutdown to further prevent mechanical stress and damage to the plant machinery thereby it avoids optimal energy production. | No remarks | 12.51 | 21.58 | -9.07 | 0.19904 | 0.39471 | -0.19567 | -0.84333 | Cost Pressure: Expenditure growth is higher than revenue growth | 1.6 | Poor | 🔴 | Declining revenue or high expenditure with low profitability | Immediate management intervention required; perform financial and technical audit; reduce operational costs urgently; identify causes of low revenue; address outages and inefficiencies; consider restructuring or rehabilitation plan
Shishi HPS | 1.8 | 2014-07-01 | 2015-06-30 | 2014-2015 | 8 | 3.5 | 0.007 | 3.493 | 4.5 | 10.48 | 10.41 | 0.07 | Shishi HPC generates electricity as per the required load demand of one out of three feeders of Shishi, lower Chitral district, for which it has been mandated under the agreement between PEDO & PESCO. The maximum demand of that feeder is 800 kW while its average load demand is 400 kW therefore; it cannot exceed its energy generation beyond feeder load demand. Moreover, besides low flow season in winters, in high flow season, due to excessive hydrology, the power plant is mostly kept shutdown due to abnormal sand and gravel in the Shishi intake which results in damage to the runner blades. It is pertinent to mention that during the floods season, the power plant do not generate electricity ultimately resulting in plant shutdown to further prevent mechanical stress and damage to the plant machinery thereby it avoids optimal energy production. | No remarks | 15 | 27.65 | -12.65 | -0.30133 | -1.0055 | 0.7042 | 0.0066794 | Efficient Plant: Revenue growth exceeds expenditure growth | 1.6 | Poor | 🔴 | Declining revenue or high expenditure with low profitability | Immediate management intervention required; perform financial and technical audit; reduce operational costs urgently; identify causes of low revenue; address outages and inefficiencies; consider restructuring or rehabilitation plan
Shishi HPS | 1.8 | 2015-07-01 | 2016-06-30 | 2015-2016 | 8 | 6.98 | 0.01396 | 6.966 | 1.02 | 20.94 | 21.84 | -0.9 | Shishi HPC generates electricity as per the required load demand of one out of three feeders of Shishi, lower Chitral district, for which it has been mandated under the agreement between PEDO & PESCO. The maximum demand of that feeder is 800 kW while its average load demand is 400 kW therefore; it cannot exceed its energy generation beyond feeder load demand. Moreover, besides low flow season in winters, in high flow season, due to excessive hydrology, the power plant is mostly kept shutdown due to abnormal sand and gravel in the Shishi intake which results in damage to the runner blades. It is pertinent to mention that during the floods season, the power plant do not generate electricity ultimately resulting in plant shutdown to further prevent mechanical stress and damage to the plant machinery thereby it avoids optimal energy production. | No remarks | 10.48 | 10.41 | 0.07 | 0.99809 | -13.8571 | 14.8552 | -0.04298 | Efficient Plant: Revenue growth exceeds expenditure growth | 2.2 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Shishi HPS | 1.8 | 2016-07-01 | 2017-06-30 | 2016-2017 | 8 | 3.45 | 0.0069 | 3.4431 | 4.55 | 10.35 | 7.69 | 2.66 | Shishi HPC generates electricity as per the required load demand of one out of three feeders of Shishi, lower Chitral district, for which it has been mandated under the agreement between PEDO & PESCO. The maximum demand of that feeder is 800 kW while its average load demand is 400 kW therefore; it cannot exceed its energy generation beyond feeder load demand. Moreover, besides low flow season in winters, in high flow season, due to excessive hydrology, the power plant is mostly kept shutdown due to abnormal sand and gravel in the Shishi intake which results in damage to the runner blades. It is pertinent to mention that during the floods season, the power plant do not generate electricity ultimately resulting in plant shutdown to further prevent mechanical stress and damage to the plant machinery thereby it avoids optimal energy production. | No remarks | 20.94 | 21.84 | -0.9 | -0.50573 | -3.9556 | 3.4498 | 0.257 | Efficient Plant: Revenue growth exceeds expenditure growth | 2.4 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Shishi HPS | 1.8 | 2017-07-01 | 2018-06-30 | 2017-2018 | 8 | 1.07 | 0.00214 | 1.0679 | 6.93 | 3.2 | 7.19 | -3.99 | Shishi HPC generates electricity as per the required load demand of one out of three feeders of Shishi, lower Chitral district, for which it has been mandated under the agreement between PEDO & PESCO. The maximum demand of that feeder is 800 kW while its average load demand is 400 kW therefore; it cannot exceed its energy generation beyond feeder load demand. Moreover, besides low flow season in winters, in high flow season, due to excessive hydrology, the power plant is mostly kept shutdown due to abnormal sand and gravel in the Shishi intake which results in damage to the runner blades. It is pertinent to mention that during the floods season, the power plant do not generate electricity ultimately resulting in plant shutdown to further prevent mechanical stress and damage to the plant machinery thereby it avoids optimal energy production. | No remarks | 10.35 | 7.69 | 2.66 | -0.69082 | -2.5 | 1.8092 | -1.2469 | Efficient Plant: Revenue growth exceeds expenditure growth | 1.6 | Poor | 🔴 | Declining revenue or high expenditure with low profitability | Immediate management intervention required; perform financial and technical audit; reduce operational costs urgently; identify causes of low revenue; address outages and inefficiencies; consider restructuring or rehabilitation plan
Shishi HPS | 1.8 | 2018-07-01 | 2019-06-30 | 2018-2019 | 8 | 1.3 | 0.0026 | 1.2974 | 6.7 | 3.9 | 9.23 | -5.33 | Shishi HPC generates electricity as per the required load demand of one out of three feeders of Shishi, lower Chitral district, for which it has been mandated under the agreement between PEDO & PESCO. The maximum demand of that feeder is 800 kW while its average load demand is 400 kW therefore; it cannot exceed its energy generation beyond feeder load demand. Moreover, besides low flow season in winters, in high flow season, due to excessive hydrology, the power plant is mostly kept shutdown due to abnormal sand and gravel in the Shishi intake which results in damage to the runner blades. It is pertinent to mention that during the floods season, the power plant do not generate electricity ultimately resulting in plant shutdown to further prevent mechanical stress and damage to the plant machinery thereby it avoids optimal energy production. | No remarks | 3.2 | 7.19 | -3.99 | 0.21875 | 0.33584 | -0.11709 | -1.3667 | Cost Pressure: Expenditure growth is higher than revenue growth | 1.6 | Poor | 🔴 | Declining revenue or high expenditure with low profitability | Immediate management intervention required; perform financial and technical audit; reduce operational costs urgently; identify causes of low revenue; address outages and inefficiencies; consider restructuring or rehabilitation plan
Shishi HPS | 1.8 | 2019-07-01 | 2020-06-30 | 2019-2020 | 8 | 2.3 | 0.0046 | 2.2954 | 5.7 | 6.89 | 9.57 | -2.68 | Shishi HPC generates electricity as per the required load demand of one out of three feeders of Shishi, lower Chitral district, for which it has been mandated under the agreement between PEDO & PESCO. The maximum demand of that feeder is 800 kW while its average load demand is 400 kW therefore; it cannot exceed its energy generation beyond feeder load demand. Moreover, besides low flow season in winters, in high flow season, due to excessive hydrology, the power plant is mostly kept shutdown due to abnormal sand and gravel in the Shishi intake which results in damage to the runner blades. It is pertinent to mention that during the floods season, the power plant do not generate electricity ultimately resulting in plant shutdown to further prevent mechanical stress and damage to the plant machinery thereby it avoids optimal energy production. | No remarks | 3.9 | 9.23 | -5.33 | 0.76667 | -0.49719 | 1.2639 | -0.38897 | Efficient Plant: Revenue growth exceeds expenditure growth | 2.2 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Shishi HPS | 1.8 | 2020-07-01 | 2021-06-30 | 2020-2021 | 8 | 2.34 | 0.00468 | 2.3353 | 5.66 | 7.03 | 5.02 | 2.01 | Shishi HPC generates electricity as per the required load demand of one out of three feeders of Shishi, lower Chitral district, for which it has been mandated under the agreement between PEDO & PESCO. The maximum demand of that feeder is 800 kW while its average load demand is 400 kW therefore; it cannot exceed its energy generation beyond feeder load demand. Moreover, besides low flow season in winters, in high flow season, due to excessive hydrology, the power plant is mostly kept shutdown due to abnormal sand and gravel in the Shishi intake which results in damage to the runner blades. It is pertinent to mention that during the floods season, the power plant do not generate electricity ultimately resulting in plant shutdown to further prevent mechanical stress and damage to the plant machinery thereby it avoids optimal energy production. | No remarks | 6.89 | 9.57 | -2.68 | 0.020319 | -1.75 | 1.7703 | 0.28592 | Efficient Plant: Revenue growth exceeds expenditure growth | 2.7 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Shishi HPS | 1.8 | 2021-07-01 | 2022-06-30 | 2021-2022 | 8 | 2.64 | 0.00528 | 2.6347 | 5.36 | 7.9 | 12.28 | -4.38 | Shishi HPC generates electricity as per the required load demand of one out of three feeders of Shishi, lower Chitral district, for which it has been mandated under the agreement between PEDO & PESCO. The maximum demand of that feeder is 800 kW while its average load demand is 400 kW therefore; it cannot exceed its energy generation beyond feeder load demand. Moreover, besides low flow season in winters, in high flow season, due to excessive hydrology, the power plant is mostly kept shutdown due to abnormal sand and gravel in the Shishi intake which results in damage to the runner blades. It is pertinent to mention that during the floods season, the power plant do not generate electricity ultimately resulting in plant shutdown to further prevent mechanical stress and damage to the plant machinery thereby it avoids optimal energy production. | No remarks | 7.03 | 5.02 | 2.01 | 0.12376 | -3.1791 | 3.3029 | -0.55443 | Efficient Plant: Revenue growth exceeds expenditure growth | 2.2 | Average | 🟠 | Rising costs or weak growth affecting profitability | Conduct detailed cost audit; analyze expenditure drivers; reduce non-essential expenses; improve plant utilization factor; review staffing and maintenance efficiency; investigate revenue leakages
Shishi HPS | 1.8 | 2022-07-01 | 2023-06-30 | 2022-2023 | 8 | 2.17 | 0.00434 | 2.1657 | 5.83 | 1.16 | 17.72 | -16.56 | Shishi HPC generates electricity as per the required load demand of one out of three feeders of Shishi, lower Chitral district, for which it has been mandated under the agreement between PEDO & PESCO. The maximum demand of that feeder is 800 kW while its average load demand is 400 kW therefore; it cannot exceed its energy generation beyond feeder load demand. Moreover, besides low flow season in winters, in high flow season, due to excessive hydrology, the power plant is mostly kept shutdown due to abnormal sand and gravel in the Shishi intake which results in damage to the runner blades. It is pertinent to mention that during the floods season, the power plant do not generate electricity ultimately resulting in plant shutdown to further prevent mechanical stress and damage to the plant machinery thereby it avoids optimal energy production. | No remarks | 7.9 | 12.28 | -4.38 | -0.85316 | 2.7808 | -3.634 | -14.2759 | Cost Pressure: Expenditure growth is higher than revenue growth | 1 | Poor | 🔴 | Declining revenue or high expenditure with low profitability | Immediate management intervention required; perform financial and technical audit; reduce operational costs urgently; identify causes of low revenue; address outages and inefficiencies; consider restructuring or rehabilitation plan
Shishi HPS | 1.8 | 2023-07-01 | 2024-06-30 | 2023-2024 | 8 | 2.41 | 0.00482 | 2.4052 | 5.59 | 0 | 33.08 | -33.08 | Shishi HPC generates electricity as per the required load demand of one out of three feeders of Shishi, lower Chitral district, for which it has been mandated under the agreement between PEDO & PESCO. The maximum demand of that feeder is 800 kW while its average load demand is 400 kW therefore; it cannot exceed its energy generation beyond feeder load demand. Moreover, besides low flow season in winters, in high flow season, due to excessive hydrology, the power plant is mostly kept shutdown due to abnormal sand and gravel in the Shishi intake which results in damage to the runner blades. It is pertinent to mention that during the floods season, the power plant do not generate electricity ultimately resulting in plant shutdown to further prevent mechanical stress and damage to the plant machinery thereby it avoids optimal energy production. | No remarks | 1.16 | 17.72 | -16.56 | -1 | 0.99758 | -1.9976 |  | Cost Pressure: Expenditure growth is higher than revenue growth |  | Not available (insufficient data) | Not available (insufficient data) | Not available (insufficient data) | Not available (insufficient data)

## Installed_Capacity
Sr.No | Power Plant | Installed Capacity (MW)
1 | Daral Khwar HPS | 36.6
2 | Jabori HPS | 10.2
3 | Koto HPS | 40.8
4 | Machai HPS | 2.6
5 | Malakand-3 HPS | 81
6 | Reshun HPS | 4.2
7 | Shishi HPS | 1.8
8 | Pehur HPS | 18
9 | Karora HPS | 11.8

## Monthly_Expenditure
Date | Power Plant | Total Expenditure During the month (PKR)
2025-07-31 | Daral Khwar HPS | 9944438
2025-07-31 | Jabori HPS | 1618474
2025-07-31 | Machai HPS | 1619232
2025-07-31 | Malakand-3 HPS | 10711894
2025-07-31 | Pehur HPS | 2590755
2025-07-31 | Shishi HPS | 760902
2025-08-31 | Daral Khwar HPS | 9497890
2025-08-31 | Jabori HPS | 1510972
2025-08-31 | Koto HPS | 2681420
2025-08-31 | Machai HPS | 2392237
2025-08-31 | Malakand-3 HPS | 23895083
2025-08-31 | Pehur HPS | 11322428
2025-08-31 | Reshun HPS | 6724772
2025-08-31 | Shishi HPS | 1025917
2025-09-30 | Daral Khwar HPS | 37977157
2025-09-30 | Jabori HPS | 2512657
2025-09-30 | Karora HPS | 559401
2025-09-30 | Koto HPS | 2977986
2025-09-30 | Machai HPS | 2014430
2025-09-30 | Malakand-3 HPS | 6227322
2025-09-30 | Pehur HPS | 9463802
2025-09-30 | Reshun HPS | 6724772
2025-09-30 | Shishi HPS | 1025917
2025-10-31 | Daral Khwar HPS | 7676206
2025-10-31 | Jabori HPS | 1858462
2025-10-31 | Karora HPS | 412536
2025-10-31 | Koto HPS | 8305127
2025-10-31 | Machai HPS | 2576886
2025-10-31 | Malakand-3 HPS | 21389290
2025-10-31 | Pehur HPS | 7187670
2025-10-31 | Reshun HPS | 6429992
2025-11-30 | Daral Khwar HPS | 6773975
2025-11-30 | Jabori HPS | 2569582
2025-11-30 | Karora HPS | 961179
2025-11-30 | Koto HPS | 2581264
2025-11-30 | Machai HPS | 5083347
2025-11-30 | Malakand-3 HPS | 42290879
2025-11-30 | Pehur HPS | 19712845
2025-11-30 | Reshun HPS | 8345712
2025-12-31 | Daral Khwar HPS | 10888258
2025-12-31 | Jabori HPS | 2461991
2025-12-31 | Karora HPS | 755902
2025-12-31 | Koto HPS | 7689394
2025-12-31 | Machai HPS | 3893605
2025-12-31 | Malakand-3 HPS | 116050589
2025-12-31 | Pehur HPS | 14763524
2025-12-31 | Reshun HPS | 7607817
2026-01-31 | Daral Khwar HPS | 9317267
2026-01-31 | Jabori HPS | 3626307
2026-01-31 | Karora HPS | 822582
2026-01-31 | Koto HPS | 6122464
2026-01-31 | Machai HPS | 3626377
2026-01-31 | Malakand-3 HPS | 8594217
2026-01-31 | Pehur HPS | 11840293
2026-01-31 | Reshun HPS | 8379463
2026-02-28 | Daral Khwar HPS | 45545397
2026-02-28 | Jabori HPS | 3055634
2026-02-28 | Karora HPS | 1803911
2026-02-28 | Koto HPS | 4271096
2026-02-28 | Machai HPS | 2464172
2026-02-28 | Malakand-3 HPS | 89118116
2026-02-28 | Pehur HPS | 12061161
2026-02-28 | Reshun HPS | 9145159
2026-03-31 | Daral Khwar HPS | 9346270
2026-03-31 | Jabori HPS | 2878437
2026-03-31 | Karora HPS | 1446886
2026-03-31 | Koto HPS | 7714213
2026-03-31 | Machai HPS | 7311033
2026-03-31 | Malakand-3 HPS | 125670317
2026-03-31 | Pehur HPS | 19170131
2026-03-31 | Reshun HPS | 16123065
2026-04-09 | Pehur HPS | 16473596
2026-04-24 | Pehur HPS | 17873100

## Cleaning_Report
Item | Value
Rows - Generation_Data.xlsx | 1782
Rows - Link file 'Generation Data' (khali/formula rows hata kar) | 3562
Column-shift (email/Aux. Cons.) theek ki gayi rows | 484
Duplicate rows (Plant+Date) hata di gayi | 683
Negative/galat values theek ki gayi | 33
Capacity installed-capacity sheet se overwrite (mismatch rows) | 0
Hydrology/Cumic ke typing-error outliers (median x10 se zyada) theek kiye | 6
Rows ADDED (jin dino ki entry source me thi hi nahi) | 99
FINAL rows in Clean_Generation_Data | 4760
Date range | 2025-01-01 to 2026-09-19
Baaqi missing values (numeric columns) | 0
Added days - Daral Khwar HPS | 4
Added days - Jabori HPS | 5
Added days - Karora HPS | 7
Added days - Koto HPS | 7
Added days - Machai HPS | 20
Added days - Malakand-3 HPS | 9
Added days - Pehur HPS | 20
Added days - Reshun HPS | 22
Added days - Shishi HPS | 5
Missing before cleaning - Maximum Station Load (MW) | 83
Missing before cleaning - Avg Station Load (MW) | 82
Missing before cleaning - Total Daily Units Generated (kWh) | 82
Missing before cleaning - Daily Net Energy Output (kWh) | 83
Missing before cleaning - Avg Historical Hydrology | 194
Missing before cleaning - Actual Avg Cumic | 121
Missing before cleaning - Daily Design Plant Factor | 1127
Missing before cleaning - Expected Generation (KWh) | 142
Missing before cleaning - Aux. Cons. | 1
Missing before cleaning - Remarks/ Issues | 154
Missing before cleaning - Email Address | 819
Previous Years sheet - duplicate rows hata di | 0
Note | Previous Years: pehle saal ki 'Previous Year' / growth columns khali rehti hain (pichla saal hai hi nahi).
Note | Shishi HPS ka data 2025-10-26 par khatam hota hai, is liye us ke baad rows nahi banayi gayin.